## Introduction
Network Headroom Report 2024
Summary Page
Published April 2024
The data contained in this workbook is an accompaniment to Northern Powergrid's 2024 Network Development Report and can also be viewed alongside the 2024 NDP Metholodology. The workbook can be used to identify areas of the network with headroom availability up to, and including, 2050. This can be broken down into each Distribution Future Energy Scenario (DFES) - Consumer Transformation, Leading the Way, Falling Short and System Transformation - as well as Northern Powergrid's Best View Scenario (which supersedes the Planning Scenario). This can be viewed for every Bulk Supply Point (BSP) and Primary Substation. The Generation Headroom calculations are completed by finding the difference in the forecast minimum demand, based on the DFES 2023 data, the results of the latest fault level survey, and the forecast reverse power flow capacity, at each substation. This takes into account the forecast generation capacity based on the DFES 2023 data. The reverse power flow forecast takes into account the current reverse power flow limits and any changes which are scheduled to take place in the future, driven by anticipated investment. The Demand Headroom calculations are completed by finding the difference in the forecast demand, based on the DFES 2023 data, and the forecast firm capacity, at each substation. The firm capacity forecast takes into account the current firm capacity and any changes which are scheduled to take place in the future, driven by anticipated investment outcomes. Netherlands Way, Wetherby and Seaham are new substations so therefore have no demand forecasts. This results in forecast headrooms being equal to their proposed firm capacities. The forecast substation headrooms are currently under review and will be addressed in the next update of the NDP. The results should be only used as a guide and will be updated in the next refresh of the data, due in 2025.
Contents
Worksheet |  | Description
Demand Headroom Capacity |  | Details of the demand headroom capacity (in MW) for each BSP and Primary substation for each of the DFES scenarios and Northern Powergrid's Best View scenario.
Generation Headroom Capacity |  | Details of the generation headroom capacity (in MW) for each BSP and Primary substation for each of the DFES scenarios and Northern Powergrid's Best View scenario.
EISD Table |  | Details of the Earliest In-Service Date for Demand and Generation at each GSP, scenario-independent, as advised by National Grid.
DOCUMENT CONTROL
Approvals
Role | Approver | Date
Author | Dr Richard Mandeya | 2024-04-26
Reviewer | Dr Neal Wade | 2024-04-29
Manager Approval | Dr Gillian Williamson | 2024-04-29
Version Control
Version | Comment | Date
V1.0 | First issue for Stakeholder Consultation | 2024-03-28
V1.1 | Second issue final publication | 2024-04-29

## Demand Headroom
Version 1.1
Please filter on your selected substation
Licence Area | Substation Name | Voltage (kV) | Supply Voltage (kV) | BSP Group | GSP | Substation Location | Scenario Name | Demand Headroom Capacity (MW) 2024 | Demand Headroom Capacity (MW) 2025 | Demand Headroom Capacity (MW) 2026 | Demand Headroom Capacity (MW) 2027 | Demand Headroom Capacity (MW) 2028 | Demand Headroom Capacity (MW) 2029 | Demand Headroom Capacity (MW) 2030 | Demand Headroom Capacity (MW) 2035 | Demand Headroom Capacity (MW) 2040 | Demand Headroom Capacity (MW) 2045 | Demand Headroom Capacity (MW) 2050 | Bulk Supply Point or Primary | Row Number
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Consumer Transformation | 18.469 | 18.322 | 65.908 | 65.29 | 65.11 | 64.864 | 64.498 | 61.994 | 52.459 | 45.46 | 38.966 | BSP | 1
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Consumer Transformation | 31.058 | 29.197 | 26.543 | 23.408 | 21.105 | 18.679 | 15.736 | -15.991 | -41.536 | -60.607 | -78.282 | BSP | 2
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Consumer Transformation | 122.331 | 115.709 | 113.77 | 111.676 | 110.223 | 108.583 | 106.422 | 94.998 | 66.707 | 46.024 | 27.937 | BSP | 3
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Consumer Transformation | 9.077 | 6.055 | 2.762 | -1.19 | -4.006 | -6.943 | -10.523 | -26.565 | -59.783 | -85.719 | -110.482 | BSP | 4
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 68.212 | 65.511 | 63.822 | 61.776 | 60.341 | 58.824 | 56.923 | 48.331 | 31.373 | 18.947 | 7.642 | BSP | 5
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Consumer Transformation | 17.33 | 17.502 | 17.516 | 17.384 | 17.425 | 17.383 | 17.229 | 15.356 | 8.953 | 4.548 | 0.827 | BSP | 6
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Consumer Transformation | 29.847 | 28.367 | 26.35 | 24.024 | 22.079 | 20.045 | 17.607 | 72.314 | 53.537 | 39.125 | 25.956 | BSP | 7
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Consumer Transformation | 43.008 | 41.472 | 39.292 | 36.896 | 35.338 | 33.659 | 31.508 | 21.424 | 0.234 | -15.095 | -29.167 | BSP | 8
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 45.273 | 40.966 | 40.127 | 39.119 | 38.439 | 37.62 | 28.218 | -1.389 | -16.207 | -26.418 | -35.089 | BSP | 9
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Consumer Transformation | 70.951 | 68.698 | 67.526 | 66.042 | 65.095 | 64.117 | 62.887 | 57.665 | 43.612 | 32.458 | 21.819 | BSP | 10
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Consumer Transformation | 40.092 | 38.05 | 36.291 | 34.101 | 32.651 | 31.072 | 29.04 | 14.444 | -5.97 | -20.769 | -34.264 | BSP | 11
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Consumer Transformation | 34.474 | 26.047 | 17.548 | -0.036 | -7.985 | -16.421 | -26.651 | -119.334 | -214.403 | -285.432 | -348.857 | BSP | 12
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Consumer Transformation | 90.328 | 89.833 | 89.095 | 88.202 | 87.6 | 86.964 | 86.173 | 82.567 | 75.427 | 69.958 | 64.683 | BSP | 13
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Consumer Transformation | 53.841 | 53.064 | 51.896 | 50.399 | 49.289 | 48.078 | 46.629 | 38.725 | 16.283 | -2.191 | -19.39 | BSP | 14
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Consumer Transformation | 40.949 | 37.996 | 34.918 | 31.272 | 28.356 | 25.228 | 21.466 | 2.439 | -29.781 | -53.06 | -73.644 | BSP | 15
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Consumer Transformation | 63.098 | 62.985 | 62.578 | 61.945 | 61.786 | 61.586 | 61.267 | 59.475 | 49.568 | 41.919 | 34.669 | BSP | 16
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 42.019 | 41.729 | 41.215 | 40.541 | 40.086 | 39.588 | 38.933 | 35.821 | 28.656 | 23.286 | 18.348 | BSP | 17
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Consumer Transformation | 17.148 | 16.261 | 14.87 | 13.181 | 12.075 | 10.876 | 9.365 | 2.087 | -10.791 | -19.605 | -27.611 | BSP | 18
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Consumer Transformation | 57.621 | 55.804 | 53.053 | 49.779 | 47.722 | 45.574 | 42.915 | 31.101 | 7.225 | -10.296 | -26.775 | BSP | 19
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Consumer Transformation | 49.991 | 49.057 | 47.526 | 84.58 | 83.045 | 81.395 | 79.331 | 69.387 | 51.377 | 38.175 | 26.48 | BSP | 20
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Consumer Transformation | 37.872 | 35.446 | 33.649 | 31.296 | 29.655 | 27.886 | 25.596 | 14.764 | -12.526 | -33.771 | -53.426 | BSP | 21
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Consumer Transformation | 59.427 | 57.903 | 55.725 | 53.199 | 51.254 | 49.208 | 46.719 | 62.213 | 42.011 | 27.246 | 13.997 | BSP | 22
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Consumer Transformation | 89.01 | 88.464 | 87.549 | 86.396 | 85.619 | 84.812 | 83.798 | 79.41 | 68.777 | 60.513 | 52.816 | BSP | 23
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Consumer Transformation | 81.807 | 81 | 79.87 | 78.534 | 77.422 | 76.26 | 74.864 | 68.54 | 59.197 | 52.462 | 46.434 | BSP | 24
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Consumer Transformation | 90.944 | 90.03 | 88.783 | 87.384 | 86.36 | 85.29 | 83.99 | 78.054 | 66.582 | 57.963 | 49.986 | BSP | 25
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Consumer Transformation | 46.141 | 45.585 | 44.739 | 43.619 | 42.442 | 41.005 | 39.204 | 27.029 | 9.867 | -0.303 | -7.04 | BSP | 26
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Consumer Transformation | 55.872 | 54.947 | 53.641 | 52.097 | 50.956 | 49.74 | 48.279 | 41.058 | 27.388 | 17.007 | 7.384 | BSP | 27
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 62.72 | 62.877 | 62.952 | 63 | 63.135 | 63.241 | 63.28 | 63.279 | 58.466 | 54.588 | 51.033 | BSP | 28
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 33.31 | 28.047 | 22.435 | 18.23 | 15.127 | 11.937 | 8.085 | -8.798 | -41.622 | -66.278 | -88.599 | BSP | 29
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Consumer Transformation | 40.381 | 40.083 | 39.476 | 38.687 | 38.13 | 37.443 | 36.503 | 30.595 | 14.16 | 2.254 | -7.715 | BSP | 30
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Consumer Transformation | 53.891 | 51.664 | 48.992 | 46.595 | 44.658 | 42.635 | 40.082 | 28.99 | 8.266 | -7.27 | -21.042 | BSP | 31
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Consumer Transformation | 44.366 | 42.777 | 40.319 | 37.386 | 35.302 | 33.119 | 30.383 | 18.344 | -6.947 | -26.017 | -43.489 | BSP | 32
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Consumer Transformation | 113.613 | 111.537 | 110.939 | 109.94 | 109.385 | 108.564 | 107.349 | 72.925 | 48.44 | 31.331 | 17.285 | BSP | 33
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Consumer Transformation | 80.169 | 80.155 | 80.01 | 79.75 | 79.593 | 79.378 | 79.072 | 76.885 | 71.013 | 66.544 | 62.593 | BSP | 34
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Consumer Transformation | 67.871 | 66.679 | 65.092 | 63.45 | 62.328 | 61.153 | 59.676 | 53.215 | 39.438 | 29.243 | 19.814 | BSP | 35
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Consumer Transformation | 25.452 | 25.518 | 25.468 | 25.308 | 25.234 | 25.135 | 24.965 | 23.894 | 16.904 | 11.066 | 5.731 | BSP | 36
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP | 37
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 55.166 | 54.68 | 51.754 | 50.916 | 50.016 | 48.984 | 47.738 | 40.162 | 29.229 | 21.854 | 16.264 | BSP | 38
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Consumer Transformation | 49.284 | 45.782 | 43.357 | 40.833 | 39.132 | 37.346 | 35.101 | 25.25 | 6.114 | -7.758 | -20.518 | BSP | 39
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 4.458 | 4.141 | 3.446 | 2.477 | 2.088 | 1.617 | 0.97 | -2.983 | -17.871 | -29.406 | -40.163 | BSP | 40
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Consumer Transformation | 40.428 | 40.433 | 40.435 | 40.433 | 106.629 | 106.622 | 106.611 | 106.528 | 106.395 | 106.244 | 106.09 | BSP | 41
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 69.456 | 66.112 | 65.527 | 64.88 | 64.278 | 63.632 | 62.92 | 58.835 | 53.168 | 48.594 | 44.573 | BSP | 42
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Consumer Transformation | 54.604 | 53.885 | 52.981 | 51.878 | 50.82 | 49.622 | 48.237 | 39.547 | 25.305 | 14.927 | 6.242 | BSP | 43
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Consumer Transformation | 82.633 | 82.183 | 81.599 | 80.923 | 80.316 | 79.692 | 78.981 | 75.644 | 70.421 | 66.157 | 62.252 | BSP | 44
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Consumer Transformation | 23.986 | 20.096 | 17.695 | 14.802 | 12.563 | 10.188 | 7.159 | -6.611 | -36.054 | -58.332 | -78.217 | BSP | 45
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Consumer Transformation | 46.554 | 45.254 | 43.224 | 40.772 | 39.055 | 37.217 | 34.889 | 23.979 | 0.963 | -16.214 | -31.787 | BSP | 46
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Consumer Transformation | 45.15 | 42.646 | 41.004 | 38.878 | 37.563 | 36.09 | 34.171 | 24.291 | 3.408 | -11.078 | -23.983 | BSP | 47
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 27.805 | 25.794 | 22.695 | 18.953 | 16.42 | 13.711 | 10.299 | -5.564 | -33.578 | -53.275 | -71.537 | BSP | 48
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Consumer Transformation | 67.792 | 66.987 | 65.865 | 64.487 | 63.644 | 62.729 | 61.667 | 55.694 | 40.532 | 28.536 | 17.054 | BSP | 49
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Consumer Transformation | 33.853 | 31.515 | 28.304 | 24.663 | 22.099 | 19.406 | 16.17 | 1.068 | -24.54 | -42.796 | -59.607 | BSP | 50
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Consumer Transformation | 26.969 | 21.602 | 16.068 | 9.915 | 4.817 | -0.487 | -6.855 | -35.68 | -85.583 | -122.75 | -156.114 | BSP | 51
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Consumer Transformation | 53.928 | 48.248 | 45.182 | 42.035 | 39.604 | 37.089 | 34.009 | 20.816 | -0.823 | -16.255 | -30.024 | BSP | 52
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Consumer Transformation | 43.708 | 42.025 | 39.729 | 37.064 | 34.908 | 32.682 | 30.013 | 18.202 | -1.658 | -17.219 | -31.916 | BSP | 53
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Consumer Transformation | 56.759 | 56.13 | 55.005 | 53.565 | 52.467 | 51.301 | 49.798 | 42.959 | 25.81 | 12.516 | 0.656 | BSP | 54
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Falling Short | 18.223 | 18.203 | 66.105 | 65.915 | 65.629 | 65.257 | 64.843 | 62.38 | 59.447 | 57.305 | 56.136 | BSP | 55
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Falling Short | 31.268 | 30.126 | 28.739 | 27.084 | 25.073 | 22.742 | 20.432 | -8.16 | -17.281 | -23.593 | -27.881 | BSP | 56
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Falling Short | 122.554 | 116.581 | 115.765 | 114.755 | 113.376 | 111.664 | 109.894 | 101.017 | 92.715 | 87.386 | 84.929 | BSP | 57
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Falling Short | 9.135 | 6.994 | 5.311 | 3.271 | 0.775 | -2.117 | -4.94 | -17.499 | -27.604 | -34.745 | -40.032 | BSP | 58
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 68.47 | 66.347 | 65.668 | 64.793 | 63.649 | 62.27 | 60.917 | 55.044 | 50.67 | 48.11 | 46.799 | BSP | 59
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Falling Short | 16.879 | 16.858 | 16.777 | 16.623 | 16.388 | 16.073 | 15.694 | 13.064 | 9.55 | 6.693 | 4.943 | BSP | 60
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Falling Short | 29.827 | 28.697 | 27.379 | 25.861 | 24.068 | 22.028 | 20.012 | 76.704 | 68.859 | 63.075 | 58.78 | BSP | 61
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Falling Short | 43.485 | 42.878 | 42.113 | 41.173 | 39.919 | 38.388 | 36.874 | 29.975 | 24.398 | 21.056 | 19.338 | BSP | 62
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 44.946 | 40.786 | 40.273 | 39.631 | 38.809 | 37.817 | 28.424 | -0.76 | -8.141 | -13.735 | -16.916 | BSP | 63
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Falling Short | 70.915 | 68.982 | 68.481 | 67.819 | 66.959 | 65.93 | 64.94 | 60.885 | 58.249 | 56.708 | 55.645 | BSP | 64
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Falling Short | 40.152 | 38.718 | 38.057 | 37.157 | 35.945 | 34.455 | 32.964 | 21.286 | 15.406 | 11.743 | 9.897 | BSP | 65
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Falling Short | 35.831 | 29.826 | 25.384 | 12.296 | 5.519 | -2.429 | -10.383 | -90.845 | -123.235 | -144.947 | -157.71 | BSP | 66
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Falling Short | 90.299 | 90.014 | 89.652 | 89.208 | 88.661 | 88.024 | 87.398 | 84.543 | 82.13 | 80.377 | 79.062 | BSP | 67
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Falling Short | 52.96 | 52.029 | 50.956 | 49.707 | 48.263 | 46.649 | 44.994 | 36.408 | 27.644 | 20.37 | 14.555 | BSP | 68
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Falling Short | 41.121 | 38.894 | 37.106 | 34.975 | 32.405 | 29.423 | 26.39 | 11.325 | -2.936 | -13.159 | -19.376 | BSP | 69
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Falling Short | 62.818 | 62.837 | 62.777 | 62.622 | 62.365 | 62.027 | 61.678 | 59.912 | 58.182 | 57.036 | 56.35 | BSP | 70
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 41.971 | 41.843 | 41.641 | 41.356 | 40.968 | 40.493 | 40.022 | 37.829 | 36.02 | 34.911 | 34.297 | BSP | 71
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Falling Short | 17.315 | 16.987 | 16.502 | 15.855 | 14.994 | 13.937 | 12.873 | 7.807 | 3.242 | 0.274 | -1.176 | BSP | 72
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Falling Short | 58.156 | 57.437 | 56.447 | 55.186 | 53.559 | 51.601 | 49.699 | 41.615 | 35.756 | 32.35 | 30.578 | BSP | 73
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Falling Short | 49.781 | 49.097 | 48.198 | 86.068 | 84.651 | 82.972 | 81.287 | 73.341 | 66.431 | 61.572 | 58.537 | BSP | 74
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Falling Short | 37.85 | 35.936 | 35.193 | 34.165 | 32.801 | 31.149 | 29.518 | 22.141 | 16.418 | 13.093 | 11.31 | BSP | 75
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Falling Short | 59.607 | 58.674 | 57.53 | 56.164 | 54.479 | 52.501 | 50.548 | 68.661 | 61.257 | 56.122 | 52.827 | BSP | 76
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Falling Short | 89.098 | 88.862 | 88.507 | 88.028 | 87.4 | 86.643 | 85.914 | 82.921 | 80.992 | 79.988 | 79.452 | BSP | 77
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Falling Short | 81.799 | 81.195 | 80.467 | 79.607 | 78.583 | 77.41 | 76.252 | 70.932 | 66.604 | 63.607 | 61.455 | BSP | 78
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Falling Short | 91.21 | 90.723 | 90.138 | 89.446 | 88.592 | 87.595 | 86.615 | 82.24 | 78.814 | 76.632 | 75.279 | BSP | 79
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Falling Short | 45.782 | 45.182 | 44.445 | 43.529 | 42.378 | 40.971 | 39.368 | 29.307 | 16.914 | 7.61 | 3.194 | BSP | 80
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Falling Short | 55.486 | 54.664 | 53.72 | 52.635 | 51.37 | 49.943 | 48.501 | 41.384 | 34.565 | 29.055 | 24.747 | BSP | 81
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 62.396 | 62.482 | 62.545 | 62.574 | 62.546 | 62.476 | 62.397 | 61.893 | 61.277 | 60.853 | 60.565 | BSP | 82
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 36.886 | 34.46 | 32.192 | 30.139 | 27.578 | 24.56 | 21.637 | 9.492 | 1.384 | -3.327 | -6.215 | BSP | 83
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Falling Short | 40.197 | 39.995 | 39.685 | 39.24 | 38.601 | 37.781 | 36.881 | 31.815 | 26.332 | 22.604 | 21.026 | BSP | 84
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Falling Short | 55.082 | 53.996 | 52.843 | 51.631 | 50.074 | 48.207 | 46.41 | 39.014 | 34.206 | 31.579 | 30.127 | BSP | 85
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Falling Short | 44.731 | 43.982 | 42.964 | 41.666 | 39.983 | 37.956 | 35.996 | 27.724 | 21.954 | 18.671 | 16.854 | BSP | 86
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Falling Short | 113.14 | 111.138 | 110.929 | 110.488 | 109.762 | 108.762 | 107.575 | 74.554 | 65.66 | 59.471 | 57.112 | BSP | 87
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Falling Short | 79.486 | 79.208 | 78.878 | 78.483 | 78.016 | 77.481 | 76.905 | 73.586 | 69.764 | 66.383 | 63.72 | BSP | 88
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Falling Short | 68.359 | 67.837 | 67.227 | 66.521 | 65.598 | 64.49 | 63.415 | 58.877 | 55.693 | 53.889 | 52.876 | BSP | 89
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Falling Short | 25.231 | 25.232 | 25.188 | 25.085 | 24.924 | 24.717 | 24.501 | 23.359 | 22.271 | 21.584 | 21.158 | BSP | 90
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Falling Short | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP | 91
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Falling Short | 54.601 | 53.889 | 50.82 | 49.874 | 48.781 | 47.538 | 46.201 | 38.631 | 30.102 | 23.133 | 18.477 | BSP | 92
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Falling Short | 50.024 | 47.505 | 46.57 | 45.489 | 44.086 | 42.4 | 40.758 | 33.844 | 29.012 | 26.247 | 24.732 | BSP | 93
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 4.221 | 4.112 | 3.9 | 3.569 | 3.101 | 2.513 | 1.886 | -1.502 | -4.976 | -7.316 | -8.512 | BSP | 94
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Falling Short | 40.329 | 40.269 | 40.206 | 40.14 | 106.271 | 106.198 | 106.124 | 105.716 | 105.261 | 104.775 | 104.276 | BSP | 95
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 68.725 | 64.995 | 64.045 | 63.054 | 62.012 | 60.917 | 59.783 | 53.711 | 47.171 | 40.942 | 35.319 | BSP | 96
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Falling Short | 53.804 | 52.795 | 51.701 | 50.488 | 49.138 | 47.647 | 46.046 | 36.796 | 26.034 | 16.881 | 10.307 | BSP | 97
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Falling Short | 82.227 | 81.642 | 81.004 | 80.309 | 79.544 | 78.716 | 77.891 | 73.925 | 70.2 | 66.823 | 63.744 | BSP | 98
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Falling Short | 24.277 | 21.112 | 20.032 | 18.65 | 16.839 | 14.655 | 12.522 | 3.228 | -3.648 | -7.605 | -9.706 | BSP | 99
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Falling Short | 46.789 | 46.201 | 45.382 | 44.316 | 42.915 | 41.217 | 39.537 | 31.962 | 25.992 | 22.402 | 20.551 | BSP | 100
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Falling Short | 45.112 | 43.206 | 42.661 | 41.861 | 40.748 | 39.348 | 37.907 | 30.707 | 23.787 | 19.307 | 17.339 | BSP | 101
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 28.069 | 27.212 | 26.008 | 24.446 | 22.422 | 19.968 | 17.543 | 6.257 | -3.689 | -10.289 | -14.052 | BSP | 102
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Falling Short | 67.432 | 66.763 | 66.008 | 65.143 | 64.16 | 63.072 | 61.943 | 55.83 | 49.178 | 43.628 | 39.298 | BSP | 103
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Falling Short | 34.291 | 32.994 | 31.439 | 29.618 | 27.405 | 24.833 | 22.276 | 10.336 | -0.198 | -7.703 | -12.668 | BSP | 104
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Falling Short | 27.985 | 24.095 | 20.997 | 17.404 | 13.058 | 8.029 | 3.088 | -19.186 | -36.854 | -48.404 | -56.02 | BSP | 105
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Falling Short | 54.928 | 50.384 | 49.019 | 47.46 | 45.491 | 43.149 | 40.878 | 31.428 | 24.953 | 21.231 | 19.22 | BSP | 106
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Falling Short | 43.729 | 42.49 | 41.049 | 39.394 | 37.45 | 35.258 | 33.124 | 23.633 | 16.027 | 10.376 | 5.794 | BSP | 107
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Falling Short | 56.683 | 56.317 | 55.77 | 55.032 | 54.051 | 52.856 | 51.682 | 46.571 | 42.821 | 40.645 | 39.47 | BSP | 108
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Leading the Way | 18.47 | 18.276 | 65.8 | 65.136 | 64.916 | 64.606 | 63.874 | 53.151 | 44.754 | 39.097 | 40.512 | BSP | 109
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Leading the Way | 31.137 | 29.232 | 26.487 | 23.311 | 21.064 | 18.652 | 15.095 | -33.672 | -57.001 | -73.376 | -73.341 | BSP | 110
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Leading the Way | 122.421 | 115.756 | 113.654 | 111.428 | 109.911 | 108.145 | 105.085 | 71.972 | 46.862 | 29.774 | 32.797 | BSP | 111
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Leading the Way | 9.152 | 6.098 | 2.721 | -1.254 | -3.943 | -6.789 | -11.122 | -51.13 | -82.031 | -104.916 | -104.698 | BSP | 112
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 68.275 | 65.582 | 63.865 | 61.808 | 60.434 | 58.952 | 56.6 | 35.868 | 20.68 | 10.428 | 11.822 | BSP | 113
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Leading the Way | 17.315 | 17.442 | 17.391 | 17.195 | 17.162 | 17.019 | 16.582 | 9.613 | 4.236 | 0.877 | 1.82 | BSP | 114
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Leading the Way | 29.886 | 28.393 | 26.319 | 23.942 | 22.037 | 20.012 | 17.163 | 60.608 | 43.315 | 30.683 | 29.435 | BSP | 115
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Leading the Way | 43.127 | 41.596 | 39.352 | 36.942 | 35.459 | 33.831 | 31.193 | 5.093 | -13.833 | -26.39 | -23.962 | BSP | 116
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 45.288 | 40.914 | 39.951 | 38.825 | 38.01 | 36.996 | 27.122 | -12.44 | -25.283 | -33.691 | -33.084 | BSP | 117
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Leading the Way | 70.982 | 68.722 | 67.517 | 66.009 | 65.125 | 64.193 | 62.502 | 45.884 | 32.799 | 23.122 | 24.3 | BSP | 118
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Leading the Way | 40.122 | 38.043 | 36.204 | 33.962 | 32.548 | 30.975 | 28.384 | -1.382 | -19.695 | -31.933 | -29.943 | BSP | 119
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Leading the Way | 34.642 | 26.09 | 17.204 | -0.745 | -8.744 | -17.444 | -30.375 | -185.794 | -271.607 | -331.994 | -331.518 | BSP | 120
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Leading the Way | 90.344 | 89.842 | 89.088 | 88.194 | 87.625 | 87.015 | 86.077 | 77.326 | 70.758 | 66.037 | 66.157 | BSP | 121
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Leading the Way | 53.843 | 52.976 | 51.686 | 50.104 | 48.955 | 47.67 | 45.598 | 20.898 | 0.082 | -16.41 | -17.119 | BSP | 122
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Leading the Way | 40.961 | 37.927 | 34.682 | 30.869 | 27.845 | 24.518 | 19.896 | -18.289 | -47.216 | -67.13 | -68.492 | BSP | 123
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Leading the Way | 63.121 | 62.975 | 62.526 | 61.883 | 61.737 | 61.538 | 60.893 | 49.677 | 40.889 | 34.712 | 36.801 | BSP | 124
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 42.031 | 41.723 | 41.18 | 40.498 | 40.073 | 39.601 | 38.8 | 30.012 | 23.525 | 19.013 | 19.859 | BSP | 125
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Leading the Way | 17.171 | 16.254 | 14.805 | 13.074 | 11.972 | 10.745 | 8.846 | -7.102 | -18.471 | -25.553 | -24.639 | BSP | 126
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Leading the Way | 57.723 | 55.935 | 53.163 | 49.878 | 47.917 | 45.82 | 42.416 | 13.308 | -8.089 | -22.423 | -20.43 | BSP | 127
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Leading the Way | 50.007 | 49.047 | 47.444 | 84.42 | 82.887 | 81.196 | 78.62 | 56.998 | 40.802 | 29.672 | 29.957 | BSP | 128
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Leading the Way | 37.916 | 35.438 | 33.544 | 31.138 | 29.598 | 27.915 | 24.926 | -7.838 | -32.953 | -51.229 | -48.891 | BSP | 129
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Leading the Way | 59.484 | 57.959 | 55.724 | 53.15 | 51.23 | 49.161 | 46.153 | 48.801 | 30.657 | 18.229 | 18.537 | BSP | 130
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Leading the Way | 89.032 | 88.48 | 87.543 | 86.374 | 85.649 | 84.882 | 83.542 | 70.797 | 61.084 | 54.152 | 55.197 | BSP | 131
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Leading the Way | 81.884 | 81.089 | 79.946 | 78.606 | 77.527 | 76.376 | 74.795 | 63.224 | 54.737 | 48.962 | 48.575 | BSP | 132
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Leading the Way | 91.005 | 90.095 | 88.815 | 87.393 | 86.4 | 85.341 | 83.757 | 69.857 | 59.376 | 51.981 | 52.255 | BSP | 133
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Leading the Way | 46.057 | 45.388 | 44.342 | 42.949 | 41.43 | 39.535 | 37.005 | 17.654 | 3.739 | -3.822 | -4.845 | BSP | 134
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Leading the Way | 55.891 | 54.932 | 53.566 | 51.98 | 50.829 | 49.574 | 47.779 | 31.883 | 19.437 | 10.433 | 9.679 | BSP | 135
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 62.742 | 62.878 | 62.917 | 62.955 | 63.1 | 63.216 | 63.127 | 57.781 | 53.459 | 50.228 | 51.826 | BSP | 136
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 33.827 | 28.795 | 23.072 | 18.771 | 15.756 | 12.599 | 7.708 | -31.722 | -61.554 | -82.171 | -80.087 | BSP | 137
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Leading the Way | 40.38 | 40.007 | 39.259 | 38.323 | 37.648 | 36.788 | 35.202 | 16.764 | 2.433 | -7.236 | -5.468 | BSP | 138
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Leading the Way | 54.114 | 51.988 | 49.285 | 46.881 | 45.066 | 43.145 | 40.088 | 14.381 | -4.222 | -16.96 | -14.987 | BSP | 139
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Leading the Way | 44.448 | 42.857 | 40.339 | 37.369 | 35.406 | 33.313 | 29.882 | -0.923 | -23.787 | -39.624 | -37.347 | BSP | 140
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Leading the Way | 113.574 | 111.316 | 110.44 | 109.182 | 108.354 | 107.162 | 104.871 | 49.58 | 28.399 | 14.662 | 17.932 | BSP | 141
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Leading the Way | 80.161 | 80.119 | 79.932 | 79.628 | 79.427 | 79.148 | 78.63 | 72.323 | 67.141 | 63.391 | 63.334 | BSP | 142
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Leading the Way | 67.983 | 66.816 | 65.198 | 63.559 | 62.505 | 61.38 | 59.596 | 42.694 | 30.258 | 21.705 | 23.162 | BSP | 143
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Leading the Way | 25.453 | 25.487 | 25.396 | 25.212 | 25.142 | 25.041 | 24.634 | 16.938 | 10.468 | 5.375 | 6.376 | BSP | 144
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Leading the Way | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP | 145
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Leading the Way | 55.131 | 54.585 | 51.558 | 50.583 | 49.531 | 48.292 | 46.669 | 34.481 | 25.139 | 19.077 | 17.457 | BSP | 146
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Leading the Way | 49.44 | 45.991 | 43.537 | 41.008 | 39.402 | 37.683 | 34.936 | 11.279 | -5.741 | -16.959 | -14.915 | BSP | 147
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 4.479 | 4.116 | 3.339 | 2.292 | 1.88 | 1.357 | 0.139 | -16.463 | -29.866 | -39.477 | -37.82 | BSP | 148
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Leading the Way | 40.428 | 40.433 | 40.435 | 40.433 | 106.63 | 106.623 | 106.613 | 106.51 | 106.379 | 106.23 | 106.098 | BSP | 149
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 69.442 | 66.08 | 65.463 | 64.773 | 64.125 | 63.416 | 62.547 | 56.559 | 51.416 | 47.37 | 45.114 | BSP | 150
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Leading the Way | 54.555 | 53.753 | 52.721 | 51.47 | 50.226 | 48.781 | 46.971 | 31.598 | 19.057 | 10.082 | 7.423 | BSP | 151
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Leading the Way | 82.639 | 82.185 | 81.588 | 80.898 | 80.293 | 79.66 | 78.836 | 72.947 | 68.074 | 64.214 | 63.026 | BSP | 152
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Leading the Way | 24.077 | 20.172 | 17.685 | 14.748 | 12.636 | 10.361 | 6.601 | -29.211 | -55.683 | -74.088 | -71.175 | BSP | 153
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Leading the Way | 46.578 | 45.241 | 43.125 | 40.612 | 38.957 | 37.151 | 34.178 | 6.321 | -14.342 | -28.51 | -26.509 | BSP | 154
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Leading the Way | 45.169 | 42.616 | 40.876 | 38.663 | 37.31 | 35.742 | 33.16 | 8.065 | -10.203 | -21.795 | -19.594 | BSP | 155
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 27.839 | 25.747 | 22.518 | 18.71 | 16.247 | 13.558 | 9.403 | -25.758 | -50.971 | -67.302 | -65.52 | BSP | 156
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Leading the Way | 67.776 | 66.877 | 65.65 | 64.209 | 63.319 | 62.332 | 60.827 | 43.934 | 29.974 | 19.443 | 18.703 | BSP | 157
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Leading the Way | 33.926 | 31.533 | 28.21 | 24.504 | 21.956 | 19.218 | 15.277 | -15.805 | -38.714 | -53.858 | -53.805 | BSP | 158
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Leading the Way | 27.289 | 21.926 | 16.244 | 10.011 | 5.052 | -0.211 | -7.726 | -67.942 | -113.581 | -145.737 | -146.066 | BSP | 159
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Leading the Way | 54.128 | 48.525 | 45.421 | 42.24 | 39.905 | 37.432 | 33.782 | 6.728 | -12.66 | -25.436 | -24.099 | BSP | 160
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Leading the Way | 43.785 | 42.107 | 39.784 | 37.13 | 35.09 | 32.966 | 30 | 5.709 | -12.79 | -26.596 | -27.697 | BSP | 161
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Leading the Way | 56.791 | 56.144 | 54.966 | 53.485 | 52.435 | 51.293 | 49.249 | 29.062 | 13.562 | 2.475 | 4.315 | BSP | 162
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - System Transformation | 18.254 | 18.122 | 65.849 | 65.467 | 65.074 | 64.603 | 64.025 | 60.296 | 53.856 | 46.421 | 36.23 | BSP | 163
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - System Transformation | 30.717 | 28.94 | 26.707 | 24.205 | 21.673 | 19.004 | 16.149 | -16.153 | -33.44 | -52.259 | -77.381 | BSP | 164
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - System Transformation | 121.802 | 115.068 | 113.372 | 111.683 | 109.915 | 107.939 | 105.691 | 93.041 | 72.695 | 52.315 | 25.801 | BSP | 165
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - System Transformation | 8.574 | 5.55 | 2.674 | -0.576 | -3.753 | -7.062 | -10.587 | -27.82 | -51.602 | -77.587 | -112.606 | BSP | 166
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 68.012 | 65.339 | 63.918 | 62.295 | 60.73 | 59.082 | 57.313 | 48.608 | 37.37 | 25.334 | 8.714 | BSP | 167
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - System Transformation | 17.032 | 17.06 | 16.989 | 16.821 | 16.601 | 16.284 | 15.854 | 12.464 | 6.763 | 1.225 | -5.423 | BSP | 168
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - System Transformation | 29.548 | 28.023 | 26.159 | 24.095 | 21.972 | 19.752 | 17.412 | 71.712 | 57.548 | 42.94 | 24.281 | BSP | 169
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - System Transformation | 42.644 | 41.148 | 39.363 | 37.546 | 35.776 | 33.886 | 31.806 | 21.223 | 6.671 | -8.409 | -28.638 | BSP | 170
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 44.941 | 40.593 | 39.842 | 39.007 | 38.057 | 36.951 | 27.332 | -3.533 | -15.773 | -27.076 | -40.099 | BSP | 171
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - System Transformation | 70.718 | 68.439 | 67.422 | 66.222 | 65.095 | 63.926 | 62.692 | 56.755 | 47.868 | 36.901 | 20.673 | BSP | 172
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - System Transformation | 39.766 | 37.725 | 36.249 | 34.531 | 32.84 | 31.017 | 29.009 | 13.825 | -0.288 | -14.999 | -34.923 | BSP | 173
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - System Transformation | 33.555 | 25.263 | 17.935 | 2.105 | -6.4 | -15.432 | -25.124 | -118.081 | -184.355 | -252.626 | -342.003 | BSP | 174
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - System Transformation | 90.193 | 89.703 | 89.074 | 88.356 | 87.649 | 86.906 | 86.105 | 82.112 | 76.936 | 71.283 | 63.711 | BSP | 175
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - System Transformation | 53.232 | 52.28 | 51.091 | 49.703 | 48.228 | 46.623 | 44.843 | 34.763 | 16.481 | -3.151 | -28.014 | BSP | 176
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - System Transformation | 40.54 | 37.601 | 34.879 | 31.803 | 28.633 | 25.24 | 21.558 | 2.037 | -22.171 | -45.276 | -73.541 | BSP | 177
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - System Transformation | 62.824 | 62.677 | 62.372 | 61.959 | 61.605 | 61.198 | 60.7 | 57.761 | 50.958 | 43.006 | 31.898 | BSP | 178
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 41.864 | 41.546 | 41.09 | 40.545 | 40.014 | 39.44 | 38.797 | 35.447 | 30.026 | 24.655 | 17.63 | BSP | 179
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - System Transformation | 17.039 | 16.284 | 15.226 | 13.99 | 12.723 | 11.362 | 9.876 | 2.154 | -5.79 | -14.489 | -26.503 | BSP | 180
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - System Transformation | 57.378 | 55.731 | 53.551 | 51.093 | 48.789 | 46.392 | 43.854 | 31.534 | 17.291 | 0.114 | -25.133 | BSP | 181
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - System Transformation | 49.645 | 48.603 | 47.146 | 84.404 | 82.646 | 80.764 | 78.729 | 68.125 | 54.557 | 41.059 | 23.596 | BSP | 182
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - System Transformation | 37.545 | 35.099 | 33.57 | 31.717 | 29.886 | 27.925 | 25.764 | 14.473 | -4.482 | -24.646 | -52.43 | BSP | 183
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - System Transformation | 59.115 | 57.549 | 55.587 | 53.426 | 51.284 | 49.03 | 46.635 | 61.722 | 47.115 | 32.182 | 12.815 | BSP | 184
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - System Transformation | 88.917 | 88.403 | 87.652 | 86.754 | 85.891 | 84.996 | 84.047 | 79.476 | 72.853 | 65.009 | 53.553 | BSP | 185
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - System Transformation | 81.636 | 80.885 | 79.923 | 78.812 | 77.599 | 76.327 | 74.991 | 68.408 | 62.053 | 55.207 | 46.414 | BSP | 186
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - System Transformation | 90.815 | 89.961 | 88.932 | 87.834 | 86.731 | 85.577 | 84.348 | 78.31 | 70.671 | 62.395 | 51.183 | BSP | 187
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - System Transformation | 45.84 | 45.138 | 44.206 | 43.045 | 41.688 | 40.066 | 38.154 | 25.523 | 9.994 | -0.631 | -10.162 | BSP | 188
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - System Transformation | 55.486 | 54.459 | 53.202 | 51.803 | 50.381 | 48.869 | 47.233 | 38.619 | 27.456 | 15.927 | 1.662 | BSP | 189
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 62.451 | 62.488 | 62.495 | 62.506 | 62.494 | 62.444 | 62.333 | 61.428 | 57.206 | 52.819 | 47.184 | BSP | 190
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 32.52 | 27.258 | 22.507 | 19.156 | 15.83 | 12.389 | 8.828 | -8.065 | -27.216 | -50.744 | -84.787 | BSP | 191
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - System Transformation | 40.026 | 39.609 | 39.027 | 38.348 | 37.585 | 36.672 | 35.58 | 28.655 | 16.38 | 4.499 | -10.539 | BSP | 192
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - System Transformation | 53.459 | 51.13 | 48.737 | 46.673 | 44.609 | 42.455 | 40.184 | 29.344 | 15.193 | 0.318 | -20.027 | BSP | 193
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - System Transformation | 44.033 | 42.459 | 40.364 | 38.005 | 35.713 | 33.316 | 30.774 | 18.422 | 2.012 | -16.368 | -42.334 | BSP | 194
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - System Transformation | 113.042 | 110.771 | 110.2 | 109.415 | 108.497 | 107.285 | 105.699 | 69.476 | 50.137 | 32.867 | 12.322 | BSP | 195
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - System Transformation | 79.779 | 79.58 | 79.285 | 78.906 | 78.494 | 78.011 | 77.443 | 73.763 | 67.807 | 61.956 | 55.113 | BSP | 196
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - System Transformation | 67.599 | 66.393 | 65.045 | 63.748 | 62.504 | 61.2 | 59.797 | 53.101 | 43.73 | 33.647 | 19.898 | BSP | 197
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - System Transformation | 25.29 | 25.305 | 25.249 | 25.126 | 24.964 | 24.766 | 24.519 | 22.869 | 17.887 | 12.144 | 4.202 | BSP | 198
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - System Transformation | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | 25.87 | BSP | 199
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - System Transformation | 54.828 | 54.188 | 51.141 | 50.191 | 49.08 | 47.824 | 46.414 | 37.901 | 27.875 | 20.094 | 12.849 | BSP | 200
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - System Transformation | 48.914 | 45.411 | 43.365 | 41.373 | 39.47 | 37.478 | 35.356 | 25.144 | 12.888 | -0.916 | -20.364 | BSP | 201
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 4.249 | 3.978 | 3.496 | 2.871 | 2.266 | 1.569 | 0.749 | -4.359 | -14.055 | -25.651 | -42.262 | BSP | 202
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - System Transformation | 40.378 | 40.347 | 40.311 | 40.27 | 106.423 | 106.372 | 106.316 | 105.971 | 105.524 | 105.06 | 104.596 | BSP | 203
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 69.065 | 65.492 | 64.676 | 63.802 | 62.892 | 61.923 | 60.891 | 54.955 | 48.009 | 41.244 | 34.054 | BSP | 204
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - System Transformation | 54.167 | 53.246 | 52.179 | 50.957 | 49.621 | 48.129 | 46.451 | 36.263 | 22.094 | 10.099 | -2.04 | BSP | 205
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - System Transformation | 82.388 | 81.822 | 81.157 | 80.421 | 79.663 | 78.878 | 78.063 | 73.975 | 69.207 | 64.541 | 59.384 | BSP | 206
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - System Transformation | 23.563 | 19.605 | 17.471 | 15.058 | 12.636 | 10.076 | 7.316 | -6.532 | -27.094 | -48.333 | -76.961 | BSP | 207
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - System Transformation | 46.229 | 44.93 | 43.199 | 41.233 | 39.315 | 37.277 | 35.065 | 23.764 | 7.991 | -8.67 | -31.507 | BSP | 208
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - System Transformation | 44.852 | 42.406 | 41.105 | 39.516 | 37.916 | 36.152 | 34.166 | 23.302 | 8.976 | -5.561 | -24.823 | BSP | 209
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 27.421 | 25.626 | 23.191 | 20.365 | 17.434 | 14.317 | 10.961 | -6.174 | -23.679 | -43.421 | -70.81 | BSP | 210
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - System Transformation | 67.454 | 66.658 | 65.711 | 64.638 | 63.536 | 62.343 | 61.018 | 53.408 | 42.332 | 29.696 | 13.329 | BSP | 211
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - System Transformation | 33.492 | 31.316 | 28.684 | 25.833 | 22.947 | 19.915 | 16.689 | 0.463 | -15.965 | -34.525 | -59.517 | BSP | 212
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - System Transformation | 26.406 | 21.262 | 16.569 | 11.532 | 6.185 | 0.591 | -5.287 | -34.093 | -67.1 | -102.934 | -150.451 | BSP | 213
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - System Transformation | 53.581 | 47.953 | 45.34 | 42.761 | 40.162 | 37.464 | 34.647 | 21.539 | 7.973 | -7.143 | -28.206 | BSP | 214
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - System Transformation | 43.341 | 41.592 | 39.463 | 37.115 | 34.774 | 32.361 | 29.825 | 17.614 | 2.238 | -13.712 | -34.114 | BSP | 215
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - System Transformation | 56.463 | 55.759 | 54.727 | 53.491 | 52.229 | 50.887 | 49.443 | 42.091 | 30.376 | 17.459 | -0.496 | BSP | 216
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NPg Best View | 18.537 | 18.487 | 66.075 | 65.491 | 65.209 | 64.853 | 64.384 | 61.714 | 52.804 | 46.243 | 39.868 | BSP | 217
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NPg Best View | 31.518 | 30.017 | 27.742 | 24.999 | 23.131 | 21.107 | 18.689 | -10.593 | -33.873 | -51.336 | -67.949 | BSP | 218
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NPg Best View | 122.962 | 116.8 | 115.165 | 113.328 | 112.001 | 110.426 | 108.387 | 97.57 | 71.699 | 52.705 | 35.379 | BSP | 219
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NPg Best View | 9.687 | 7.175 | 4.439 | 1.079 | -1.074 | -3.382 | -6.166 | -19.69 | -50.353 | -74.445 | -97.808 | BSP | 220
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 68.513 | 66.058 | 64.637 | 62.885 | 61.764 | 60.546 | 59.05 | 51.777 | 36.304 | 24.906 | 14.294 | BSP | 221
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NPg Best View | 17.498 | 17.814 | 17.926 | 17.853 | 17.91 | 17.83 | 17.583 | 15.363 | 9.73 | 5.872 | 2.283 | BSP | 222
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NPg Best View | 30.211 | 29.024 | 27.329 | 25.34 | 23.773 | 22.089 | 20.101 | 76.264 | 59.325 | 46.231 | 33.941 | BSP | 223
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NPg Best View | 43.525 | 42.378 | 40.487 | 38.404 | 37.091 | 35.662 | 33.91 | 25.23 | 5.632 | -8.565 | -21.925 | BSP | 224
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 45.489 | 41.368 | 40.549 | 39.557 | 38.675 | 37.615 | 27.955 | -2.039 | -15.257 | -24.346 | -32.735 | BSP | 225
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NPg Best View | 71.219 | 69.19 | 68.267 | 67.053 | 66.394 | 65.685 | 64.783 | 60.67 | 47.534 | 37.031 | 26.961 | BSP | 226
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NPg Best View | 40.389 | 38.634 | 37.094 | 35.177 | 33.921 | 32.529 | 30.803 | 18.111 | -0.71 | -14.375 | -27.232 | BSP | 227
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NPg Best View | 35.808 | 28.483 | 21.105 | 4.604 | -2.155 | -9.588 | -18.49 | -104.624 | -190.07 | -254.31 | -313.723 | BSP | 228
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NPg Best View | 90.438 | 90.051 | 89.405 | 88.629 | 88.125 | 87.588 | 86.947 | 83.838 | 77.154 | 72.006 | 66.951 | BSP | 229
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NPg Best View | 53.994 | 53.43 | 52.311 | 50.947 | 49.731 | 48.41 | 46.899 | 39.071 | 17.736 | 0.049 | -16.849 | BSP | 230
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NPg Best View | 41.42 | 38.84 | 36.137 | 32.843 | 30.278 | 27.408 | 23.976 | 6.102 | -22.385 | -43.045 | -62.31 | BSP | 231
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NPg Best View | 63.192 | 63.206 | 62.836 | 62.295 | 62.096 | 61.864 | 61.55 | 59.94 | 50.395 | 42.997 | 35.868 | BSP | 232
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 42.147 | 41.965 | 41.544 | 40.978 | 40.624 | 40.227 | 39.717 | 37.054 | 30.341 | 25.309 | 20.588 | BSP | 233
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NPg Best View | 17.304 | 16.577 | 15.298 | 13.76 | 12.744 | 11.626 | 10.273 | 3.621 | -8.008 | -15.969 | -23.558 | BSP | 234
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NPg Best View | 58.06 | 56.604 | 54.263 | 51.437 | 49.878 | 48.199 | 46.147 | 36.361 | 14.758 | -1.194 | -16.51 | BSP | 235
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NPg Best View | 50.295 | 49.629 | 48.371 | 85.713 | 84.47 | 83.07 | 81.325 | 72.402 | 56.175 | 44.215 | 33.191 | BSP | 236
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NPg Best View | 38.262 | 36.178 | 34.719 | 32.751 | 31.507 | 30.131 | 28.389 | 19.19 | -6.309 | -26.247 | -45.016 | BSP | 237
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NPg Best View | 59.835 | 58.655 | 56.837 | 54.672 | 53.117 | 51.417 | 49.364 | 66.336 | 48.249 | 34.95 | 22.625 | BSP | 238
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NPg Best View | 89.17 | 88.769 | 88.024 | 87.062 | 86.502 | 85.905 | 85.159 | 81.642 | 71.803 | 64.107 | 56.873 | BSP | 239
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NPg Best View | 82.037 | 81.414 | 80.496 | 79.385 | 78.529 | 77.603 | 76.496 | 71.07 | 62.679 | 56.601 | 51 | BSP | 240
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NPg Best View | 91.37 | 90.756 | 89.797 | 88.669 | 87.921 | 87.093 | 86.063 | 80.949 | 70.376 | 62.381 | 54.812 | BSP | 241
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NPg Best View | 46.347 | 45.923 | 45.1 | 43.906 | 42.53 | 40.754 | 38.496 | 24.865 | 10.943 | 3.032 | -3.222 | BSP | 242
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NPg Best View | 56.129 | 55.423 | 54.283 | 52.913 | 51.889 | 50.76 | 49.412 | 42.655 | 30.059 | 20.432 | 11.195 | BSP | 243
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NPg Best View | 63.009 | 63.359 | 63.562 | 63.717 | 63.899 | 64.039 | 64.104 | 64.22 | 59.572 | 55.816 | 52.339 | BSP | 244
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NPg Best View | 35.836 | 31.904 | 27.371 | 23.888 | 21.53 | 19.026 | 16.033 | 2.622 | -26.543 | -48.574 | -68.699 | BSP | 245
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NPg Best View | 40.663 | 40.609 | 40.074 | 39.363 | 38.659 | 37.789 | 36.677 | 30.477 | 15.602 | 4.786 | -4.842 | BSP | 246
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NPg Best View | 55.182 | 53.708 | 51.784 | 49.995 | 48.793 | 47.468 | 45.764 | 37.289 | 18.887 | 5.002 | -7.449 | BSP | 247
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NPg Best View | 44.95 | 43.811 | 41.849 | 39.441 | 37.948 | 36.332 | 34.322 | 24.592 | 1.504 | -16.01 | -32.289 | BSP | 248
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NPg Best View | 114.013 | 112.24 | 111.762 | 110.784 | 110.052 | 108.931 | 107.33 | 72.015 | 50.085 | 34.785 | 21.184 | BSP | 249
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NPg Best View | 80.374 | 80.52 | 80.479 | 80.31 | 80.176 | 79.948 | 79.592 | 77.273 | 71.959 | 67.887 | 64.057 | BSP | 250
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NPg Best View | 68.396 | 67.539 | 66.257 | 64.896 | 64.068 | 63.174 | 62.062 | 56.814 | 44.152 | 34.732 | 25.893 | BSP | 251
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NPg Best View | 25.528 | 25.679 | 25.67 | 25.572 | 25.502 | 25.405 | 25.249 | 24.279 | 17.525 | 11.858 | 6.613 | BSP | 252
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NPg Best View | 25.883 | 25.893 | 25.901 | 25.907 | 25.912 | 25.916 | 25.917 | 25.918 | 25.918 | 25.918 | 25.918 | BSP | 253
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NPg Best View | 55.355 | 55.018 | 52.18 | 51.398 | 50.469 | 49.335 | 47.936 | 39.885 | 30.599 | 24.378 | 19.095 | BSP | 254
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NPg Best View | 49.987 | 46.941 | 44.947 | 42.826 | 41.548 | 40.166 | 38.452 | 30.386 | 12.908 | 0.169 | -11.757 | BSP | 255
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 4.516 | 4.313 | 3.613 | 2.699 | 2.192 | 1.605 | 0.882 | -3.111 | -17.222 | -28.213 | -38.8 | BSP | 256
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NPg Best View | 40.458 | 40.491 | 40.515 | 40.533 | 106.745 | 106.749 | 106.743 | 106.668 | 106.539 | 106.391 | 106.239 | BSP | 257
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NPg Best View | 69.445 | 66.09 | 65.383 | 64.568 | 63.739 | 62.823 | 61.752 | 56.892 | 51.519 | 47.15 | 43.103 | BSP | 258
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NPg Best View | 54.905 | 54.414 | 53.632 | 52.602 | 51.488 | 50.14 | 48.502 | 39.03 | 26.568 | 17.454 | 9.083 | BSP | 259
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NPg Best View | 82.79 | 82.474 | 82.023 | 81.49 | 81.008 | 80.492 | 79.893 | 76.919 | 72.115 | 68.152 | 64.448 | BSP | 260
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NPg Best View | 24.643 | 21.243 | 19.374 | 17.033 | 15.421 | 13.651 | 11.411 | 0.035 | -26.951 | -47.476 | -66.13 | BSP | 261
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NPg Best View | 46.998 | 46.043 | 44.375 | 42.297 | 40.998 | 39.55 | 37.733 | 28.442 | 7.388 | -8.363 | -22.983 | BSP | 262
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NPg Best View | 45.388 | 43.127 | 41.644 | 39.716 | 38.487 | 37.066 | 35.271 | 25.929 | 7.029 | -6.093 | -18.417 | BSP | 263
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 28.447 | 26.945 | 24.386 | 21.198 | 19.286 | 17.144 | 14.453 | 0.846 | -24.246 | -41.94 | -58.932 | BSP | 264
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NPg Best View | 67.917 | 67.234 | 66.162 | 64.848 | 63.971 | 63.002 | 61.889 | 55.841 | 41.549 | 30.176 | 18.933 | BSP | 265
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NPg Best View | 34.449 | 32.542 | 29.771 | 26.559 | 24.45 | 22.155 | 19.42 | 6.062 | -16.847 | -33.253 | -48.907 | BSP | 266
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NPg Best View | 28.041 | 23.465 | 18.738 | 13.409 | 9.194 | 4.717 | -0.539 | -25.396 | -70.475 | -104.254 | -135.284 | BSP | 267
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NPg Best View | 54.89 | 49.81 | 47.435 | 44.894 | 43.208 | 41.376 | 39.109 | 28.557 | 9.529 | -4.133 | -16.579 | BSP | 268
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NPg Best View | 44.112 | 42.764 | 40.844 | 38.588 | 36.905 | 35.146 | 33.085 | 23.171 | 4.882 | -9.535 | -23.331 | BSP | 269
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NPg Best View | 57.115 | 56.769 | 55.94 | 54.807 | 54.04 | 53.175 | 52.041 | 46.379 | 30.564 | 18.216 | 7.018 | BSP | 270
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Consumer Transformation | 13.052 | 12.781 | 12.536 | 12.446 | 12.428 | 12.407 | 12.37 | 12.158 | 10.56 | 9.256 | 8.025 | Primary | 271
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Consumer Transformation | 12.282 | 10.658 | 10.572 | 10.423 | 10.337 | 10.211 | 10.03 | 8.72 | 5.769 | 3.804 | 2.257 | Primary | 272
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Consumer Transformation | 11.495 | 11.216 | 10.843 | 10.389 | 9.916 | 9.427 | 8.856 | 6.25 | 1.67 | -1.921 | -5.084 | Primary | 273
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Consumer Transformation | 6.04 | 4.71 | 4.748 | 4.718 | 4.699 | 4.652 | 4.557 | 3.981 | 1.837 | 0.282 | -1.013 | Primary | 274
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 15.357 | 14.951 | 14.447 | 13.967 | 13.601 | 13.227 | 12.77 | 10.866 | 7.3 | 4.576 | 2.081 | Primary | 275
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 17.144 | 17.137 | 17.11 | 17.076 | 17.069 | 17.059 | 17.036 | 16.924 | 16.274 | 15.748 | 15.241 | Primary | 276
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Consumer Transformation | 9.011 | 8.478 | 7.756 | 6.928 | 6.331 | 5.719 | 5 | 1.837 | -3.833 | -8.12 | -12.214 | Primary | 277
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Consumer Transformation | 17.214 | 17.256 | 17.266 | 17.249 | 17.269 | 17.285 | 17.286 | 17.281 | 16.016 | 14.971 | 13.994 | Primary | 278
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Consumer Transformation | 1.043 | 0.852 | 0.573 | 0.231 | -0.08 | -0.404 | -0.791 | -2.572 | -6.547 | -9.76 | -12.652 | Primary | 279
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Consumer Transformation | 3.403 | 2.926 | 3.07 | 3.179 | 3.311 | 3.432 | 3.533 | 3.896 | 3.277 | 2.802 | 2.347 | Primary | 280
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Consumer Transformation | 11.999 | 11.752 | 11.379 | 10.929 | 10.617 | 10.292 | 9.896 | 9.218 | 6.091 | 3.703 | 1.389 | Primary | 281
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Consumer Transformation | 2.616 | 2.296 | 1.885 | 1.478 | 1.156 | 0.795 | 0.322 | -1.985 | -5.857 | -8.432 | -10.642 | Primary | 282
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Consumer Transformation | 3.331 | 3.327 | 3.312 | 3.288 | 3.27 | 3.249 | 3.22 | 3.068 | 2.743 | 2.494 | 2.269 | Primary | 283
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Consumer Transformation | 15.727 | 15.536 | 15.237 | 14.877 | 14.665 | 14.446 | 14.175 | 13.02 | 9.984 | 7.637 | 5.375 | Primary | 284
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Consumer Transformation | 13.069 | 12.559 | 12.52 | 12.459 | 12.44 | 12.418 | 12.385 | 12.215 | 11.338 | 10.593 | 9.861 | Primary | 285
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Consumer Transformation | 10.628 | 10.633 | 10.59 | 10.501 | 10.46 | 10.406 | 10.323 | 9.845 | 7.864 | 6.433 | 5.199 | Primary | 286
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Consumer Transformation | 15.567 | 15.225 | 14.741 | 14.179 | 13.748 | 13.296 | 12.751 | 10.214 | 6.313 | 3.61 | 1.223 | Primary | 287
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Consumer Transformation | 8.364 | 8.393 | 8.398 | 8.379 | 8.374 | 8.359 | 8.326 | 8.031 | 6.684 | 5.677 | 4.845 | Primary | 288
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Consumer Transformation | 5.835 | 5.704 | 5.505 | 5.243 | 5.068 | 4.884 | 4.668 | 3.603 | 0.06 | -2.978 | -5.928 | Primary | 289
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Consumer Transformation | 21.434 | 21.393 | 21.293 | 21.151 | 21.05 | 20.943 | 20.802 | 20.223 | 18.936 | 17.959 | 17.072 | Primary | 290
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Consumer Transformation | 3.689 | 3.56 | 3.395 | 3.207 | 3.088 | 2.964 | 2.827 | 2.114 | 0.247 | -1.377 | -2.985 | Primary | 291
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Consumer Transformation | 11.535 | 11.073 | 10.418 | 9.644 | 9.082 | 8.487 | 7.772 | 4.362 | -1.65 | -6.047 | -10.091 | Primary | 292
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Consumer Transformation | 9.37 | 8.918 | 8.309 | 7.66 | 7.17 | 6.658 | 6.026 | 3.464 | -1.12 | -4.545 | -7.636 | Primary | 293
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Consumer Transformation | 14.653 | 14.377 | 14.018 | 13.659 | 13.379 | 13.092 | 12.74 | 11.282 | 9.066 | 7.494 | 6.066 | Primary | 294
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Consumer Transformation | 3.012 | 2.969 | 2.815 | 2.575 | 2.475 | 2.342 | 2.145 | 0.884 | -2.749 | -5.294 | -7.553 | Primary | 295
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Consumer Transformation | 5.393 | 5.177 | 4.87 | 4.501 | 4.207 | 3.895 | 3.522 | 1.717 | -1.009 | -2.92 | -4.586 | Primary | 296
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 15.169 | 15.137 | 15.076 | 14.99 | 14.931 | 14.863 | 14.775 | 14.37 | 12.988 | 11.909 | 10.962 | Primary | 297
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 4.304 | 1.337 | 1.291 | 1.177 | 1.104 | 0.986 | 0.801 | -0.501 | -4.683 | -7.696 | -10.174 | Primary | 298
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Consumer Transformation | 7.45 | 7.347 | 7.156 | 6.887 | 6.701 | 6.477 | 6.192 | 4.384 | 0.353 | -2.483 | -4.888 | Primary | 299
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Consumer Transformation | 11.684 | 11.393 | 10.945 | 10.397 | 10.024 | 9.638 | 9.162 | 7.063 | 2.268 | -1.503 | -5.028 | Primary | 300
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Consumer Transformation | 5.797 | 5.359 | 4.702 | 3.911 | 3.31 | 2.672 | 1.889 | -1.853 | -8.905 | -14.133 | -18.798 | Primary | 301
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Consumer Transformation | 6.88 | 6.864 | 6.844 | 6.819 | 6.797 | 6.775 | 6.751 | 6.638 | 6.319 | 6.038 | 5.764 | Primary | 302
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Consumer Transformation | 3.7 | 3.664 | 3.612 | 3.55 | 3.492 | 3.429 | 3.349 | 2.938 | 2.218 | 1.673 | 1.188 | Primary | 303
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Consumer Transformation | 11.578 | 11.178 | 10.597 | 9.91 | 9.474 | 9.019 | 8.463 | 6.027 | 1.275 | -2.314 | -5.796 | Primary | 304
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 13.548 | 13.46 | 13.368 | 13.264 | 13.158 | 13.051 | 12.943 | 12.398 | 11.164 | 9.949 | 8.729 | Primary | 305
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Consumer Transformation | 4.614 | 4.499 | 4.338 | 4.151 | 4.005 | 3.855 | 3.675 | 2.901 | 1.773 | 0.953 | 0.195 | Primary | 306
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 9.41 | 9.078 | 8.57 | 7.964 | 7.553 | 7.122 | 6.578 | 4.224 | -0.679 | -4.372 | -7.834 | Primary | 307
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Consumer Transformation | 11.54 | 11.268 | 10.85 | 10.354 | 9.953 | 9.528 | 8.992 | 6.567 | 2.239 | -0.929 | -3.712 | Primary | 308
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Consumer Transformation | 9.323 | 9.357 | 9.339 | 9.278 | 9.293 | 9.293 | 9.266 | 8.992 | 7.247 | 5.929 | 4.713 | Primary | 309
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Consumer Transformation | 10.219 | 10.208 | 10.134 | 10.016 | 9.929 | 9.826 | 9.666 | 9.022 | 7.826 | 6.989 | 6.228 | Primary | 310
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Consumer Transformation | 17.455 | 17.277 | 17.028 | 16.735 | 16.501 | 16.251 | 15.947 | 14.501 | 12.601 | 11.393 | 10.407 | Primary | 311
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Consumer Transformation | 7.673 | 22.187 | 21.915 | 21.6 | 21.345 | 21.081 | 20.753 | 19.3 | 15.886 | 13.187 | 10.762 | Primary | 312
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Consumer Transformation | 10.132 | 9.702 | 9.075 | 8.319 | 7.706 | 7.084 | 6.349 | 20.361 | 14.197 | 9.2 | 4.539 | Primary | 313
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Consumer Transformation | 3.848 | 3.713 | 3.538 | 3.369 | 3.254 | 3.137 | 2.99 | 2.442 | 1.599 | 1.011 | 0.44 | Primary | 314
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Consumer Transformation | 5.872 | 4.918 | 3.756 | 2.614 | 1.653 | 0.651 | -0.536 | -5.228 | -11.654 | -16.315 | -20.294 | Primary | 315
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Consumer Transformation | 3.749 | 3.358 | 2.811 | 2.148 | 1.445 | 0.704 | -0.201 | -4.373 | -11.615 | -17.449 | -22.658 | Primary | 316
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Consumer Transformation | 5.022 | 4.435 | 3.594 | 2.59 | 1.787 | 0.962 | -0.018 | 19.749 | 11.713 | 5.345 | -0.562 | Primary | 317
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Consumer Transformation | 4.092 | 4.161 | 4.221 | 4.269 | 4.315 | 4.354 | 4.383 | 4.438 | 4.209 | 4.08 | 3.995 | Primary | 318
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Consumer Transformation | 7.95 | 7.495 | 6.808 | 5.968 | 5.324 | 4.62 | 3.752 | 16.23 | 8.888 | 3.889 | -0.336 | Primary | 319
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Consumer Transformation | 12.827 | 12.919 | 12.998 | 13.055 | 13.106 | 13.149 | 13.182 | 13.24 | 12.431 | 11.852 | 11.385 | Primary | 320
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Consumer Transformation | 9.528 | 9.679 | 9.821 | 9.952 | 10.075 | 10.192 | 10.303 | 10.754 | 10.857 | 10.951 | 11.038 | Primary | 321
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Consumer Transformation | 11.114 | 11.217 | 11.294 | 11.37 | 11.467 | 11.55 | 11.607 | 11.77 | 10.058 | 8.717 | 7.514 | Primary | 322
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Consumer Transformation | 9.024 | 9.095 | 9.139 | 9.165 | 9.211 | 9.249 | 9.267 | 9.333 | 8.57 | 7.99 | 7.445 | Primary | 323
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Consumer Transformation | 10.767 | 10.469 | 10.019 | 9.49 | 9.107 | 8.687 | 8.158 | 5.48 | 1.31 | -1.378 | -3.634 | Primary | 324
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Consumer Transformation | 5.101 | 5.039 | 4.949 | 4.846 | 4.739 | 4.628 | 4.491 | 3.935 | 3.6 | 3.423 | 3.301 | Primary | 325
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Consumer Transformation | 7.652 | 7.635 | 7.599 | 7.549 | 7.509 | 7.464 | 7.405 | 7.109 | 6.586 | 6.122 | 5.665 | Primary | 326
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Consumer Transformation | 13.023 | 12.516 | 11.878 | 11.247 | 10.752 | 10.238 | 9.604 | 6.808 | 1.618 | -2.263 | -5.711 | Primary | 327
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Consumer Transformation | 0.818 | 0.819 | 0.809 | 0.792 | 0.777 | 0.759 | 0.732 | 0.576 | 0.232 | -0.035 | -0.277 | Primary | 328
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Consumer Transformation | 2.402 | 2.17 | 1.867 | 1.527 | 1.252 | 0.967 | 0.623 | -0.846 | -2.836 | -4.289 | -5.65 | Primary | 329
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 9.586 | 9.369 | 9.02 | 8.584 | 8.301 | 7.99 | 7.601 | 5.669 | 2.185 | -0.154 | -2.285 | Primary | 330
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Consumer Transformation | 8.383 | 8.231 | 8.038 | 7.872 | 7.758 | 7.631 | 7.449 | 6.653 | 4.281 | 2.441 | 0.769 | Primary | 331
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Consumer Transformation | 5.194 | 4.882 | 4.46 | 3.977 | 3.627 | 3.261 | 2.826 | 0.822 | -3.211 | -6.379 | -9.387 | Primary | 332
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Consumer Transformation | 4.201 | 4.23 | 4.252 | 4.266 | 4.28 | 4.288 | 4.289 | 4.24 | 3.953 | 3.758 | 3.609 | Primary | 333
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Consumer Transformation | 21.91 | 21.723 | 21.464 | 21.186 | 21.012 | 20.833 | 20.609 | 19.643 | 17.012 | 14.965 | 13.055 | Primary | 334
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Consumer Transformation | 7.444 | 7.5 | 7.528 | 7.546 | 7.601 | 7.647 | 7.672 | 7.741 | 6.596 | 5.687 | 4.826 | Primary | 335
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Consumer Transformation | 12.954 | 12.591 | 12.153 | 11.759 | 11.452 | 11.133 | 10.733 | 9.034 | 5.762 | 3.284 | 1.07 | Primary | 336
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Consumer Transformation | 8.453 | 8.43 | 8.33 | 8.169 | 8.046 | 7.905 | 7.7 | 6.731 | 4.122 | 2.122 | 0.322 | Primary | 337
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Consumer Transformation | 2.12 | 1.32 | 0.239 | -0.909 | -1.686 | -2.491 | -3.48 | -7.752 | -15.78 | -21.656 | -27.099 | Primary | 338
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Consumer Transformation | 0.989 | 0.859 | 0.696 | 0.499 | 0.309 | 0.107 | -0.125 | -0.835 | -1.622 | -2.28 | -2.897 | Primary | 339
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Consumer Transformation | 2.866 | 2.756 | 2.599 | 2.395 | 2.217 | 2.016 | 1.776 | 0.345 | -2.557 | -4.774 | -6.718 | Primary | 340
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Consumer Transformation | 12.957 | 12.89 | 12.742 | 12.536 | 12.364 | 12.183 | 11.948 | 12.044 | 10.234 | 8.887 | 7.731 | Primary | 341
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Consumer Transformation | 14.47 | 14.262 | 14.92 | 14.491 | 14.187 | 13.871 | 13.472 | 11.745 | 8.019 | 5.128 | 2.421 | Primary | 342
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Consumer Transformation | 22.186 | 22.192 | 22.107 | 21.91 | 21.704 | 21.417 | 21.027 | 18.147 | 12.552 | 9.079 | 6.646 | Primary | 343
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Consumer Transformation | 9.79 | 9.497 | 9.091 | 8.613 | 8.225 | 7.82 | 7.34 | 12.12 | 7.92 | 4.589 | 1.487 | Primary | 344
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Consumer Transformation | 1.893 | 1.559 | 1.116 | 0.605 | 0.258 | -0.104 | -0.539 | -2.333 | -5.187 | -7.326 | -9.412 | Primary | 345
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Consumer Transformation | 7.966 | 7.58 | 6.945 | 6.16 | 5.713 | 5.254 | 4.684 | 2.258 | -4.237 | -9.371 | -14.383 | Primary | 346
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Consumer Transformation | 5.244 | 2.942 | 2.925 | 2.876 | 2.835 | 2.778 | 2.691 | 2.212 | 0.8 | -0.267 | -1.175 | Primary | 347
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Consumer Transformation | 7.447 | 6.97 | 6.283 | 5.494 | 4.907 | 4.298 | 3.543 | 0.326 | -5.144 | -9.165 | -12.859 | Primary | 348
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Consumer Transformation | 3.351 | 3.077 | 17.361 | 16.867 | 16.456 | 16.022 | 15.481 | 12.973 | 7.787 | 3.873 | 0.486 | Primary | 349
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Consumer Transformation | -0.464 | -0.609 | -0.813 | -1.058 | -1.266 | -1.478 | -1.731 | -2.84 | -5.017 | -6.814 | -8.511 | Primary | 350
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Consumer Transformation | 2.558 | 2.567 | 2.555 | 2.522 | 2.511 | 2.493 | 2.462 | 2.26 | 1.442 | 0.859 | 0.356 | Primary | 351
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Consumer Transformation | 10.336 | 10.038 | 9.576 | 9.02 | 8.604 | 8.175 | 7.645 | 5.432 | 1.296 | -1.809 | -4.643 | Primary | 352
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Consumer Transformation | 8.228 | 7.849 | 7.279 | 6.605 | 6.185 | 5.739 | 5.181 | 2.649 | -2.407 | -6.092 | -9.574 | Primary | 353
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Consumer Transformation | 11.222 | 11.097 | 10.892 | 10.641 | 10.452 | 10.247 | 9.985 | 8.738 | 6.826 | 5.522 | 4.361 | Primary | 354
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Consumer Transformation | 3.621 | 2.712 | 2.729 | 2.688 | 2.688 | 2.659 | 2.585 | 1.935 | -0.578 | -2.371 | -3.867 | Primary | 355
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Consumer Transformation | 14.901 | 14.822 | 14.708 | 14.554 | 14.413 | 14.251 | 14.057 | 12.818 | 10.309 | 8.478 | 6.919 | Primary | 356
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Consumer Transformation | 4.442 | 4.35 | 4.221 | 4.07 | 3.955 | 3.838 | 3.7 | 3.093 | 1.835 | 0.836 | -0.106 | Primary | 357
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Consumer Transformation | 2.05 | 1.978 | 1.864 | 1.726 | 1.629 | 1.528 | 1.401 | 0.861 | -0.439 | -1.445 | -2.37 | Primary | 358
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Consumer Transformation | 14.954 | 14.596 | 14.072 | 13.443 | 12.986 | 12.497 | 11.896 | 8.969 | 3.534 | -0.501 | -4.199 | Primary | 359
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Consumer Transformation | 2.735 | 2.577 | 4.286 | 3.902 | 3.582 | 3.235 | 2.78 | 0.725 | -4.091 | -7.869 | -11.278 | Primary | 360
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Consumer Transformation | 14.809 | 14.736 | 14.594 | 14.404 | 14.343 | 14.273 | 14.179 | 13.656 | 11.371 | 9.615 | 7.927 | Primary | 361
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Consumer Transformation | 4.417 | 4.309 | 4.162 | 3.991 | 3.841 | 3.686 | 3.502 | 2.691 | 1.267 | 0.156 | -0.859 | Primary | 362
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Consumer Transformation | 4.585 | 4.062 | 3.32 | 2.459 | 1.781 | 1.071 | 0.205 | -3.584 | -9.18 | -13.215 | -16.967 | Primary | 363
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Consumer Transformation | 11.533 | 11.142 | 10.6 | 9.983 | 9.536 | 9.077 | 8.525 | 6.186 | 2.245 | -0.739 | -3.632 | Primary | 364
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Consumer Transformation | 12.139 | 10.532 | 10.416 | 10.204 | 10.056 | 9.833 | 9.515 | 7.286 | 3.395 | 1.157 | -0.358 | Primary | 365
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Consumer Transformation | 0.81 | 0.412 | -0.017 | -0.343 | -0.621 | -0.905 | -1.255 | -2.657 | -4.15 | -5.057 | -5.812 | Primary | 366
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Consumer Transformation | 7.273 | 6.504 | 5.472 | 4.31 | 3.477 | 2.625 | 1.627 | -2.62 | -9.145 | -13.874 | -18.367 | Primary | 367
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Consumer Transformation | 9.176 | 9.174 | 9.165 | 9.151 | 9.138 | 9.121 | 9.098 | 8.966 | 8.79 | 8.617 | 8.443 | Primary | 368
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Consumer Transformation | 1.687 | 1.486 | 1.182 | 0.786 | 0.363 | -0.149 | -0.791 | -5.045 | -10.678 | -13.84 | -15.766 | Primary | 369
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Consumer Transformation | 10.342 | 9.912 | 9.378 | 8.863 | 8.518 | 8.157 | 7.713 | 5.636 | 0.584 | -3.316 | -6.912 | Primary | 370
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Consumer Transformation | 8.719 | 8.306 | 7.682 | 6.925 | 6.417 | 5.877 | 5.213 | 2.054 | -3.573 | -7.587 | -11.248 | Primary | 371
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Consumer Transformation | 1.328 | 1.231 | 1.093 | 0.919 | 0.755 | 0.564 | 0.33 | -1.118 | -3.006 | -4.139 | -4.941 | Primary | 372
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Consumer Transformation | 7.178 | 6.826 | 6.298 | 5.668 | 5.196 | 4.711 | 4.122 | 1.618 | -3.777 | -8.053 | -12.074 | Primary | 373
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Consumer Transformation | 0.945 | 0.904 | 0.781 | 0.599 | 0.533 | 0.453 | 0.331 | -0.248 | -2.593 | -4.357 | -5.969 | Primary | 374
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Consumer Transformation | 1.499 | 1.499 | 1.498 | 1.497 | 1.496 | 1.495 | 1.493 | 1.484 | 1.468 | 1.453 | 1.438 | Primary | 375
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 24.078 | 24.112 | 24.1 | 24.046 | 24.055 | 24.058 | 24.039 | 23.952 | 22.383 | 21.138 | 19.938 | Primary | 376
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 33.847 | 33.795 | 33.7 | 33.579 | 33.506 | 33.426 | 33.317 | 32.894 | 31.879 | 31.113 | 30.377 | Primary | 377
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 20.491 | 20.406 | 20.283 | 20.136 | 20.002 | 19.865 | 19.7 | 19.022 | 18.162 | 17.544 | 17 | Primary | 378
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 14.614 | 14.375 | 14.046 | 13.68 | 13.415 | 13.129 | 12.779 | 11.007 | 7.997 | 5.866 | 3.98 | Primary | 379
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Consumer Transformation | 13.516 | 13.189 | 12.737 | 13.197 | 12.691 | 12.178 | 11.579 | 9.048 | 5.208 | 2.362 | -0.144 | Primary | 380
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Consumer Transformation | 10.367 | 9.275 | 8.788 | 8.19 | 7.805 | 7.404 | 6.908 | 4.963 | 1.102 | -1.88 | -4.775 | Primary | 381
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Consumer Transformation | 1.431 | 15.19 | 14.868 | 14.488 | 14.108 | 13.69 | 13.183 | 10.513 | 6.62 | 3.848 | 1.574 | Primary | 382
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Consumer Transformation | 10.491 | 9.755 | 8.999 | 8.491 | 8.166 | 7.832 | 7.42 | 5.604 | 1.306 | -1.982 | -5.061 | Primary | 383
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Consumer Transformation | 15.372 | 15.34 | 15.294 | 15.235 | 15.2 | 15.163 | 15.121 | 14.883 | 13.995 | 13.182 | 12.372 | Primary | 384
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Consumer Transformation | 3.65 | 2.605 | 1.147 | -0.538 | -1.858 | -3.216 | -4.833 | -10.841 | -19.883 | -26.786 | -33.17 | Primary | 385
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Consumer Transformation | 5.989 | 5.248 | 4.309 | 3.377 | 2.733 | 2.077 | 1.288 | -1.911 | -6.958 | -10.452 | -13.703 | Primary | 386
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Consumer Transformation | 4.404 | 4.416 | 4.331 | 4.172 | 4.212 | 4.238 | 4.231 | 4.03 | 0.975 | -1.564 | -4.173 | Primary | 387
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 17.14 | 14.114 | 13.827 | 13.488 | 13.218 | 12.941 | 12.625 | 11.428 | 9.193 | 7.273 | 5.38 | Primary | 388
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Consumer Transformation | 14.752 | 14.722 | 14.671 | 14.598 | 14.529 | 14.445 | 14.344 | 13.665 | 12.282 | 11.272 | 10.419 | Primary | 389
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Consumer Transformation | 9.249 | 9.051 | 8.803 | 8.499 | 8.19 | 7.837 | 7.425 | 4.777 | 0.755 | -2.056 | -4.296 | Primary | 390
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Consumer Transformation | 11.721 | 11.707 | 11.634 | 11.513 | 11.483 | 11.447 | 11.387 | 11.099 | 8.896 | 7.112 | 5.366 | Primary | 391
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Consumer Transformation | 11.291 | 11.336 | 11.344 | 11.321 | 11.343 | 11.357 | 11.354 | 11.321 | 10.514 | 9.917 | 9.345 | Primary | 392
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 3.778 | 3.611 | 3.414 | 3.176 | 2.919 | 2.622 | 2.28 | 0.004 | -3.216 | -5.436 | -7.157 | Primary | 393
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Consumer Transformation | 14.724 | 14.644 | 14.513 | 14.343 | 14.267 | 14.178 | 14.069 | 13.361 | 11.196 | 9.517 | 7.953 | Primary | 394
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Consumer Transformation | 10.613 | 10.295 | 9.801 | 9.205 | 8.866 | 8.513 | 8.077 | 6.227 | 1.879 | -1.391 | -4.553 | Primary | 395
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Consumer Transformation | 9.487 | 9.366 | 9.131 | 8.817 | 8.698 | 8.562 | 8.382 | 7.385 | 3.754 | 1.002 | -1.589 | Primary | 396
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Consumer Transformation | 7.071 | 6.707 | 6.143 | 5.457 | 4.972 | 4.454 | 3.8 | 0.721 | -4.543 | -8.194 | -11.414 | Primary | 397
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Consumer Transformation | 4.379 | 3.895 | 3.224 | 2.462 | 1.879 | 1.256 | 0.504 | 14.159 | 8.844 | 5.097 | 1.84 | Primary | 398
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Consumer Transformation | 10.989 | 10.983 | 10.932 | 10.853 | 10.756 | 10.617 | 10.415 | 9.092 | 7.469 | 6.698 | 6.34 | Primary | 399
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Consumer Transformation | 15.358 | 15.033 | 14.53 | 13.918 | 13.569 | 13.212 | 12.776 | 10.935 | 6.736 | 3.508 | 0.322 | Primary | 400
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Consumer Transformation | 8.818 | 8.344 | 7.655 | 6.824 | 6.161 | 5.437 | 4.543 | -0.082 | -7.171 | -11.998 | -16.083 | Primary | 401
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Consumer Transformation | 3.271 | 3.153 | 2.991 | 3.303 | 3.149 | 2.99 | 2.798 | 1.942 | 0.589 | -0.46 | -1.438 | Primary | 402
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Consumer Transformation | 7.087 | 6.855 | 6.481 | 6.031 | 5.658 | 5.274 | 4.793 | 9.772 | 4.836 | 0.929 | -2.549 | Primary | 403
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Consumer Transformation | 4.124 | 3.915 | 3.61 | 3.263 | 3.046 | 2.824 | 2.553 | 1.425 | -0.772 | -2.43 | -4.06 | Primary | 404
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 12.309 | 12.297 | 12.258 | 12.194 | 12.162 | 12.124 | 12.07 | 11.764 | 10.681 | 9.783 | 8.911 | Primary | 405
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 25.325 | 25.288 | 25.229 | 25.148 | 25.098 | 25.045 | 24.981 | 24.652 | 23.41 | 22.382 | 21.39 | Primary | 406
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Consumer Transformation | 14.598 | 14.422 | 14.187 | 13.911 | 13.654 | 13.382 | 13.057 | 11.584 | 9.848 | 8.714 | 7.824 | Primary | 407
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Consumer Transformation | 12.689 | 12.75 | 12.787 | 12.799 | 12.823 | 12.842 | 12.846 | 12.844 | 11.855 | 11.071 | 10.35 | Primary | 408
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Consumer Transformation | 19.976 | 19.94 | 19.884 | 19.804 | 19.751 | 19.696 | 19.634 | 19.414 | 18.706 | 18.065 | 17.424 | Primary | 409
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Consumer Transformation | 6.863 | 6.51 | 5.97 | 5.319 | 4.902 | 4.471 | 3.94 | 1.96 | -1.379 | -3.778 | -6.085 | Primary | 410
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 21.09 | 21.088 | 21.007 | 20.864 | 20.818 | 20.756 | 20.651 | 20.082 | 17.488 | 15.493 | 13.619 | Primary | 411
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Consumer Transformation | 13.999 | 13.927 | 13.794 | 13.626 | 13.592 | 13.553 | 13.498 | 13.184 | 10.634 | 8.557 | 6.535 | Primary | 412
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Consumer Transformation | 4.246 | 4.146 | 3.991 | 3.807 | 3.692 | 3.571 | 3.418 | 2.732 | 1.381 | 0.387 | -0.555 | Primary | 413
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Consumer Transformation | 0.966 | 0.928 | 0.878 | 0.819 | 0.767 | 0.707 | 0.638 | 0.214 | -0.368 | -0.795 | -1.154 | Primary | 414
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Consumer Transformation | 16.23 | 16.156 | 16.026 | 15.846 | 15.725 | 15.586 | 15.416 | 14.448 | 11.868 | 9.879 | 8.069 | Primary | 415
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 22.15 | 21.943 | 21.626 | 21.243 | 20.932 | 20.609 | 20.208 | 18.475 | 15.26 | 12.846 | 10.734 | Primary | 416
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 26.319 | 26.217 | 26.059 | 25.866 | 25.738 | 25.605 | 25.442 | 24.732 | 22.932 | 21.517 | 20.209 | Primary | 417
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Consumer Transformation | 2.37 | 2.225 | 2.036 | 1.828 | 1.623 | 1.412 | 1.162 | 0.057 | -1.676 | -3.087 | -4.356 | Primary | 418
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Consumer Transformation | 2.285 | 2.072 | 1.771 | 1.398 | 1.187 | 0.951 | 0.667 | -1.013 | -5.693 | -9.411 | -12.958 | Primary | 419
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Consumer Transformation | 14.342 | 14.296 | 14.206 | 14.082 | 13.989 | 13.869 | 13.711 | 12.803 | 11.389 | 10.496 | 9.815 | Primary | 420
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Consumer Transformation | 4.588 | 4.498 | 4.364 | 4.208 | 4.093 | 3.973 | 3.826 | 3.186 | 1.728 | 0.571 | -0.485 | Primary | 421
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Consumer Transformation | 14.492 | 14.473 | 14.432 | 14.389 | 14.37 | 14.338 | 14.283 | 13.96 | 12.814 | 11.929 | 11.151 | Primary | 422
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Consumer Transformation | 9.128 | 9.257 | 9.365 | 9.451 | 9.547 | 9.632 | 9.703 | 10.901 | 10.44 | 10.158 | 9.939 | Primary | 423
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Consumer Transformation | 1.167 | 0.817 | 0.32 | -0.263 | -0.745 | -1.248 | -1.854 | -4.575 | -8.029 | -10.351 | -12.354 | Primary | 424
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 16.833 | 16.799 | 16.735 | 16.647 | 16.6 | 16.547 | 16.481 | 16.112 | 14.917 | 13.985 | 13.113 | Primary | 425
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 16.766 | 16.726 | 16.656 | 16.562 | 16.5 | 16.425 | 16.328 | 15.699 | 14.443 | 13.586 | 12.864 | Primary | 426
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Consumer Transformation | 4.384 | 3.962 | 3.37 | 2.679 | 2.13 | 1.554 | 0.86 | 12.537 | 7.628 | 3.918 | 0.544 | Primary | 427
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Consumer Transformation | 14.345 | 14.247 | 14.096 | 13.903 | 13.795 | 13.679 | 13.543 | 12.85 | 10.695 | 8.964 | 7.332 | Primary | 428
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Consumer Transformation | 7.796 | 7.204 | 6.459 | 5.728 | 5.098 | 4.449 | 3.645 | 17.265 | 11.59 | 7.283 | 3.449 | Primary | 429
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Consumer Transformation | 4.912 | 4.835 | 4.697 | 4.529 | 4.431 | 4.31 | 4.139 | 3.151 | -0.262 | -2.861 | -5.147 | Primary | 430
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Consumer Transformation | 10.362 | 10.059 | 9.568 | 8.956 | 8.541 | 8.116 | 7.597 | 5.342 | -0.542 | -5.288 | -9.786 | Primary | 431
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Consumer Transformation | 0.144 | 0.06 | -0.06 | -0.212 | -0.314 | -0.425 | -0.557 | -1.232 | -2.88 | -4.203 | -5.447 | Primary | 432
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Consumer Transformation | 13.268 | 12.956 | 12.5 | 11.979 | 11.586 | 11.175 | 10.665 | 8.409 | 4.305 | 1.275 | -1.47 | Primary | 433
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Consumer Transformation | 17.499 | 17.494 | 17.472 | 17.432 | 17.405 | 17.372 | 17.326 | 17.059 | 15.969 | 15.136 | 14.404 | Primary | 434
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Consumer Transformation | 12.596 | 12.376 | 12.078 | 11.735 | 11.563 | 11.383 | 11.174 | 10.139 | 7.297 | 4.95 | 2.525 | Primary | 435
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Consumer Transformation | 6.931 | 6.817 | 6.647 | 6.431 | 6.255 | 6.066 | 5.84 | 4.639 | 1.662 | -0.736 | -2.892 | Primary | 436
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Consumer Transformation | 9.406 | 9.291 | 9.096 | 8.83 | 8.65 | 8.434 | 8.163 | 6.34 | 1.959 | -1.327 | -4.179 | Primary | 437
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Consumer Transformation | 15.303 | 15.287 | 15.27 | 15.25 | 15.227 | 15.203 | 15.175 | 16.014 | 15.807 | 15.584 | 15.361 | Primary | 438
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Consumer Transformation | 16.38 | 16.287 | 16.129 | 15.927 | 15.749 | 15.561 | 15.321 | 14.268 | 12.216 | 10.668 | 9.294 | Primary | 439
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Consumer Transformation | 12.822 | 12.664 | 12.422 | 12.122 | 11.905 | 11.683 | 11.418 | 10.426 | 7.766 | 5.549 | 3.46 | Primary | 440
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Consumer Transformation | 10.34 | 9.824 | 9.229 | 8.728 | 8.428 | 8.118 | 7.736 | 6.118 | 2.416 | -0.362 | -3.033 | Primary | 441
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Consumer Transformation | 9.409 | 8.89 | 8.19 | 7.449 | 6.922 | 6.373 | 5.684 | 2.806 | -2.256 | -6.016 | -9.525 | Primary | 442
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Consumer Transformation | 2.197 | 2.245 | 2.284 | 2.314 | 2.345 | 2.37 | 2.387 | 2.421 | 2.232 | 2.127 | 2.06 | Primary | 443
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Consumer Transformation | 9.635 | 8.919 | 8.105 | 7.423 | 6.92 | 6.404 | 5.772 | 20.068 | 14.23 | 9.676 | 5.471 | Primary | 444
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Consumer Transformation | 4.567 | 4.384 | 4.09 | 3.691 | 3.422 | 3.108 | 2.716 | 0.38 | -5.301 | -9.565 | -13.367 | Primary | 445
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Consumer Transformation | 3.3 | 2.882 | 2.3 | 1.619 | 1.09 | 0.552 | -0.086 | -2.741 | -7.488 | -11.225 | -14.788 | Primary | 446
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Consumer Transformation | 23.136 | 23.115 | 23.008 | 22.826 | 22.783 | 22.73 | 22.644 | 22.197 | 19.126 | 16.669 | 14.327 | Primary | 447
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Consumer Transformation | 6.325 | 6.142 | 5.887 | 5.582 | 5.352 | 5.106 | 4.816 | 3.364 | 0.725 | -1.298 | -3.183 | Primary | 448
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Consumer Transformation | 6.75 | 6.741 | 6.724 | 6.702 | 6.689 | 6.675 | 6.655 | 6.567 | 6.381 | 6.245 | 6.119 | Primary | 449
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Consumer Transformation | 11.527 | 10.843 | 9.833 | 8.634 | 7.871 | 7.081 | 6.129 | 2.21 | -5.122 | -10.722 | -16.198 | Primary | 450
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Consumer Transformation | 21.177 | 21.216 | 21.217 | 21.171 | 21.09 | 20.951 | 20.749 | 19.12 | 17.092 | 16.203 | 15.913 | Primary | 451
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Consumer Transformation | 11.203 | 10.956 | 10.575 | 10.121 | 9.835 | 9.535 | 9.161 | 7.484 | 3.601 | 0.705 | -2.006 | Primary | 452
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Consumer Transformation | 12.645 | 12.514 | 12.305 | 12.009 | 11.676 | 11.258 | 10.735 | 7.335 | 2.114 | -1.142 | -3.357 | Primary | 453
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Consumer Transformation | 0.143 | 0.049 | -0.089 | -0.26 | -0.417 | -0.589 | -0.802 | -1.91 | -3.782 | -5.178 | -6.401 | Primary | 454
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Consumer Transformation | 6.88 | 1.007 | 0.651 | 0.237 | -0.088 | -0.425 | -0.829 | 6.082 | 3.323 | 1.332 | -0.481 | Primary | 455
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 456
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Consumer Transformation | 3.576 | 3.28 | 2.867 | 2.387 | 2.038 | 1.677 | 1.244 | -0.683 | -4.068 | -6.722 | -9.308 | Primary | 457
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Consumer Transformation | 12.389 | 12.192 | 11.896 | 11.528 | 11.188 | 10.768 | 10.228 | 6.573 | 1.011 | -2.193 | -4.308 | Primary | 458
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Consumer Transformation | 5.466 | 5.206 | 4.817 | 4.387 | 4.12 | 3.83 | 3.458 | 1.914 | -0.888 | -2.823 | -4.576 | Primary | 459
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Consumer Transformation | 0.973 | 0.728 | 0.433 | 0.176 | 0.01 | -0.161 | -0.375 | -1.237 | -2.722 | -3.759 | -4.763 | Primary | 460
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Consumer Transformation | 12.662 | 12.504 | 12.233 | 11.891 | 11.711 | 11.517 | 11.263 | 10.111 | 7.194 | 5 | 2.915 | Primary | 461
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Consumer Transformation | 7.188 | 7.25 | 7.294 | 7.326 | 7.365 | 7.396 | 7.408 | 7.435 | 6.179 | 5.199 | 4.325 | Primary | 462
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Consumer Transformation | 13.482 | 13.413 | 13.276 | 13.083 | 13.022 | 12.952 | 12.857 | 12.321 | 9.858 | 7.936 | 6.072 | Primary | 463
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Consumer Transformation | 6.917 | 6.518 | 5.971 | 5.337 | 4.779 | 4.197 | 3.495 | 0.344 | -4.02 | -7.324 | -10.33 | Primary | 464
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Consumer Transformation | 9.736 | 9.693 | 9.558 | 9.341 | 9.204 | 9.003 | 8.72 | 6.623 | 2.95 | 0.787 | -0.746 | Primary | 465
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Consumer Transformation | 14.74 | 14.777 | 14.809 | 14.835 | 14.861 | 14.886 | 14.908 | 14.995 | 14.874 | 14.78 | 14.693 | Primary | 466
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Consumer Transformation | 5.552 | 5.531 | 5.494 | 5.45 | 5.425 | 5.397 | 5.357 | 5.181 | 4.891 | 4.687 | 4.477 | Primary | 467
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Consumer Transformation | 14.005 | 14.041 | 14.053 | 14.037 | 14.038 | 14.035 | 14.019 | 13.937 | 12.793 | 11.908 | 11.111 | Primary | 468
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Consumer Transformation | 3.989 | 3.669 | 3.171 | 2.561 | 2.187 | 1.799 | 1.324 | -0.677 | -4.684 | -7.628 | -10.412 | Primary | 469
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Consumer Transformation | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary | 470
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Consumer Transformation | 8.695 | 7.583 | 6.883 | 6.06 | 5.465 | 4.857 | 4.129 | 1.087 | -5.129 | -10.009 | -14.575 | Primary | 471
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Consumer Transformation | 8.631 | 7.995 | 7.118 | 6.166 | 22.658 | 22.029 | 21.251 | 17.963 | 11.951 | 7.507 | 3.188 | Primary | 472
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Consumer Transformation | 3.25 | 3.346 | 3.413 | 3.443 | 3.469 | 3.485 | 3.48 | 3.361 | 1.523 | 0.019 | -1.3 | Primary | 473
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Consumer Transformation | 1.829 | 1.503 | 1.043 | 0.491 | -0.076 | -0.655 | -1.344 | -4.24 | -9.495 | -13.785 | -17.586 | Primary | 474
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Consumer Transformation | 14.378 | 14.188 | 13.908 | 13.586 | 13.338 | 13.082 | 12.766 | 11.401 | 8.165 | 5.615 | 3.288 | Primary | 475
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Consumer Transformation | 5.59 | 5.072 | 4.289 | 3.346 | 2.72 | 2.061 | 1.255 | -2.37 | -8.738 | -13.399 | -17.893 | Primary | 476
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Consumer Transformation | 4.896 | 3.902 | 3.525 | 3.128 | 2.864 | 2.574 | 2.195 | 0.378 | -3.586 | -6.495 | -9.098 | Primary | 477
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Consumer Transformation | 14.913 | 14.695 | 14.371 | 14.001 | 13.784 | 13.559 | 13.276 | 12.192 | 9.868 | 8.07 | 6.308 | Primary | 478
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Consumer Transformation | 3.481 | 3.151 | 2.65 | 2.055 | 1.665 | 1.249 | 0.723 | 13.002 | 8.38 | 5.03 | 1.914 | Primary | 479
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Consumer Transformation | 6.748 | 6.486 | 6.121 | 5.672 | 5.364 | 5.03 | 4.639 | 2.497 | -1.993 | -5.349 | -8.436 | Primary | 480
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Consumer Transformation | 8.212 | 7.741 | 7.06 | 6.258 | 5.719 | 5.161 | 4.482 | 1.583 | -3.244 | -6.607 | -9.819 | Primary | 481
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Consumer Transformation | 5.881 | 5.499 | 4.974 | 4.371 | 3.844 | 3.306 | 2.666 | -0.021 | -3.535 | -6.002 | -8.139 | Primary | 482
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Consumer Transformation | 1.022 | 0.201 | -0.772 | -1.635 | -2.34 | -3.066 | -3.966 | -7.806 | -15.382 | -21.197 | -26.311 | Primary | 483
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Consumer Transformation | 9.643 | 9.085 | 8.356 | 7.618 | 7.18 | 6.728 | 6.171 | 3.819 | -1.289 | -5.146 | -8.881 | Primary | 484
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Consumer Transformation | 10.587 | 10.065 | 9.393 | 8.726 | 8.214 | 7.664 | 6.975 | 3.638 | -1.771 | -5.47 | -8.637 | Primary | 485
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Consumer Transformation | 12.37 | 12.379 | 12.337 | 12.24 | 12.175 | 12.076 | 11.933 | 10.785 | 8.066 | 6.36 | 5.101 | Primary | 486
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Consumer Transformation | 8.581 | 8.453 | 8.256 | 8.018 | 7.84 | 7.651 | 7.409 | 6.324 | 3.974 | 2.159 | 0.496 | Primary | 487
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Consumer Transformation | 2.89 | 2.83 | 2.704 | 2.527 | 2.429 | 2.304 | 2.137 | 1.002 | -1.32 | -2.774 | -3.945 | Primary | 488
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Consumer Transformation | 12.824 | 12.593 | 12.235 | 11.805 | 11.521 | 11.226 | 10.86 | 9.306 | 5.938 | 3.37 | 0.946 | Primary | 489
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Consumer Transformation | 18.282 | 18.192 | 18.031 | 17.823 | 17.65 | 17.47 | 17.241 | 16.265 | 14.493 | 13.144 | 11.932 | Primary | 490
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Consumer Transformation | 15.444 | 15.337 | 15.169 | 14.955 | 14.855 | 14.75 | 14.628 | 14.022 | 11.806 | 10.003 | 8.184 | Primary | 491
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Consumer Transformation | 2.761 | 2.457 | 2.01 | 1.416 | 0.896 | 0.257 | -0.535 | -4.674 | -10.421 | -14.099 | -16.858 | Primary | 492
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Consumer Transformation | 9.818 | 9.875 | 9.896 | 9.877 | 9.889 | 9.888 | 9.864 | 9.626 | 8.008 | 6.825 | 5.796 | Primary | 493
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Consumer Transformation | 6.133 | 5.993 | 5.781 | 5.513 | 5.349 | 5.16 | 4.929 | 3.683 | 1.046 | -0.904 | -2.633 | Primary | 494
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Consumer Transformation | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary | 495
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Consumer Transformation | 6.743 | 6.151 | 5.383 | 4.588 | 4.065 | 3.51 | 2.819 | -0.191 | -5.084 | -8.535 | -11.791 | Primary | 496
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Consumer Transformation | 14.343 | 14.022 | 13.544 | 12.965 | 12.631 | 12.283 | 11.86 | 9.964 | 5.867 | 2.701 | -0.414 | Primary | 497
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Consumer Transformation | 3.101 | 2.929 | 2.693 | 2.42 | 2.216 | 2.006 | 1.754 | 0.694 | -1.168 | -2.646 | -4.083 | Primary | 498
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Consumer Transformation | 8.807 | 8.513 | 8.094 | 7.543 | 7.058 | 6.459 | 5.725 | 0.519 | -7.787 | -12.938 | -16.719 | Primary | 499
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Consumer Transformation | 13.018 | 12.504 | 11.885 | 11.301 | 10.879 | 10.441 | 9.899 | 7.546 | 3.269 | 0.084 | -2.894 | Primary | 500
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Consumer Transformation | 4.978 | 4.884 | 4.753 | 4.602 | 4.482 | 4.359 | 4.213 | 3.583 | 2.341 | 1.34 | 0.411 | Primary | 501
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Consumer Transformation | 6.013 | 5.52 | 4.822 | 3.999 | 3.406 | 2.797 | 2.068 | -0.981 | -7.151 | -12.052 | -16.801 | Primary | 502
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Consumer Transformation | 9.926 | 9.602 | 9.091 | 8.47 | 8.05 | 7.616 | 7.081 | 4.905 | -0.043 | -3.865 | -7.383 | Primary | 503
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Consumer Transformation | 15.523 | 15.207 | 14.809 | 14.417 | 14.11 | 13.799 | 13.426 | 11.917 | 8.978 | 6.725 | 4.681 | Primary | 504
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Consumer Transformation | 6.052 | 5.821 | 5.421 | 4.907 | 4.615 | 4.302 | 3.902 | 2.173 | -2.006 | -5.116 | -8.055 | Primary | 505
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Consumer Transformation | 12.886 | 12.435 | 11.841 | 11.16 | 10.492 | 9.79 | 8.95 | 5.199 | -0.223 | -4.304 | -7.844 | Primary | 506
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Consumer Transformation | 12.779 | 12.719 | 12.612 | 12.464 | 12.402 | 12.334 | 12.25 | 11.872 | 10.376 | 9.167 | 7.991 | Primary | 507
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Consumer Transformation | 9.269 | 8.884 | 8.343 | 7.731 | 7.308 | 6.855 | 6.303 | 3.797 | -0.043 | -2.668 | -5.061 | Primary | 508
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Consumer Transformation | 11.378 | 11.401 | 11.373 | 11.294 | 11.24 | 11.155 | 11.025 | 10.06 | 8.054 | 6.841 | 5.96 | Primary | 509
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Consumer Transformation | 5.58 | 5.518 | 5.351 | 5.094 | 4.961 | 4.785 | 4.54 | 2.953 | -0.648 | -3.009 | -4.975 | Primary | 510
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Consumer Transformation | 28.572 | 28.492 | 28.363 | 28.192 | 28.054 | 27.894 | 27.696 | 26.521 | 24.601 | 23.322 | 22.279 | Primary | 511
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Consumer Transformation | 3.155 | 2.944 | 2.678 | 2.366 | 2.13 | 1.881 | 1.605 | 0.063 | -3.879 | -7.338 | -10.639 | Primary | 512
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Consumer Transformation | 1.898 | 1.858 | 1.797 | 1.723 | 1.66 | 1.595 | 1.515 | 1.168 | 0.718 | 0.372 | 0.045 | Primary | 513
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Consumer Transformation | 11.602 | 11.266 | 10.815 | 10.306 | 9.943 | 9.565 | 9.113 | 7.105 | 3.136 | 0.052 | -2.904 | Primary | 514
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Consumer Transformation | 9.904 | 9.912 | 9.874 | 9.797 | 9.781 | 9.751 | 9.694 | 9.323 | 7.743 | 6.553 | 5.463 | Primary | 515
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Consumer Transformation | 10.722 | 10.654 | 10.498 | 10.263 | 10.139 | 10.004 | 9.831 | 8.907 | 4.087 | 0.043 | -3.728 | Primary | 516
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Consumer Transformation | 1.808 | 1.741 | 1.644 | 1.517 | 1.419 | 1.307 | 1.174 | 0.46 | -0.929 | -1.962 | -2.871 | Primary | 517
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Consumer Transformation | 11.889 | 11.911 | 11.887 | 11.8 | 11.67 | 11.475 | 11.208 | 8.943 | 5.1 | 2.97 | 1.753 | Primary | 518
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Consumer Transformation | 15.668 | 15.62 | 15.544 | 15.464 | 15.415 | 15.355 | 15.268 | 14.795 | 13.564 | 12.697 | 11.934 | Primary | 519
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Consumer Transformation | 7.716 | 6.496 | 5.81 | 5.002 | 4.365 | 3.705 | 2.919 | -0.378 | -6.522 | -11.406 | -15.994 | Primary | 520
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Consumer Transformation | 11.956 | 11.848 | 11.656 | 11.417 | 11.249 | 11.074 | 10.845 | 9.887 | 7.66 | 5.944 | 4.388 | Primary | 521
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Consumer Transformation | 15.95 | 16.027 | 16.016 | 15.91 | 15.736 | 15.455 | 15.044 | 11.555 | 6.759 | 4.517 | 3.609 | Primary | 522
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Consumer Transformation | 8.707 | 8.303 | 7.669 | 6.906 | 6.475 | 6.019 | 5.443 | 2.782 | -3.341 | -7.881 | -12.184 | Primary | 523
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Consumer Transformation | 4.245 | 4.186 | 4.098 | 3.993 | 3.917 | 3.837 | 3.739 | 3.301 | 2.544 | 1.959 | 1.401 | Primary | 524
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Consumer Transformation | 8.767 | 8.355 | 7.798 | 7.214 | 6.886 | 6.541 | 6.106 | 4.257 | -0.057 | -3.282 | -6.31 | Primary | 525
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 14.463 | 14.298 | 14.038 | 13.7 | 13.475 | 13.229 | 12.933 | 11.397 | 7.582 | 4.551 | 1.694 | Primary | 526
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 13.453 | 13.334 | 13.131 | 12.842 | 12.647 | 12.43 | 12.17 | 10.68 | 6.004 | 2.179 | -1.426 | Primary | 527
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Consumer Transformation | 12.308 | 12.32 | 12.297 | 12.241 | 12.214 | 12.175 | 12.109 | 11.676 | 10.054 | 8.93 | 7.99 | Primary | 528
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Consumer Transformation | 8.127 | 8.165 | 8.158 | 8.113 | 8.143 | 8.168 | 8.179 | 8.188 | 6.876 | 5.794 | 4.721 | Primary | 529
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Consumer Transformation | 17.505 | 17.371 | 17.165 | 16.915 | 16.753 | 16.583 | 16.375 | 15.463 | 13.858 | 12.742 | 11.692 | Primary | 530
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Consumer Transformation | 4.959 | 4.962 | 4.95 | 4.921 | 4.884 | 4.833 | 4.766 | 4.247 | 3.294 | 2.543 | 1.905 | Primary | 531
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Consumer Transformation | 2.15 | 1.649 | 1.003 | 0.361 | -0.048 | -0.469 | -0.991 | -3.23 | -8.105 | -11.779 | -15.237 | Primary | 532
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Consumer Transformation | 11.44 | 11.026 | 10.489 | 9.939 | 9.539 | 9.129 | 8.63 | 6.521 | 2.176 | -1.125 | -4.156 | Primary | 533
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Consumer Transformation | 10 | 9.484 | 8.774 | 8.01 | 7.521 | 6.995 | 6.341 | 3.108 | -2.96 | -7.115 | -10.77 | Primary | 534
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 13.005 | 13.027 | 13.013 | 12.959 | 12.906 | 12.824 | 12.701 | 11.734 | 9.971 | 8.993 | 8.387 | Primary | 535
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Consumer Transformation | 16.033 | 15.814 | 15.472 | 15.06 | 14.801 | 14.532 | 14.198 | 12.786 | 10.06 | 8.042 | 6.118 | Primary | 536
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Consumer Transformation | 12.841 | 12.731 | 12.531 | 12.264 | 12.039 | 11.8 | 11.49 | 10.138 | 6.968 | 4.512 | 2.367 | Primary | 537
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Consumer Transformation | 9.381 | 9.124 | 8.717 | 8.221 | 7.892 | 7.531 | 7.072 | 4.792 | 0.528 | -2.403 | -4.992 | Primary | 538
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Consumer Transformation | 11.541 | 9.833 | 9.592 | 9.276 | 9.085 | 8.887 | 8.631 | 7.649 | 5.004 | 2.909 | 0.902 | Primary | 539
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Consumer Transformation | 4.113 | 3.987 | 3.817 | 3.629 | 3.468 | 3.3 | 3.096 | 2.217 | 0.859 | -0.156 | -1.077 | Primary | 540
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Consumer Transformation | 13.895 | 13.429 | 12.766 | 12.013 | 11.46 | 10.885 | 10.172 | 7.113 | 2.155 | -1.529 | -5.023 | Primary | 541
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Consumer Transformation | 2.146 | 1.783 | 1.203 | 0.499 | -0.034 | -0.587 | -1.278 | -4.194 | -10.682 | -15.71 | -20.25 | Primary | 542
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Consumer Transformation | 14.574 | 14.285 | 13.868 | 13.402 | 13.075 | 12.733 | 12.306 | 10.453 | 7.217 | 4.868 | 2.669 | Primary | 543
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Consumer Transformation | 7.596 | 7.139 | 6.484 | 5.743 | 5.266 | 4.772 | 4.163 | 1.567 | -4.003 | -8.237 | -12.338 | Primary | 544
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Consumer Transformation | 18.619 | 18.678 | 18.657 | 18.557 | 18.522 | 18.465 | 18.361 | 17.663 | 13.914 | 10.951 | 8.279 | Primary | 545
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Consumer Transformation | 12.532 | 12.379 | 12.165 | 11.923 | 11.719 | 11.504 | 11.239 | 10.045 | 8.075 | 6.748 | 5.658 | Primary | 546
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Consumer Transformation | 3.311 | 2.967 | 2.462 | 1.856 | 1.413 | 0.944 | 0.368 | -2.329 | -7.191 | -10.858 | -14.282 | Primary | 547
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Consumer Transformation | 3.371 | 2.435 | 1.211 | -0.163 | -1.574 | -3.028 | -4.752 | -12.227 | -22.07 | -29.43 | -35.625 | Primary | 548
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Consumer Transformation | 3.879 | 3.43 | 2.824 | 2.186 | 1.682 | 1.158 | 0.51 | 14.953 | 9.429 | 5.056 | 1.097 | Primary | 549
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Consumer Transformation | 12.472 | 11.956 | 11.249 | 10.445 | 9.899 | 9.344 | 8.687 | 5.921 | 1.12 | -2.546 | -6.159 | Primary | 550
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Consumer Transformation | 21.734 | 18.78 | 18.889 | 18.975 | 19.054 | 19.131 | 19.206 | 19.4 | 19.199 | 19.037 | 18.895 | Primary | 551
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Consumer Transformation | 3.464 | 3.174 | 2.77 | 2.266 | 1.835 | 1.315 | 0.683 | -2.909 | -8.101 | -11.45 | -14.048 | Primary | 552
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Consumer Transformation | 12.599 | 12.471 | 12.249 | 11.973 | 11.899 | 11.815 | 11.701 | 11.093 | 7.843 | 5.183 | 2.5 | Primary | 553
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Consumer Transformation | 14.045 | 14.115 | 14.164 | 14.198 | 14.26 | 14.317 | 14.364 | 14.541 | 14.258 | 14.041 | 13.809 | Primary | 554
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Consumer Transformation | 15.001 | 15.046 | 15.067 | 15.061 | 15.082 | 15.098 | 15.1 | 15.088 | 14.293 | 13.666 | 13.07 | Primary | 555
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Consumer Transformation | 9.622 | 9.043 | 8.209 | 7.233 | 6.55 | 5.848 | 5.002 | 1.416 | -4.471 | -8.789 | -12.891 | Primary | 556
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Consumer Transformation | 15.789 | 15.7 | 15.563 | 15.386 | 15.304 | 15.213 | 15.105 | 14.457 | 12.016 | 9.988 | 8.025 | Primary | 557
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Consumer Transformation | 5.503 | 5.428 | 5.268 | 5.04 | 4.95 | 4.85 | 4.714 | 4.006 | 0.459 | -2.372 | -5.067 | Primary | 558
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Consumer Transformation | 13.995 | 13.813 | 13.53 | 13.186 | 12.93 | 12.659 | 12.32 | 10.812 | 8.059 | 6.097 | 4.333 | Primary | 559
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Consumer Transformation | 18.289 | 14.827 | 14.751 | 14.664 | 14.602 | 14.533 | 14.435 | 14.116 | 13.742 | 13.526 | 13.35 | Primary | 560
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Consumer Transformation | 11.555 | 11.318 | 10.991 | 10.629 | 10.383 | 10.125 | 9.813 | 8.386 | 5.905 | 4.078 | 2.329 | Primary | 561
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Consumer Transformation | 2.514 | 2.31 | 2.017 | 1.665 | 1.4 | 1.106 | 0.748 | -1.22 | -4.234 | -6.206 | -7.836 | Primary | 562
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Consumer Transformation | 10.876 | 10.49 | 9.955 | 9.38 | 9.021 | 8.652 | 8.197 | 6.343 | 3.099 | 0.74 | -1.633 | Primary | 563
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Consumer Transformation | 10.027 | 9.703 | 9.2 | 8.599 | 8.231 | 7.844 | 7.356 | 6.354 | 2.418 | -0.472 | -3.2 | Primary | 564
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Consumer Transformation | 5.756 | 5.549 | 5.239 | 4.818 | 4.437 | 3.989 | 3.445 | 0.376 | -5.232 | -9.309 | -12.66 | Primary | 565
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Consumer Transformation | 16.366 | 16.218 | 16.013 | 15.771 | 15.566 | 15.354 | 15.101 | 13.928 | 11.878 | 10.265 | 8.792 | Primary | 566
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Consumer Transformation | 8.851 | 7.05 | 6.578 | 5.981 | 5.556 | 5.073 | 4.499 | 8.174 | 1.172 | -4.03 | -8.521 | Primary | 567
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Consumer Transformation | 3.793 | 3.639 | 3.427 | 3.184 | 2.984 | 2.778 | 2.531 | 1.47 | -0.053 | -1.208 | -2.295 | Primary | 568
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Consumer Transformation | 14.348 | 14.031 | 13.553 | 12.985 | 12.578 | 12.157 | 11.64 | 9.472 | 6.033 | 3.634 | 1.445 | Primary | 569
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Consumer Transformation | -0.33 | -0.564 | -0.892 | -0.277 | -0.608 | -0.958 | -1.385 | -3.214 | -6.314 | -8.672 | -10.779 | Primary | 570
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Consumer Transformation | 9.18 | 8.836 | 8.34 | 7.758 | 7.314 | 6.852 | 6.295 | 3.804 | -1.124 | -4.964 | -8.571 | Primary | 571
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Consumer Transformation | 7.709 | 7.391 | 6.893 | 6.287 | 5.883 | 5.454 | 4.91 | 2.45 | -2.471 | -6.079 | -9.43 | Primary | 572
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Consumer Transformation | 4.98 | 4.486 | 3.782 | 2.945 | 2.332 | 1.693 | 0.922 | -2.446 | -9.236 | -14.59 | -19.748 | Primary | 573
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Consumer Transformation | 16.065 | 15.737 | 15.241 | 14.646 | 14.218 | 13.761 | 13.188 | 10.699 | 6.682 | 3.885 | 1.347 | Primary | 574
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Consumer Transformation | 7.887 | 7.935 | 7.928 | 7.87 | 7.869 | 7.85 | 7.801 | 7.388 | 5.445 | 4.072 | 2.897 | Primary | 575
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Consumer Transformation | 13.808 | 14.507 | 14.104 | 5.662 | 4.89 | 4.097 | 3.146 | 0.138 | -4.177 | -7.717 | -10.906 | Primary | 576
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Consumer Transformation | 10.928 | 10.475 | 9.836 | 9.083 | 8.462 | 7.818 | 7.049 | 3.629 | -1.68 | -5.583 | -9.101 | Primary | 577
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Consumer Transformation | 6.627 | 6.646 | 6.589 | 6.461 | 6.442 | 6.405 | 6.331 | 5.956 | 4.046 | 2.561 | 1.173 | Primary | 578
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Consumer Transformation | 11.735 | 11.303 | 10.685 | 9.969 | 9.488 | 8.995 | 8.391 | 5.85 | 1.225 | -2.211 | -5.487 | Primary | 579
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Consumer Transformation | 5.082 | 4.559 | 3.844 | 2.988 | 2.255 | 1.467 | 0.522 | -4.282 | -12.007 | -17.835 | -23.118 | Primary | 580
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Consumer Transformation | 10.367 | 10.465 | 10.556 | 10.636 | 10.711 | 10.782 | 10.849 | 11.136 | 11.03 | 10.955 | 10.891 | Primary | 581
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Consumer Transformation | 11.314 | 11.427 | 11.518 | 11.581 | 11.62 | 11.635 | 11.619 | 11.21 | 10.232 | 9.779 | 9.596 | Primary | 582
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Consumer Transformation | 2.512 | 2.599 | 2.675 | 2.739 | 2.802 | 2.859 | 2.907 | 3.087 | 2.843 | 2.692 | 2.576 | Primary | 583
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Consumer Transformation | 6.382 | 6.159 | 5.844 | 5.506 | 5.291 | 5.065 | 4.776 | 3.697 | 1.667 | 0.232 | -1.051 | Primary | 584
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Consumer Transformation | 0.596 | 0.394 | 0.134 | -0.148 | -0.4 | -0.663 | -0.978 | -2.444 | -4.537 | -6.064 | -7.388 | Primary | 585
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Consumer Transformation | 12.483 | 12.232 | 11.857 | 11.398 | 11.026 | 10.625 | 10.137 | 7.778 | 4.005 | 1.365 | -0.865 | Primary | 586
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Consumer Transformation | 12.914 | 11.021 | 11.036 | 10.993 | 10.937 | 10.852 | 10.719 | 10.134 | 8.592 | 7.483 | 6.585 | Primary | 587
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Consumer Transformation | 9.167 | 8.787 | 15.291 | 14.794 | 14.433 | 14.058 | 13.587 | 11.568 | 7.746 | 4.887 | 2.243 | Primary | 588
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Consumer Transformation | 10.089 | 9.968 | 9.789 | 9.558 | 9.422 | 9.264 | 9.075 | 7.793 | 4.363 | 1.7 | -0.722 | Primary | 589
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Consumer Transformation | 3.159 | 1.421 | 0.858 | 0.409 | 0.081 | -0.264 | -0.699 | -2.628 | -7.52 | -11.395 | -14.939 | Primary | 590
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Consumer Transformation | 12.591 | 12.569 | 12.522 | 12.455 | 12.428 | 12.398 | 12.359 | 12.124 | 11.041 | 10.091 | 9.14 | Primary | 591
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Consumer Transformation | 8.414 | 8.255 | 14.963 | 14.589 | 14.397 | 14.187 | 13.911 | 12.6 | 8.941 | 6.22 | 3.659 | Primary | 592
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Consumer Transformation | 4.912 | 3.606 | 2.883 | 2.292 | 1.813 | 1.301 | 0.672 | -2.2 | -7.209 | -10.895 | -14.163 | Primary | 593
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Consumer Transformation | 10.168 | 9.694 | 8.989 | 8.162 | 7.667 | 7.158 | 6.537 | 3.923 | -1.553 | -5.687 | -9.742 | Primary | 594
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Consumer Transformation | 10.291 | 10.128 | 7.723 | 7.329 | 6.969 | 6.508 | 5.927 | 2.155 | -2.956 | -5.91 | -7.876 | Primary | 595
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Consumer Transformation | 8.308 | 7.839 | 7.181 | 6.421 | 5.88 | 5.311 | 4.619 | 1.49 | -3.28 | -6.674 | -9.828 | Primary | 596
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Consumer Transformation | 6.814 | 4.769 | 4.08 | 3.326 | 2.843 | 2.335 | 1.704 | -0.742 | -5.74 | -9.511 | -13.031 | Primary | 597
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Consumer Transformation | 8.566 | 7.931 | 8.017 | 8.046 | 8.053 | 8.029 | 7.969 | 7.33 | 5.266 | 3.97 | 3.06 | Primary | 598
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Consumer Transformation | 18.762 | 18.74 | 18.682 | 18.583 | 18.469 | 18.314 | 18.11 | 16.594 | 14.314 | 13.095 | 12.407 | Primary | 599
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Consumer Transformation | 8.659 | 8.539 | 8.305 | 8.004 | 7.842 | 7.671 | 7.442 | 6.479 | 3.704 | 1.54 | -0.575 | Primary | 600
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Consumer Transformation | 10.724 | 10.559 | 10.305 | 9.994 | 9.671 | 9.324 | 8.894 | 6.868 | 3.526 | 1.001 | -1.101 | Primary | 601
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Consumer Transformation | 12.026 | 11.747 | 11.307 | 10.764 | 10.436 | 10.096 | 9.674 | 7.93 | 3.657 | 0.381 | -2.74 | Primary | 602
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Consumer Transformation | 12.305 | 12.288 | 12.219 | 12.111 | 12.079 | 12.033 | 11.963 | 11.521 | 9.798 | 8.571 | 7.453 | Primary | 603
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Consumer Transformation | 8.382 | 8.507 | 8.622 | 8.736 | 8.845 | 8.946 | 9.032 | 9.386 | 9.06 | 8.819 | 8.604 | Primary | 604
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Consumer Transformation | 8.061 | 6.234 | 6.039 | 5.791 | 5.726 | 5.638 | 5.504 | 4.644 | 1.465 | -0.903 | -3.115 | Primary | 605
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Consumer Transformation | 9.953 | 8.787 | 8.87 | 8.923 | 8.981 | 9.033 | 9.069 | 9.205 | 8.433 | 7.844 | 7.312 | Primary | 606
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Consumer Transformation | 1.194 | 0.979 | 0.686 | 0.346 | 0.084 | -0.189 | -0.52 | -1.976 | -4.478 | -6.445 | -8.332 | Primary | 607
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 2.858 | 2.816 | 2.747 | 2.671 | 2.657 | 2.64 | 2.614 | 2.484 | 1.573 | 0.837 | 0.066 | Primary | 608
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Consumer Transformation | 12.893 | 12.801 | 12.651 | 12.449 | 12.283 | 12.082 | 11.83 | 10.157 | 7.371 | 5.624 | 4.298 | Primary | 609
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Consumer Transformation | 24.496 | 24.549 | 24.593 | 24.617 | 24.635 | 24.65 | 24.663 | 24.677 | 24.05 | 23.473 | 22.911 | Primary | 610
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Consumer Transformation | 13.817 | 13.849 | 13.846 | 13.815 | 13.82 | 13.822 | 13.806 | 13.751 | 12.795 | 12.018 | 11.275 | Primary | 611
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Consumer Transformation | -1.724 | -1.826 | -1.979 | -2.181 | -2.344 | -2.522 | -2.734 | -3.906 | -6.333 | -8.282 | -10.065 | Primary | 612
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Consumer Transformation | 3.267 | 3.016 | 2.658 | 2.183 | 1.781 | 1.299 | 0.714 | -3.092 | -10.137 | -15.034 | -19.052 | Primary | 613
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Consumer Transformation | 10.983 | 10.799 | 10.482 | 10.087 | 9.839 | 9.582 | 9.255 | 7.891 | 4.681 | 2.256 | -0.035 | Primary | 614
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Consumer Transformation | 11.365 | 11.479 | 11.578 | 11.658 | 11.724 | 11.773 | 11.801 | 11.738 | 11.409 | 11.337 | 11.397 | Primary | 615
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Consumer Transformation | 8.092 | 7.668 | 7.041 | 6.29 | 5.753 | 5.183 | 4.488 | 1.178 | -5.269 | -10.019 | -14.284 | Primary | 616
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Consumer Transformation | 11.761 | 11.019 | 10.8 | 10.521 | 10.356 | 10.185 | 9.989 | 9.258 | 6.672 | 4.409 | 2.2 | Primary | 617
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Consumer Transformation | 4.022 | 3.672 | 3.232 | 2.804 | 2.457 | 2.105 | 1.678 | -0.078 | -3.578 | -6.307 | -8.761 | Primary | 618
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Consumer Transformation | 10.979 | 10.79 | 10.459 | 10.032 | 9.715 | 9.386 | 8.972 | 7.186 | 3.011 | -0.308 | -3.395 | Primary | 619
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Consumer Transformation | -1.253 | -1.458 | -1.751 | -2.09 | -0.32 | -0.558 | -0.848 | -2.114 | -5.224 | -7.673 | -9.99 | Primary | 620
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Consumer Transformation | 15.296 | 15.249 | 15.165 | 15.036 | 14.911 | 14.761 | 14.575 | 13.363 | 10.645 | 8.694 | 7.099 | Primary | 621
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Consumer Transformation | 14.301 | 13.6 | 12.898 | 12.439 | 12.058 | 11.656 | 11.159 | 8.807 | 4.551 | 1.433 | -1.259 | Primary | 622
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Consumer Transformation | 10.055 | 9.666 | 9.068 | 8.358 | 7.919 | 7.46 | 6.892 | 4.46 | 0.132 | -2.965 | -6.015 | Primary | 623
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Consumer Transformation | 23.77 | 23.817 | 23.86 | 23.902 | 23.945 | 23.983 | 24.016 | 24.15 | 23.949 | 23.791 | 23.645 | Primary | 624
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Consumer Transformation | 8.536 | 8.583 | 8.623 | 8.654 | 8.68 | 8.703 | 8.718 | 8.757 | 7.826 | 7.078 | 6.415 | Primary | 625
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Consumer Transformation | 11.258 | 10.951 | 10.469 | 9.884 | 9.53 | 9.166 | 8.715 | 6.849 | 3.09 | 0.268 | -2.522 | Primary | 626
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Consumer Transformation | 4.365 | 4.353 | 4.332 | 4.302 | 4.291 | 4.277 | 4.261 | 4.152 | 3.77 | 3.426 | 3.08 | Primary | 627
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Consumer Transformation | 8.841 | 8.737 | 8.586 | 8.397 | 8.27 | 8.133 | 7.974 | 7.124 | 4.906 | 3.08 | 1.323 | Primary | 628
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Consumer Transformation | 13.835 | 13.55 | 13.12 | 12.615 | 12.291 | 11.957 | 11.541 | 9.759 | 5.846 | 2.781 | -0.188 | Primary | 629
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Consumer Transformation | 10.748 | 10.43 | 9.983 | 9.454 | 9.069 | 8.669 | 8.196 | 6.205 | 2.569 | -0.167 | -2.676 | Primary | 630
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Consumer Transformation | 7.775 | 7.378 | 6.819 | 6.156 | 5.549 | 4.917 | 4.158 | 0.862 | -3.812 | -7.225 | -10.195 | Primary | 631
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Consumer Transformation | 13.085 | 12.849 | 12.556 | 12.207 | 11.892 | 11.546 | 11.152 | 8.957 | 4.919 | 1.738 | -1.082 | Primary | 632
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Consumer Transformation | 7.745 | 7.725 | 7.622 | 7.444 | 7.325 | 7.172 | 6.961 | 5.546 | 1.28 | -1.858 | -4.488 | Primary | 633
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Consumer Transformation | 13.753 | 13.488 | 13.082 | 12.6 | 12.31 | 12.009 | 11.636 | 10.071 | 6.815 | 4.367 | 1.95 | Primary | 634
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Consumer Transformation | 7.158 | 6.699 | 6.102 | 5.501 | 5.064 | 4.611 | 4.05 | 18.723 | 13.61 | 9.624 | 5.941 | Primary | 635
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Consumer Transformation | 7.478 | 7.321 | 7.1 | 6.814 | 6.61 | 6.385 | 6.122 | 4.636 | 0.715 | -2.464 | -5.481 | Primary | 636
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Falling Short | 13.258 | 13.144 | 13.066 | 13.028 | 12.974 | 12.906 | 12.839 | 12.538 | 12.315 | 12.158 | 12.017 | Primary | 637
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Falling Short | 12.218 | 10.599 | 10.566 | 10.502 | 10.4 | 10.26 | 10.089 | 9.026 | 7.732 | 6.822 | 6.5 | Primary | 638
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Falling Short | 11.455 | 11.165 | 10.83 | 10.443 | 9.996 | 9.495 | 9.001 | 6.672 | 4.678 | 3.254 | 2.136 | Primary | 639
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Falling Short | 5.901 | 4.525 | 4.545 | 4.527 | 4.474 | 4.391 | 4.293 | 3.765 | 3.166 | 2.762 | 2.609 | Primary | 640
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 15.57 | 15.372 | 15.153 | 14.917 | 14.622 | 14.271 | 13.938 | 12.619 | 11.849 | 11.451 | 11.215 | Primary | 641
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 17.119 | 17.119 | 17.114 | 17.104 | 17.084 | 17.055 | 17.027 | 16.903 | 16.812 | 16.753 | 16.711 | Primary | 642
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Falling Short | 9.108 | 8.783 | 8.404 | 7.971 | 7.459 | 6.879 | 6.314 | 3.777 | 1.642 | 0.067 | -1.171 | Primary | 643
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Falling Short | 17.141 | 17.169 | 17.187 | 17.189 | 17.176 | 17.151 | 17.126 | 17.02 | 16.915 | 16.844 | 16.791 | Primary | 644
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Falling Short | 1.013 | 0.842 | 0.634 | 0.385 | 0.087 | -0.255 | -0.592 | -2.121 | -3.345 | -4.198 | -4.838 | Primary | 645
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Falling Short | 3.204 | 2.645 | 2.724 | 2.783 | 2.826 | 2.857 | 2.882 | 2.925 | 2.861 | 2.798 | 2.747 | Primary | 646
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Falling Short | 11.991 | 11.852 | 11.673 | 11.451 | 11.178 | 10.86 | 10.55 | 10.231 | 9.202 | 8.471 | 7.933 | Primary | 647
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Falling Short | 2.721 | 2.575 | 2.407 | 2.206 | 1.935 | 1.599 | 1.254 | -0.415 | -1.981 | -2.991 | -3.454 | Primary | 648
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Falling Short | 3.284 | 3.258 | 3.227 | 3.19 | 3.148 | 3.101 | 3.051 | 2.812 | 2.566 | 2.343 | 2.154 | Primary | 649
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Falling Short | 15.767 | 15.697 | 15.597 | 15.467 | 15.296 | 15.092 | 14.897 | 14.101 | 13.568 | 13.27 | 13.081 | Primary | 650
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Falling Short | 12.952 | 12.402 | 12.341 | 12.269 | 12.187 | 12.096 | 12.004 | 11.567 | 11.141 | 10.73 | 10.321 | Primary | 651
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Falling Short | 10.545 | 10.553 | 10.544 | 10.511 | 10.453 | 10.375 | 10.291 | 9.833 | 9.319 | 8.966 | 8.79 | Primary | 652
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Falling Short | 15.618 | 15.412 | 15.158 | 14.854 | 14.484 | 14.051 | 13.621 | 11.632 | 9.967 | 8.848 | 8.168 | Primary | 653
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Falling Short | 8.301 | 8.312 | 8.312 | 8.301 | 8.276 | 8.239 | 8.196 | 7.907 | 7.545 | 7.293 | 7.193 | Primary | 654
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Falling Short | 5.673 | 5.5 | 5.306 | 5.083 | 4.834 | 4.564 | 4.293 | 2.978 | 1.751 | 0.706 | -0.266 | Primary | 655
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Falling Short | 21.394 | 21.363 | 21.31 | 21.233 | 21.13 | 21.004 | 20.881 | 20.386 | 20.086 | 19.914 | 19.804 | Primary | 656
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Falling Short | 3.597 | 3.457 | 3.308 | 3.15 | 2.98 | 2.799 | 2.617 | 1.704 | 0.799 | -0.044 | -0.84 | Primary | 657
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Falling Short | 11.547 | 11.239 | 10.871 | 10.44 | 9.923 | 9.328 | 8.733 | 5.881 | 3.304 | 1.409 | 0.065 | Primary | 658
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Falling Short | 9.566 | 9.339 | 9.069 | 8.756 | 8.358 | 7.884 | 7.423 | 5.651 | 4.53 | 3.897 | 3.569 | Primary | 659
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Falling Short | 14.743 | 14.58 | 14.396 | 14.19 | 13.938 | 13.643 | 13.36 | 12.19 | 11.473 | 11.082 | 10.811 | Primary | 660
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Falling Short | 2.902 | 2.906 | 2.874 | 2.801 | 2.68 | 2.514 | 2.329 | 1.25 | 0.003 | -0.866 | -1.245 | Primary | 661
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Falling Short | 5.333 | 5.151 | 4.935 | 4.684 | 4.389 | 4.05 | 3.709 | 2.057 | 0.508 | -0.699 | -1.561 | Primary | 662
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 15.152 | 15.124 | 15.087 | 15.033 | 14.961 | 14.874 | 14.781 | 14.392 | 14.063 | 13.841 | 13.725 | Primary | 663
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 4.16 | 1.162 | 1.126 | 1.045 | 0.913 | 0.733 | 0.521 | -0.717 | -2.146 | -3.138 | -3.551 | Primary | 664
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Falling Short | 7.332 | 7.235 | 7.104 | 6.931 | 6.711 | 6.446 | 6.155 | 4.474 | 2.561 | 1.126 | 0.325 | Primary | 665
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Falling Short | 11.753 | 11.595 | 11.387 | 11.131 | 10.812 | 10.436 | 10.072 | 8.553 | 7.556 | 6.98 | 6.602 | Primary | 666
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Falling Short | 5.834 | 5.563 | 5.219 | 4.799 | 4.277 | 3.659 | 3.044 | 0.206 | -2.167 | -3.764 | -4.705 | Primary | 667
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Falling Short | 6.867 | 6.847 | 6.825 | 6.802 | 6.776 | 6.748 | 6.721 | 6.589 | 6.461 | 6.346 | 6.237 | Primary | 668
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Falling Short | 3.66 | 3.617 | 3.567 | 3.509 | 3.441 | 3.364 | 3.286 | 2.881 | 2.473 | 2.138 | 1.88 | Primary | 669
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Falling Short | 11.669 | 11.492 | 11.262 | 10.976 | 10.62 | 10.202 | 9.794 | 8.047 | 6.705 | 5.82 | 5.224 | Primary | 670
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 13.345 | 13.153 | 12.957 | 12.754 | 12.546 | 12.336 | 12.123 | 11.04 | 9.89 | 8.718 | 7.53 | Primary | 671
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Falling Short | 4.636 | 4.564 | 4.479 | 4.381 | 4.263 | 4.128 | 3.998 | 3.438 | 3.008 | 2.706 | 2.481 | Primary | 672
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 9.495 | 9.351 | 9.156 | 8.907 | 8.582 | 8.192 | 7.816 | 6.249 | 5.168 | 4.551 | 4.183 | Primary | 673
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Falling Short | 11.609 | 11.463 | 11.27 | 11.025 | 10.706 | 10.319 | 9.94 | 8.299 | 7.093 | 6.396 | 6.079 | Primary | 674
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Falling Short | 9.218 | 9.242 | 9.249 | 9.237 | 9.204 | 9.152 | 9.092 | 8.723 | 8.282 | 7.966 | 7.799 | Primary | 675
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Falling Short | 10.149 | 10.148 | 10.124 | 10.073 | 9.989 | 9.878 | 9.769 | 9.327 | 9 | 8.809 | 8.706 | Primary | 676
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Falling Short | 17.487 | 17.383 | 17.252 | 17.094 | 16.897 | 16.664 | 16.428 | 15.319 | 14.304 | 13.595 | 13.199 | Primary | 677
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Falling Short | 7.725 | 22.316 | 22.181 | 22.015 | 21.805 | 21.555 | 21.315 | 20.307 | 19.634 | 19.256 | 19.025 | Primary | 678
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Falling Short | 10.13 | 9.798 | 9.397 | 8.926 | 8.368 | 7.733 | 7.122 | 21.691 | 19.902 | 18.652 | 17.616 | Primary | 679
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Falling Short | 3.898 | 3.842 | 3.777 | 3.705 | 3.612 | 3.5 | 3.394 | 3.001 | 2.778 | 2.663 | 2.596 | Primary | 680
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Falling Short | 6.35 | 5.831 | 5.243 | 4.598 | 3.81 | 2.889 | 1.979 | -1.49 | -3.654 | -4.948 | -5.717 | Primary | 681
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Falling Short | 3.68 | 3.306 | 2.859 | 2.33 | 1.7 | 0.98 | 0.271 | -2.992 | -5.704 | -7.645 | -9.083 | Primary | 682
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Falling Short | 5.019 | 4.579 | 4.051 | 3.433 | 2.703 | 1.871 | 1.059 | 21.609 | 18.907 | 16.944 | 15.41 | Primary | 683
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Falling Short | 4.005 | 4.033 | 4.056 | 4.071 | 4.078 | 4.08 | 4.075 | 3.992 | 3.832 | 3.699 | 3.626 | Primary | 684
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Falling Short | 8.003 | 7.752 | 7.418 | 6.998 | 6.465 | 5.823 | 5.16 | 18.822 | 15.619 | 13.44 | 12.398 | Primary | 685
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Falling Short | 12.712 | 12.754 | 12.789 | 12.81 | 12.821 | 12.824 | 12.822 | 12.724 | 12.516 | 12.364 | 12.3 | Primary | 686
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Falling Short | 9.372 | 9.445 | 9.511 | 9.569 | 9.62 | 9.666 | 9.708 | 9.842 | 9.89 | 9.905 | 9.905 | Primary | 687
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Falling Short | 10.951 | 11.006 | 11.054 | 11.088 | 11.097 | 11.088 | 11.073 | 10.925 | 10.684 | 10.512 | 10.408 | Primary | 688
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Falling Short | 8.911 | 8.95 | 8.98 | 8.997 | 8.998 | 8.987 | 8.974 | 8.891 | 8.788 | 8.716 | 8.668 | Primary | 689
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Falling Short | 10.854 | 10.731 | 10.559 | 10.338 | 10.043 | 9.676 | 9.298 | 7.435 | 5.641 | 4.46 | 3.971 | Primary | 690
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Falling Short | 5.08 | 5.022 | 4.952 | 4.869 | 4.769 | 4.653 | 4.542 | 4.068 | 3.717 | 3.451 | 3.234 | Primary | 691
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Falling Short | 7.437 | 7.326 | 7.205 | 7.075 | 6.932 | 6.779 | 6.624 | 5.828 | 5.009 | 4.183 | 3.351 | Primary | 692
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Falling Short | 13.287 | 13.039 | 12.761 | 12.455 | 12.068 | 11.608 | 11.162 | 9.307 | 8.062 | 7.372 | 7.02 | Primary | 693
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Falling Short | 0.747 | 0.719 | 0.686 | 0.647 | 0.602 | 0.551 | 0.498 | 0.212 | -0.102 | -0.396 | -0.655 | Primary | 694
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Falling Short | 2.452 | 2.307 | 2.139 | 1.945 | 1.713 | 1.448 | 1.192 | 0.081 | -0.776 | -1.378 | -1.843 | Primary | 695
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 9.601 | 9.532 | 9.417 | 9.254 | 9.036 | 8.765 | 8.488 | 7.086 | 5.617 | 4.576 | 4.012 | Primary | 696
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Falling Short | 8.423 | 8.358 | 8.29 | 8.214 | 8.102 | 7.961 | 7.824 | 7.249 | 6.826 | 6.575 | 6.423 | Primary | 697
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Falling Short | 5.166 | 4.933 | 4.668 | 4.366 | 4.013 | 3.616 | 3.22 | 1.404 | -0.175 | -1.394 | -2.349 | Primary | 698
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Falling Short | 4.163 | 4.174 | 4.183 | 4.186 | 4.185 | 4.179 | 4.17 | 4.087 | 3.965 | 3.879 | 3.844 | Primary | 699
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Falling Short | 21.976 | 21.894 | 21.796 | 21.681 | 21.53 | 21.349 | 21.176 | 20.473 | 20.023 | 19.78 | 19.627 | Primary | 700
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Falling Short | 7.346 | 7.384 | 7.417 | 7.439 | 7.444 | 7.437 | 7.428 | 7.351 | 7.228 | 7.14 | 7.078 | Primary | 701
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Falling Short | 13.152 | 12.98 | 12.797 | 12.603 | 12.354 | 12.055 | 11.768 | 10.622 | 9.921 | 9.552 | 9.343 | Primary | 702
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Falling Short | 8.381 | 8.369 | 8.331 | 8.258 | 8.145 | 7.999 | 7.854 | 7.185 | 6.639 | 6.329 | 6.187 | Primary | 703
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Falling Short | 2.459 | 2.099 | 1.67 | 1.175 | 0.547 | -0.2 | -0.927 | -3.917 | -5.921 | -7.062 | -7.674 | Primary | 704
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Falling Short | 0.942 | 0.792 | 0.629 | 0.445 | 0.24 | 0.016 | -0.213 | -0.91 | -1.309 | -1.648 | -1.922 | Primary | 705
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Falling Short | 2.67 | 2.495 | 2.301 | 2.08 | 1.829 | 1.551 | 1.258 | -0.365 | -2.172 | -3.723 | -4.914 | Primary | 706
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Falling Short | 12.931 | 12.889 | 12.813 | 12.703 | 12.551 | 12.363 | 12.181 | 12.502 | 12.088 | 11.868 | 11.768 | Primary | 707
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Falling Short | 14.51 | 14.418 | 15.282 | 15.1 | 14.865 | 14.581 | 14.309 | 13.194 | 12.479 | 12.113 | 11.914 | Primary | 708
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Falling Short | 22.062 | 22.048 | 21.993 | 21.875 | 21.687 | 21.427 | 21.105 | 18.913 | 16.05 | 14.063 | 13.438 | Primary | 709
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Falling Short | 9.728 | 9.478 | 9.187 | 8.853 | 8.464 | 8.027 | 7.594 | 12.583 | 10.861 | 9.537 | 8.472 | Primary | 710
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Falling Short | 1.99 | 1.821 | 1.614 | 1.365 | 1.063 | 0.714 | 0.369 | -1.025 | -2.067 | -2.771 | -3.234 | Primary | 711
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Falling Short | 7.999 | 7.833 | 7.595 | 7.287 | 6.895 | 6.429 | 5.983 | 4.164 | 3.052 | 2.454 | 2.057 | Primary | 712
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Falling Short | 5.189 | 2.869 | 2.849 | 2.81 | 2.751 | 2.674 | 2.588 | 2.165 | 1.744 | 1.459 | 1.324 | Primary | 713
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Falling Short | 7.612 | 7.387 | 7.095 | 6.737 | 6.282 | 5.741 | 5.219 | 3.086 | 1.668 | 0.863 | 0.397 | Primary | 714
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Falling Short | 3.421 | 3.256 | 17.74 | 17.474 | 17.133 | 16.726 | 16.325 | 14.556 | 13.227 | 12.448 | 12.055 | Primary | 715
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Falling Short | -0.481 | -0.6 | -0.739 | -0.901 | -1.09 | -1.303 | -1.51 | -2.412 | -3.117 | -3.654 | -4.112 | Primary | 716
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Falling Short | 2.519 | 2.527 | 2.528 | 2.518 | 2.499 | 2.471 | 2.439 | 2.252 | 2.026 | 1.87 | 1.799 | Primary | 717
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Falling Short | 10.381 | 10.217 | 9.996 | 9.718 | 9.368 | 8.951 | 8.552 | 6.93 | 5.924 | 5.39 | 5.067 | Primary | 718
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Falling Short | 8.324 | 8.176 | 7.974 | 7.716 | 7.384 | 6.985 | 6.591 | 4.852 | 3.453 | 2.578 | 2.098 | Primary | 719
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Falling Short | 11.148 | 11.047 | 10.918 | 10.759 | 10.563 | 10.331 | 10.098 | 8.972 | 7.927 | 7.133 | 6.562 | Primary | 720
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Falling Short | 3.457 | 2.498 | 2.503 | 2.477 | 2.414 | 2.317 | 2.201 | 1.482 | 0.617 | 0.01 | -0.232 | Primary | 721
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Falling Short | 14.789 | 14.68 | 14.557 | 14.41 | 14.241 | 14.048 | 13.84 | 12.596 | 11.097 | 9.865 | 9.037 | Primary | 722
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Falling Short | 4.439 | 4.374 | 4.296 | 4.205 | 4.098 | 3.976 | 3.857 | 3.333 | 2.921 | 2.619 | 2.372 | Primary | 723
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Falling Short | 2.063 | 2.028 | 1.979 | 1.916 | 1.833 | 1.735 | 1.64 | 1.253 | 1.003 | 0.866 | 0.779 | Primary | 724
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Falling Short | 14.974 | 14.75 | 14.475 | 14.142 | 13.734 | 13.256 | 12.775 | 10.497 | 8.489 | 7.072 | 6.172 | Primary | 725
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Falling Short | 2.716 | 2.623 | 4.479 | 4.279 | 4.01 | 3.682 | 3.359 | 1.954 | 0.914 | 0.331 | 0.015 | Primary | 726
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Falling Short | 14.783 | 14.77 | 14.741 | 14.692 | 14.622 | 14.534 | 14.443 | 13.986 | 13.539 | 13.236 | 13.059 | Primary | 727
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Falling Short | 4.42 | 4.336 | 4.237 | 4.122 | 3.985 | 3.83 | 3.678 | 3 | 2.46 | 2.078 | 1.791 | Primary | 728
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Falling Short | 4.66 | 4.358 | 3.982 | 3.531 | 2.974 | 2.323 | 1.689 | -1.091 | -3.268 | -4.742 | -5.734 | Primary | 729
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Falling Short | 11.592 | 11.377 | 11.115 | 10.804 | 10.426 | 9.991 | 9.57 | 7.783 | 6.478 | 5.59 | 4.908 | Primary | 730
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Falling Short | 12.028 | 10.436 | 10.398 | 10.306 | 10.148 | 9.92 | 9.631 | 7.823 | 5.556 | 3.95 | 3.423 | Primary | 731
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Falling Short | 1.069 | 0.885 | 0.706 | 0.539 | 0.324 | 0.066 | -0.177 | -1.14 | -1.748 | -2.089 | -2.286 | Primary | 732
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Falling Short | 7.472 | 7.038 | 6.524 | 5.935 | 5.235 | 4.434 | 3.656 | 0.283 | -2.407 | -4.353 | -5.846 | Primary | 733
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Falling Short | 9.053 | 8.993 | 8.93 | 8.862 | 8.79 | 8.713 | 8.634 | 8.217 | 7.768 | 7.299 | 6.825 | Primary | 734
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Falling Short | 1.715 | 1.574 | 1.385 | 1.137 | 0.807 | 0.387 | -0.098 | -3.167 | -6.942 | -9.589 | -10.502 | Primary | 735
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Falling Short | 10.552 | 10.347 | 10.126 | 9.889 | 9.589 | 9.233 | 8.882 | 7.335 | 6.175 | 5.475 | 5.082 | Primary | 736
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Falling Short | 8.779 | 8.566 | 8.286 | 7.939 | 7.504 | 6.988 | 6.472 | 4.096 | 2.11 | 0.793 | 0.053 | Primary | 737
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Falling Short | 1.262 | 1.16 | 1.04 | 0.898 | 0.726 | 0.525 | 0.304 | -0.984 | -2.479 | -3.643 | -4.306 | Primary | 738
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Falling Short | 7.205 | 6.984 | 6.706 | 6.369 | 5.953 | 5.47 | 5.005 | 3.063 | 1.715 | 0.836 | 0.166 | Primary | 739
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Falling Short | 0.865 | 0.857 | 0.826 | 0.765 | 0.669 | 0.543 | 0.414 | -0.162 | -0.688 | -1.05 | -1.257 | Primary | 740
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Falling Short | 1.493 | 1.49 | 1.486 | 1.483 | 1.479 | 1.475 | 1.47 | 1.448 | 1.424 | 1.399 | 1.373 | Primary | 741
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 23.957 | 23.979 | 23.983 | 23.964 | 23.924 | 23.869 | 23.812 | 23.547 | 23.299 | 23.13 | 22.995 | Primary | 742
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 33.831 | 33.813 | 33.782 | 33.735 | 33.67 | 33.59 | 33.512 | 33.206 | 32.988 | 32.858 | 32.775 | Primary | 743
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 20.483 | 20.416 | 20.334 | 20.236 | 20.117 | 19.981 | 19.85 | 19.302 | 18.914 | 18.643 | 18.428 | Primary | 744
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 14.623 | 14.468 | 14.285 | 14.075 | 13.82 | 13.521 | 13.217 | 11.718 | 10.338 | 9.34 | 8.717 | Primary | 745
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Falling Short | 13.541 | 13.27 | 12.947 | 13.572 | 13.131 | 12.632 | 12.15 | 10.01 | 8.329 | 7.186 | 6.289 | Primary | 746
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Falling Short | 10.409 | 9.476 | 9.279 | 9.024 | 8.7 | 8.317 | 7.947 | 6.538 | 5.648 | 5.108 | 4.746 | Primary | 747
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Falling Short | 1.402 | 15.187 | 14.938 | 14.648 | 14.302 | 13.9 | 13.482 | 11.342 | 9.189 | 7.575 | 6.603 | Primary | 748
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Falling Short | 11.019 | 10.698 | 10.421 | 10.195 | 9.908 | 9.566 | 9.237 | 7.892 | 7.038 | 6.568 | 6.289 | Primary | 749
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Falling Short | 15.259 | 15.18 | 15.098 | 15.01 | 14.916 | 14.819 | 14.72 | 14.202 | 13.656 | 13.111 | 12.561 | Primary | 750
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Falling Short | 3.794 | 3.091 | 2.254 | 1.279 | 0.114 | -1.221 | -2.519 | -7.258 | -10.324 | -12.44 | -14.014 | Primary | 751
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Falling Short | 6.363 | 6.048 | 5.689 | 5.293 | 4.796 | 4.207 | 3.644 | 1.402 | -0.15 | -1.116 | -1.765 | Primary | 752
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Falling Short | 4.281 | 4.322 | 4.341 | 4.334 | 4.301 | 4.247 | 4.185 | 3.832 | 3.477 | 3.237 | 3.074 | Primary | 753
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 17.08 | 14.064 | 13.836 | 13.578 | 13.29 | 12.978 | 12.67 | 11.472 | 10.535 | 9.73 | 8.987 | Primary | 754
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Falling Short | 14.624 | 14.544 | 14.453 | 14.348 | 14.227 | 14.093 | 13.948 | 13.089 | 12.08 | 11.218 | 10.58 | Primary | 755
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Falling Short | 9.018 | 8.731 | 8.419 | 8.072 | 7.684 | 7.252 | 6.784 | 4.03 | 0.772 | -1.979 | -3.884 | Primary | 756
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Falling Short | 11.638 | 11.646 | 11.637 | 11.605 | 11.552 | 11.484 | 11.416 | 11.096 | 10.821 | 10.655 | 10.533 | Primary | 757
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Falling Short | 11.198 | 11.23 | 11.248 | 11.251 | 11.239 | 11.214 | 11.187 | 11.049 | 10.905 | 10.803 | 10.739 | Primary | 758
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 3.519 | 3.239 | 2.94 | 2.614 | 2.257 | 1.864 | 1.437 | -1.107 | -4.157 | -6.795 | -8.695 | Primary | 759
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Falling Short | 14.64 | 14.564 | 14.476 | 14.373 | 14.252 | 14.116 | 13.97 | 13.159 | 12.262 | 11.509 | 10.944 | Primary | 760
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Falling Short | 10.679 | 10.574 | 10.421 | 10.216 | 9.947 | 9.624 | 9.311 | 8.035 | 7.135 | 6.606 | 6.307 | Primary | 761
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Falling Short | 9.457 | 9.429 | 9.373 | 9.285 | 9.161 | 9.006 | 8.844 | 8.032 | 7.25 | 6.726 | 6.447 | Primary | 762
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Falling Short | 7.156 | 6.987 | 6.753 | 6.452 | 6.061 | 5.585 | 5.114 | 2.981 | 1.27 | 0.24 | -0.222 | Primary | 763
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Falling Short | 4.417 | 4.109 | 3.742 | 3.313 | 2.787 | 2.171 | 1.546 | 15.836 | 13.505 | 11.791 | 10.723 | Primary | 764
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Falling Short | 10.935 | 10.926 | 10.896 | 10.84 | 10.745 | 10.607 | 10.441 | 9.421 | 8.181 | 7.32 | 7.056 | Primary | 765
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Falling Short | 15.439 | 15.313 | 15.137 | 14.91 | 14.627 | 14.292 | 13.972 | 12.682 | 11.904 | 11.487 | 11.219 | Primary | 766
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Falling Short | 8.885 | 8.606 | 8.252 | 7.816 | 7.269 | 6.616 | 5.943 | 2.57 | -0.656 | -2.869 | -3.963 | Primary | 767
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Falling Short | 3.261 | 3.17 | 3.065 | 3.443 | 3.302 | 3.142 | 2.985 | 2.284 | 1.71 | 1.273 | 0.92 | Primary | 768
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Falling Short | 7.111 | 6.968 | 6.772 | 6.522 | 6.197 | 5.806 | 5.431 | 10.923 | 10.006 | 9.527 | 9.24 | Primary | 769
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Falling Short | 4.169 | 4.072 | 3.947 | 3.796 | 3.61 | 3.391 | 3.181 | 2.321 | 1.782 | 1.472 | 1.253 | Primary | 770
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 12.175 | 12.117 | 12.048 | 11.966 | 11.871 | 11.765 | 11.655 | 11.09 | 10.488 | 9.93 | 9.423 | Primary | 771
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 25.285 | 25.252 | 25.212 | 25.161 | 25.1 | 25.032 | 24.963 | 24.61 | 24.242 | 23.942 | 23.696 | Primary | 772
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Falling Short | 14.562 | 14.392 | 14.192 | 13.961 | 13.69 | 13.383 | 13.074 | 11.662 | 10.499 | 9.676 | 9.101 | Primary | 773
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Falling Short | 12.59 | 12.62 | 12.641 | 12.647 | 12.641 | 12.626 | 12.611 | 12.51 | 12.38 | 12.295 | 12.235 | Primary | 774
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Falling Short | 19.891 | 19.806 | 19.714 | 19.609 | 19.495 | 19.376 | 19.255 | 18.823 | 18.489 | 18.166 | 17.844 | Primary | 775
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Falling Short | 6.914 | 6.755 | 6.535 | 6.252 | 5.898 | 5.48 | 5.076 | 3.568 | 2.559 | 1.925 | 1.477 | Primary | 776
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 20.962 | 20.967 | 20.947 | 20.896 | 20.811 | 20.699 | 20.583 | 19.997 | 19.421 | 19.021 | 18.768 | Primary | 777
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Falling Short | 13.981 | 13.963 | 13.936 | 13.896 | 13.839 | 13.772 | 13.704 | 13.383 | 13.115 | 12.947 | 12.811 | Primary | 778
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Falling Short | 4.276 | 4.236 | 4.18 | 4.108 | 4.015 | 3.903 | 3.793 | 3.326 | 2.997 | 2.812 | 2.721 | Primary | 779
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Falling Short | 0.862 | 0.779 | 0.691 | 0.597 | 0.496 | 0.386 | 0.271 | -0.361 | -1.068 | -1.731 | -2.3 | Primary | 780
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Falling Short | 16.102 | 16.003 | 15.886 | 15.742 | 15.571 | 15.376 | 15.169 | 14.087 | 12.914 | 11.948 | 11.247 | Primary | 781
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 22.208 | 22.097 | 21.946 | 21.755 | 21.51 | 21.217 | 20.934 | 19.773 | 19.02 | 18.611 | 18.39 | Primary | 782
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 26.341 | 26.292 | 26.226 | 26.142 | 26.036 | 25.909 | 25.787 | 25.292 | 24.987 | 24.827 | 24.727 | Primary | 783
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Falling Short | 2.353 | 2.215 | 2.059 | 1.885 | 1.684 | 1.458 | 1.238 | 0.253 | -0.527 | -1.13 | -1.645 | Primary | 784
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Falling Short | 2.214 | 2.069 | 1.9 | 1.699 | 1.463 | 1.195 | 0.914 | -0.643 | -2.359 | -3.74 | -4.722 | Primary | 785
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Falling Short | 14.262 | 14.205 | 14.131 | 14.036 | 13.914 | 13.764 | 13.594 | 12.722 | 11.783 | 11.056 | 10.663 | Primary | 786
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Falling Short | 4.616 | 4.57 | 4.511 | 4.437 | 4.344 | 4.232 | 4.126 | 3.695 | 3.426 | 3.282 | 3.196 | Primary | 787
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Falling Short | 14.476 | 14.463 | 14.446 | 14.423 | 14.384 | 14.33 | 14.27 | 13.978 | 13.698 | 13.508 | 13.419 | Primary | 788
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Falling Short | 8.973 | 9.038 | 9.092 | 9.134 | 9.163 | 9.182 | 9.192 | 10.131 | 9.932 | 9.773 | 9.713 | Primary | 789
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Falling Short | 1.227 | 1.009 | 0.737 | 0.412 | 0.016 | -0.445 | -0.898 | -2.932 | -4.571 | -5.678 | -6.377 | Primary | 790
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 16.79 | 16.759 | 16.719 | 16.669 | 16.606 | 16.532 | 16.456 | 16.062 | 15.658 | 15.336 | 15.098 | Primary | 791
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 16.716 | 16.678 | 16.628 | 16.566 | 16.488 | 16.394 | 16.291 | 15.686 | 14.982 | 14.432 | 14.107 | Primary | 792
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Falling Short | 4.435 | 4.156 | 3.823 | 3.431 | 2.959 | 2.416 | 1.878 | 14.289 | 12.477 | 11.191 | 10.318 | Primary | 793
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Falling Short | 14.285 | 14.197 | 14.094 | 13.974 | 13.834 | 13.678 | 13.519 | 12.759 | 12.032 | 11.438 | 10.96 | Primary | 794
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Falling Short | 8.09 | 7.77 | 7.409 | 7.007 | 6.502 | 5.906 | 5.333 | 20.03 | 18.637 | 17.899 | 17.463 | Primary | 795
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Falling Short | 4.872 | 4.83 | 4.768 | 4.68 | 4.553 | 4.39 | 4.213 | 3.306 | 2.388 | 1.765 | 1.463 | Primary | 796
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Falling Short | 10.37 | 10.189 | 9.95 | 9.651 | 9.281 | 8.847 | 8.431 | 6.692 | 5.532 | 4.825 | 4.308 | Primary | 797
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Falling Short | 0.087 | -0.003 | -0.104 | -0.217 | -0.346 | -0.487 | -0.632 | -1.364 | -2.136 | -2.803 | -3.347 | Primary | 798
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Falling Short | 13.365 | 13.219 | 13.027 | 12.789 | 12.481 | 12.11 | 11.749 | 10.216 | 9.129 | 8.506 | 8.194 | Primary | 799
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Falling Short | 17.468 | 17.463 | 17.45 | 17.426 | 17.391 | 17.348 | 17.302 | 17.05 | 16.778 | 16.592 | 16.491 | Primary | 800
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Falling Short | 12.564 | 12.426 | 12.268 | 12.09 | 11.889 | 11.669 | 11.447 | 10.35 | 9.281 | 8.378 | 7.581 | Primary | 801
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Falling Short | 6.878 | 6.746 | 6.593 | 6.417 | 6.213 | 5.984 | 5.749 | 4.569 | 3.466 | 2.624 | 1.992 | Primary | 802
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Falling Short | 9.286 | 9.158 | 9.004 | 8.818 | 8.594 | 8.33 | 8.041 | 6.343 | 4.396 | 2.873 | 1.955 | Primary | 803
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Falling Short | 15.17 | 15.089 | 15.005 | 14.919 | 14.83 | 14.739 | 14.645 | 15.145 | 14.599 | 14.021 | 13.43 | Primary | 804
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Falling Short | 16.376 | 16.321 | 16.242 | 16.134 | 15.991 | 15.82 | 15.653 | 14.938 | 14.42 | 14.124 | 13.964 | Primary | 805
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Falling Short | 12.793 | 12.675 | 12.532 | 12.359 | 12.151 | 11.912 | 11.682 | 10.845 | 10.294 | 9.889 | 9.541 | Primary | 806
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Falling Short | 10.647 | 10.444 | 10.245 | 10.052 | 9.801 | 9.501 | 9.211 | 8.04 | 7.264 | 6.826 | 6.559 | Primary | 807
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Falling Short | 9.634 | 9.413 | 9.147 | 8.837 | 8.437 | 7.957 | 7.497 | 5.674 | 4.527 | 3.913 | 3.573 | Primary | 808
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Falling Short | 2.136 | 2.159 | 2.177 | 2.189 | 2.195 | 2.195 | 2.192 | 2.139 | 2.041 | 1.967 | 1.939 | Primary | 809
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Falling Short | 10.087 | 9.752 | 9.42 | 9.094 | 8.685 | 8.202 | 7.74 | 22.883 | 21.735 | 21.117 | 20.737 | Primary | 810
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Falling Short | 4.44 | 4.286 | 4.095 | 3.855 | 3.559 | 3.212 | 2.837 | 0.761 | -1.551 | -3.323 | -4.399 | Primary | 811
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Falling Short | 3.355 | 3.086 | 2.762 | 2.383 | 1.932 | 1.42 | 0.928 | -1.11 | -2.554 | -3.535 | -4.315 | Primary | 812
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Falling Short | 23.044 | 23.052 | 23.038 | 22.993 | 22.921 | 22.828 | 22.734 | 22.291 | 21.886 | 21.63 | 21.457 | Primary | 813
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Falling Short | 6.135 | 5.919 | 5.678 | 5.408 | 5.103 | 4.765 | 4.423 | 2.684 | 0.913 | -0.637 | -1.957 | Primary | 814
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Falling Short | 6.75 | 6.747 | 6.741 | 6.734 | 6.723 | 6.71 | 6.698 | 6.644 | 6.606 | 6.585 | 6.574 | Primary | 815
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Falling Short | 11.639 | 11.31 | 10.882 | 10.358 | 9.715 | 8.968 | 8.239 | 5.294 | 3.226 | 1.863 | 0.898 | Primary | 816
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Falling Short | 21.097 | 21.107 | 21.093 | 21.049 | 20.965 | 20.835 | 20.656 | 19.367 | 17.617 | 16.372 | 16.021 | Primary | 817
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Falling Short | 11.264 | 11.161 | 11.021 | 10.842 | 10.607 | 10.324 | 10.047 | 8.851 | 7.957 | 7.423 | 7.124 | Primary | 818
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Falling Short | 12.574 | 12.423 | 12.23 | 11.982 | 11.663 | 11.266 | 10.8 | 8.041 | 4.776 | 2.401 | 1.406 | Primary | 819
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Falling Short | 0.081 | -0.017 | -0.131 | -0.266 | -0.426 | -0.611 | -0.801 | -1.768 | -2.74 | -3.509 | -4.052 | Primary | 820
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Falling Short | 6.879 | 1.119 | 0.895 | 0.633 | 0.322 | -0.034 | -0.382 | 6.753 | 5.552 | 4.733 | 4.119 | Primary | 821
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Falling Short | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 822
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Falling Short | 3.528 | 3.31 | 3.056 | 2.762 | 2.419 | 2.032 | 1.654 | -0.066 | -1.492 | -2.605 | -3.542 | Primary | 823
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Falling Short | 12.435 | 12.328 | 12.183 | 11.986 | 11.712 | 11.355 | 10.939 | 8.269 | 4.958 | 2.677 | 1.946 | Primary | 824
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Falling Short | 5.51 | 5.396 | 5.246 | 5.062 | 4.817 | 4.517 | 4.217 | 2.997 | 2.069 | 1.465 | 1.136 | Primary | 825
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Falling Short | 1.094 | 0.996 | 0.891 | 0.784 | 0.646 | 0.478 | 0.318 | -0.32 | -0.724 | -0.941 | -1.071 | Primary | 826
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Falling Short | 12.674 | 12.62 | 12.536 | 12.42 | 12.263 | 12.072 | 11.885 | 11.084 | 10.506 | 10.173 | 9.986 | Primary | 827
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Falling Short | 7.079 | 7.11 | 7.134 | 7.145 | 7.138 | 7.119 | 7.099 | 6.978 | 6.818 | 6.709 | 6.631 | Primary | 828
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Falling Short | 13.453 | 13.439 | 13.409 | 13.36 | 13.291 | 13.205 | 13.117 | 12.648 | 12.152 | 11.797 | 11.559 | Primary | 829
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Falling Short | 6.841 | 6.499 | 6.101 | 5.648 | 5.119 | 4.521 | 3.935 | 1.276 | -0.935 | -2.652 | -4.045 | Primary | 830
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Falling Short | 9.667 | 9.657 | 9.613 | 9.528 | 9.39 | 9.195 | 8.948 | 7.321 | 5.238 | 3.769 | 3.299 | Primary | 831
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Falling Short | 14.69 | 14.705 | 14.718 | 14.727 | 14.734 | 14.738 | 14.741 | 14.738 | 14.71 | 14.68 | 14.65 | Primary | 832
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Falling Short | 5.549 | 5.543 | 5.532 | 5.516 | 5.493 | 5.464 | 5.435 | 5.31 | 5.222 | 5.174 | 5.147 | Primary | 833
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Falling Short | 13.925 | 13.944 | 13.955 | 13.95 | 13.933 | 13.908 | 13.883 | 13.745 | 13.585 | 13.48 | 13.404 | Primary | 834
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Falling Short | 4.056 | 3.92 | 3.73 | 3.486 | 3.179 | 2.814 | 2.458 | 1.018 | 0.007 | -0.61 | -0.984 | Primary | 835
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Falling Short | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary | 836
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Falling Short | 8.799 | 7.881 | 7.526 | 7.103 | 6.588 | 5.991 | 5.416 | 3.07 | 1.509 | 0.532 | -0.194 | Primary | 837
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Falling Short | 8.881 | 8.632 | 8.323 | 7.957 | 24.593 | 24.041 | 23.512 | 21.363 | 19.965 | 19.184 | 18.716 | Primary | 838
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Falling Short | 3.11 | 3.143 | 3.159 | 3.153 | 3.127 | 3.085 | 3.039 | 2.757 | 2.44 | 2.231 | 2.115 | Primary | 839
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Falling Short | 1.845 | 1.566 | 1.222 | 0.813 | 0.323 | -0.24 | -0.78 | -3.025 | -4.535 | -5.493 | -6.227 | Primary | 840
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Falling Short | 14.428 | 14.327 | 14.197 | 14.037 | 13.831 | 13.585 | 13.349 | 12.379 | 11.747 | 11.399 | 11.194 | Primary | 841
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Falling Short | 5.632 | 5.385 | 5.055 | 4.641 | 4.126 | 3.518 | 2.921 | 0.23 | -1.976 | -3.492 | -4.503 | Primary | 842
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Falling Short | 4.963 | 4.095 | 3.93 | 3.735 | 3.476 | 3.157 | 2.833 | 1.37 | 0.195 | -0.541 | -0.91 | Primary | 843
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Falling Short | 14.971 | 14.883 | 14.768 | 14.625 | 14.443 | 14.224 | 14.014 | 13.248 | 12.816 | 12.577 | 12.423 | Primary | 844
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Falling Short | 3.567 | 3.443 | 3.27 | 3.046 | 2.751 | 2.392 | 2.037 | 15.165 | 13.895 | 13.118 | 12.744 | Primary | 845
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Falling Short | 6.669 | 6.46 | 6.216 | 5.933 | 5.603 | 5.229 | 4.841 | 2.768 | 0.499 | -1.344 | -2.674 | Primary | 846
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Falling Short | 8.384 | 8.202 | 7.956 | 7.649 | 7.256 | 6.785 | 6.331 | 4.362 | 2.675 | 1.543 | 0.825 | Primary | 847
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Falling Short | 5.931 | 5.645 | 5.303 | 4.905 | 4.433 | 3.892 | 3.37 | 1.138 | -0.384 | -1.322 | -2.018 | Primary | 848
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Falling Short | 1.492 | 1.07 | 0.627 | 0.167 | -0.412 | -1.099 | -1.758 | -4.394 | -5.964 | -6.788 | -7.28 | Primary | 849
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Falling Short | 9.914 | 9.699 | 9.452 | 9.18 | 8.829 | 8.411 | 8.01 | 6.411 | 5.409 | 4.862 | 4.522 | Primary | 850
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Falling Short | 10.843 | 10.603 | 10.328 | 10.018 | 9.617 | 9.13 | 8.64 | 6.357 | 4.437 | 3.258 | 2.767 | Primary | 851
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Falling Short | 12.286 | 12.293 | 12.281 | 12.239 | 12.166 | 12.062 | 11.933 | 11.001 | 9.732 | 8.846 | 8.547 | Primary | 852
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Falling Short | 8.612 | 8.552 | 8.472 | 8.369 | 8.232 | 8.068 | 7.91 | 7.235 | 6.752 | 6.477 | 6.315 | Primary | 853
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Falling Short | 2.853 | 2.841 | 2.806 | 2.745 | 2.653 | 2.529 | 2.387 | 1.482 | 0.347 | -0.458 | -0.776 | Primary | 854
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Falling Short | 12.887 | 12.785 | 12.645 | 12.468 | 12.239 | 11.964 | 11.701 | 10.639 | 9.971 | 9.609 | 9.387 | Primary | 855
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Falling Short | 18.291 | 18.237 | 18.156 | 18.049 | 17.908 | 17.739 | 17.575 | 16.911 | 16.506 | 16.301 | 16.197 | Primary | 856
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Falling Short | 15.393 | 15.321 | 15.233 | 15.126 | 15.002 | 14.864 | 14.726 | 14.026 | 13.258 | 12.606 | 12.021 | Primary | 857
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Falling Short | 2.688 | 2.422 | 2.092 | 1.678 | 1.161 | 0.532 | -0.192 | -3.668 | -7.149 | -9.726 | -10.932 | Primary | 858
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Falling Short | 9.707 | 9.736 | 9.751 | 9.745 | 9.719 | 9.677 | 9.627 | 9.3 | 8.872 | 8.568 | 8.415 | Primary | 859
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Falling Short | 6.051 | 5.924 | 5.777 | 5.605 | 5.403 | 5.17 | 4.921 | 3.694 | 2.429 | 1.4 | 0.704 | Primary | 860
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Falling Short | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary | 861
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Falling Short | 7.006 | 6.763 | 6.475 | 6.142 | 5.717 | 5.207 | 4.702 | 2.571 | 0.963 | -0.026 | -0.539 | Primary | 862
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Falling Short | 14.447 | 14.318 | 14.141 | 13.916 | 13.634 | 13.302 | 12.977 | 11.596 | 10.683 | 10.174 | 9.877 | Primary | 863
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Falling Short | 3.114 | 3.003 | 2.873 | 2.723 | 2.544 | 2.342 | 2.146 | 1.327 | 0.707 | 0.25 | -0.124 | Primary | 864
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Falling Short | 8.728 | 8.495 | 8.207 | 7.843 | 7.387 | 6.831 | 6.182 | 1.945 | -3.446 | -7.455 | -9.277 | Primary | 865
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Falling Short | 13.319 | 13.089 | 12.846 | 12.587 | 12.26 | 11.874 | 11.503 | 9.974 | 8.98 | 8.453 | 8.161 | Primary | 866
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Falling Short | 4.98 | 4.908 | 4.823 | 4.728 | 4.615 | 4.489 | 4.366 | 3.846 | 3.473 | 3.205 | 2.979 | Primary | 867
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Falling Short | 6.076 | 5.784 | 5.429 | 5.007 | 4.495 | 3.906 | 3.339 | 0.99 | -0.771 | -2.01 | -2.98 | Primary | 868
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Falling Short | 10.001 | 9.844 | 9.631 | 9.359 | 9.009 | 8.591 | 8.19 | 6.654 | 5.722 | 5.211 | 4.917 | Primary | 869
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Falling Short | 15.679 | 15.514 | 15.328 | 15.122 | 14.866 | 14.565 | 14.277 | 13.159 | 12.531 | 12.206 | 11.998 | Primary | 870
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Falling Short | 6.062 | 5.985 | 5.856 | 5.672 | 5.424 | 5.119 | 4.819 | 3.563 | 2.603 | 2.016 | 1.696 | Primary | 871
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Falling Short | 12.855 | 12.452 | 11.988 | 11.455 | 10.831 | 10.122 | 9.416 | 6.266 | 3.654 | 1.752 | 0.388 | Primary | 872
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Falling Short | 12.727 | 12.682 | 12.623 | 12.547 | 12.455 | 12.349 | 12.243 | 11.777 | 11.341 | 10.981 | 10.674 | Primary | 873
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Falling Short | 9.33 | 9.14 | 8.899 | 8.607 | 8.243 | 7.811 | 7.375 | 5.421 | 3.748 | 2.595 | 1.932 | Primary | 874
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Falling Short | 11.283 | 11.293 | 11.281 | 11.24 | 11.168 | 11.064 | 10.936 | 10.105 | 9.051 | 8.313 | 8.053 | Primary | 875
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Falling Short | 5.502 | 5.496 | 5.454 | 5.37 | 5.236 | 5.054 | 4.844 | 3.56 | 1.965 | 0.822 | 0.342 | Primary | 876
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Falling Short | 28.493 | 28.406 | 28.3 | 28.17 | 28.013 | 27.829 | 27.631 | 26.524 | 25.278 | 24.283 | 23.651 | Primary | 877
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Falling Short | 2.899 | 2.578 | 2.241 | 1.887 | 1.51 | 1.115 | 0.711 | -1.373 | -3.507 | -5.506 | -7.357 | Primary | 878
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Falling Short | 1.832 | 1.775 | 1.709 | 1.634 | 1.548 | 1.452 | 1.358 | 0.918 | 0.527 | 0.171 | -0.165 | Primary | 879
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Falling Short | 11.647 | 11.439 | 11.198 | 10.918 | 10.584 | 10.202 | 9.829 | 8.168 | 6.845 | 5.91 | 5.187 | Primary | 880
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Falling Short | 9.842 | 9.854 | 9.853 | 9.834 | 9.797 | 9.744 | 9.685 | 9.353 | 8.984 | 8.735 | 8.617 | Primary | 881
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Falling Short | 10.663 | 10.616 | 10.542 | 10.433 | 10.289 | 10.119 | 9.947 | 9.134 | 8.467 | 8.059 | 7.782 | Primary | 882
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Falling Short | 1.737 | 1.657 | 1.566 | 1.457 | 1.332 | 1.189 | 1.037 | 0.277 | -0.518 | -1.173 | -1.63 | Primary | 883
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Falling Short | 11.795 | 11.79 | 11.758 | 11.684 | 11.561 | 11.383 | 11.152 | 9.386 | 6.9 | 5.146 | 4.623 | Primary | 884
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Falling Short | 15.657 | 15.637 | 15.609 | 15.573 | 15.518 | 15.445 | 15.37 | 14.976 | 14.585 | 14.328 | 14.209 | Primary | 885
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Falling Short | 7.747 | 6.666 | 6.257 | 5.778 | 5.211 | 4.567 | 3.938 | 1.338 | -0.607 | -1.992 | -3.069 | Primary | 886
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Falling Short | 11.947 | 11.886 | 11.796 | 11.678 | 11.52 | 11.328 | 11.142 | 10.397 | 9.946 | 9.698 | 9.538 | Primary | 887
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Falling Short | 15.757 | 15.77 | 15.735 | 15.635 | 15.452 | 15.177 | 14.814 | 12.061 | 8.208 | 5.483 | 4.69 | Primary | 888
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Falling Short | 8.798 | 8.651 | 8.442 | 8.17 | 7.812 | 7.376 | 6.95 | 5.082 | 3.656 | 2.81 | 2.384 | Primary | 889
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Falling Short | 4.223 | 4.176 | 4.119 | 4.053 | 3.974 | 3.884 | 3.796 | 3.397 | 3.068 | 2.807 | 2.592 | Primary | 890
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Falling Short | 8.942 | 8.774 | 8.582 | 8.363 | 8.083 | 7.748 | 7.422 | 6.122 | 5.241 | 4.727 | 4.419 | Primary | 891
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 14.235 | 14.026 | 13.783 | 13.501 | 13.176 | 12.814 | 12.443 | 10.568 | 8.668 | 7.035 | 5.655 | Primary | 892
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 13.164 | 12.968 | 12.742 | 12.474 | 12.166 | 11.827 | 11.475 | 9.575 | 7.512 | 5.722 | 4.226 | Primary | 893
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Falling Short | 12.234 | 12.245 | 12.244 | 12.225 | 12.186 | 12.132 | 12.07 | 11.682 | 11.185 | 10.841 | 10.685 | Primary | 894
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Falling Short | 8.031 | 8.055 | 8.067 | 8.065 | 8.049 | 8.022 | 7.993 | 7.845 | 7.707 | 7.608 | 7.518 | Primary | 895
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Falling Short | 17.528 | 17.474 | 17.396 | 17.294 | 17.165 | 17.01 | 16.858 | 16.196 | 15.672 | 15.343 | 15.158 | Primary | 896
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Falling Short | 4.671 | 4.533 | 4.385 | 4.224 | 4.051 | 3.864 | 3.666 | 2.523 | 1.184 | -0.115 | -1.276 | Primary | 897
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Falling Short | 2.398 | 2.179 | 1.935 | 1.668 | 1.329 | 0.926 | 0.539 | -1.039 | -2.053 | -2.609 | -2.948 | Primary | 898
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Falling Short | 11.641 | 11.447 | 11.223 | 10.972 | 10.655 | 10.281 | 9.922 | 8.471 | 7.455 | 6.838 | 6.431 | Primary | 899
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Falling Short | 10.179 | 9.953 | 9.68 | 9.358 | 8.946 | 8.448 | 7.946 | 5.555 | 3.468 | 2.141 | 1.523 | Primary | 900
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 12.926 | 12.929 | 12.914 | 12.877 | 12.812 | 12.719 | 12.604 | 11.794 | 10.72 | 9.969 | 9.723 | Primary | 901
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Falling Short | 16.097 | 16.007 | 15.882 | 15.722 | 15.516 | 15.27 | 15.034 | 14.089 | 13.513 | 13.212 | 13.038 | Primary | 902
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Falling Short | 12.839 | 12.78 | 12.688 | 12.558 | 12.383 | 12.169 | 11.962 | 11.111 | 10.528 | 10.213 | 10.059 | Primary | 903
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Falling Short | 9.426 | 9.327 | 9.18 | 8.983 | 8.716 | 8.385 | 8.049 | 6.44 | 4.996 | 4.08 | 3.691 | Primary | 904
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Falling Short | 11.53 | 9.884 | 9.793 | 9.664 | 9.488 | 9.274 | 9.067 | 8.304 | 7.867 | 7.636 | 7.491 | Primary | 905
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Falling Short | 4.142 | 4.066 | 3.975 | 3.868 | 3.737 | 3.584 | 3.436 | 2.806 | 2.348 | 2.051 | 1.851 | Primary | 906
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Falling Short | 14.06 | 13.844 | 13.57 | 13.237 | 12.82 | 12.328 | 11.854 | 9.894 | 8.62 | 7.921 | 7.522 | Primary | 907
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Falling Short | 2.199 | 2.006 | 1.737 | 1.391 | 0.942 | 0.404 | -0.116 | -2.217 | -3.567 | -4.317 | -4.76 | Primary | 908
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Falling Short | 14.67 | 14.549 | 14.389 | 14.194 | 13.94 | 13.632 | 13.334 | 12.082 | 11.2 | 10.688 | 10.418 | Primary | 909
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Falling Short | 7.735 | 7.548 | 7.305 | 7.007 | 6.624 | 6.168 | 5.731 | 3.918 | 2.701 | 2.007 | 1.569 | Primary | 910
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Falling Short | 18.458 | 18.482 | 18.478 | 18.437 | 18.357 | 18.246 | 18.125 | 17.448 | 16.729 | 16.26 | 16.04 | Primary | 911
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Falling Short | 12.549 | 12.447 | 12.323 | 12.175 | 11.99 | 11.772 | 11.556 | 10.581 | 9.813 | 9.338 | 9.072 | Primary | 912
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Falling Short | 3.274 | 3.04 | 2.756 | 2.418 | 2.009 | 1.536 | 1.068 | -1.102 | -2.984 | -4.387 | -5.409 | Primary | 913
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Falling Short | 3.422 | 2.567 | 1.577 | 0.449 | -0.869 | -2.364 | -3.827 | -10.222 | -14.972 | -18.194 | -20.601 | Primary | 914
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Falling Short | 4.047 | 3.778 | 3.466 | 3.107 | 2.656 | 2.124 | 1.605 | 16.663 | 15.503 | 14.847 | 14.441 | Primary | 915
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Falling Short | 12.615 | 12.341 | 12.01 | 11.624 | 11.162 | 10.634 | 10.125 | 7.993 | 6.508 | 5.523 | 4.752 | Primary | 916
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Falling Short | 21.663 | 18.663 | 18.71 | 18.745 | 18.772 | 18.796 | 18.818 | 18.86 | 18.85 | 18.841 | 18.832 | Primary | 917
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Falling Short | 3.287 | 2.987 | 2.641 | 2.231 | 1.743 | 1.173 | 0.532 | -2.833 | -6.549 | -9.486 | -11.184 | Primary | 918
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Falling Short | 12.598 | 12.572 | 12.53 | 12.471 | 12.389 | 12.289 | 12.188 | 11.709 | 11.288 | 11.005 | 10.787 | Primary | 919
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Falling Short | 13.952 | 13.992 | 14.026 | 14.051 | 14.069 | 14.08 | 14.088 | 14.096 | 14.069 | 14.039 | 14.011 | Primary | 920
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Falling Short | 14.929 | 14.958 | 14.978 | 14.986 | 14.984 | 14.973 | 14.962 | 14.891 | 14.793 | 14.724 | 14.678 | Primary | 921
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Falling Short | 9.768 | 9.475 | 9.099 | 8.643 | 8.082 | 7.426 | 6.791 | 4.13 | 2.23 | 1.006 | 0.172 | Primary | 922
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Falling Short | 15.713 | 15.631 | 15.54 | 15.434 | 15.314 | 15.182 | 15.046 | 14.317 | 13.541 | 12.875 | 12.319 | Primary | 923
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Falling Short | 5.452 | 5.429 | 5.382 | 5.308 | 5.203 | 5.078 | 4.95 | 4.325 | 3.737 | 3.355 | 3.095 | Primary | 924
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Falling Short | 14.033 | 13.95 | 13.832 | 13.68 | 13.48 | 13.238 | 13.002 | 11.972 | 11.169 | 10.681 | 10.415 | Primary | 925
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Falling Short | 18.278 | 14.828 | 14.797 | 14.754 | 14.688 | 14.602 | 14.517 | 14.239 | 14.088 | 14.002 | 13.967 | Primary | 926
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Falling Short | 11.593 | 11.465 | 11.312 | 11.134 | 10.918 | 10.667 | 10.419 | 9.288 | 8.357 | 7.705 | 7.25 | Primary | 927
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Falling Short | 2.548 | 2.434 | 2.289 | 2.111 | 1.888 | 1.623 | 1.343 | -0.154 | -1.66 | -2.691 | -3.177 | Primary | 928
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Falling Short | 11.006 | 10.867 | 10.685 | 10.466 | 10.185 | 9.848 | 9.524 | 8.213 | 7.282 | 6.696 | 6.305 | Primary | 929
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Falling Short | 10.103 | 9.979 | 9.804 | 9.576 | 9.276 | 8.913 | 8.559 | 8.175 | 7.247 | 6.714 | 6.443 | Primary | 930
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Falling Short | 5.519 | 5.208 | 4.852 | 4.439 | 3.958 | 3.408 | 2.806 | -0.254 | -3.472 | -6.054 | -7.71 | Primary | 931
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Falling Short | 16.347 | 16.22 | 16.074 | 15.905 | 15.71 | 15.489 | 15.271 | 14.266 | 13.418 | 12.764 | 12.254 | Primary | 932
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Falling Short | 8.798 | 7.037 | 6.704 | 6.318 | 5.869 | 5.356 | 4.798 | 8.854 | 5.726 | 3.319 | 1.838 | Primary | 933
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Falling Short | 3.81 | 3.701 | 3.573 | 3.426 | 3.252 | 3.056 | 2.866 | 2.048 | 1.442 | 1.016 | 0.676 | Primary | 934
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Falling Short | 14.44 | 14.302 | 14.112 | 13.87 | 13.56 | 13.188 | 12.829 | 11.37 | 10.406 | 9.884 | 9.635 | Primary | 935
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Falling Short | -0.309 | -0.475 | -0.672 | 0.095 | -0.188 | -0.515 | -0.839 | -2.201 | -3.294 | -4.069 | -4.583 | Primary | 936
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Falling Short | 9.162 | 8.937 | 8.661 | 8.332 | 7.934 | 7.475 | 7.025 | 5.007 | 3.346 | 2.138 | 1.244 | Primary | 937
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Falling Short | 7.782 | 7.656 | 7.477 | 7.241 | 6.927 | 6.546 | 6.173 | 4.554 | 3.328 | 2.607 | 2.243 | Primary | 938
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Falling Short | 4.997 | 4.696 | 4.33 | 3.89 | 3.357 | 2.743 | 2.144 | -0.463 | -2.567 | -4.073 | -5.195 | Primary | 939
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Falling Short | 16.162 | 16.027 | 15.839 | 15.594 | 15.271 | 14.88 | 14.495 | 12.859 | 11.568 | 10.77 | 10.365 | Primary | 940
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Falling Short | 7.771 | 7.804 | 7.817 | 7.804 | 7.766 | 7.705 | 7.634 | 7.179 | 6.602 | 6.193 | 6.014 | Primary | 941
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Falling Short | 13.875 | 14.648 | 14.379 | 6.075 | 5.397 | 4.617 | 3.864 | 1.564 | 0.455 | -0.234 | -0.754 | Primary | 942
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Falling Short | 10.981 | 10.663 | 10.276 | 9.817 | 9.27 | 8.642 | 8.026 | 5.269 | 3.141 | 1.732 | 0.735 | Primary | 943
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Falling Short | 6.53 | 6.557 | 6.562 | 6.535 | 6.48 | 6.403 | 6.319 | 5.951 | 5.61 | 5.381 | 5.262 | Primary | 944
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Falling Short | 11.857 | 11.646 | 11.375 | 11.044 | 10.637 | 10.16 | 9.701 | 7.812 | 6.635 | 5.998 | 5.579 | Primary | 945
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Falling Short | 4.956 | 4.513 | 4 | 3.405 | 2.71 | 1.922 | 1.12 | -2.932 | -6.921 | -10.041 | -12.259 | Primary | 946
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Falling Short | 10.257 | 10.304 | 10.346 | 10.382 | 10.412 | 10.438 | 10.462 | 10.537 | 10.551 | 10.55 | 10.543 | Primary | 947
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Falling Short | 11.17 | 11.221 | 11.258 | 11.275 | 11.273 | 11.249 | 11.206 | 10.753 | 10.014 | 9.483 | 9.325 | Primary | 948
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Falling Short | 2.406 | 2.448 | 2.483 | 2.511 | 2.53 | 2.543 | 2.553 | 2.548 | 2.477 | 2.417 | 2.389 | Primary | 949
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Falling Short | 6.432 | 6.332 | 6.208 | 6.061 | 5.867 | 5.632 | 5.402 | 4.572 | 4.058 | 3.757 | 3.589 | Primary | 950
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Falling Short | 0.607 | 0.441 | 0.256 | 0.051 | -0.189 | -0.461 | -0.73 | -1.975 | -3.013 | -3.773 | -4.335 | Primary | 951
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Falling Short | 12.534 | 12.399 | 12.215 | 11.979 | 11.679 | 11.323 | 10.961 | 9.231 | 7.837 | 7.013 | 6.615 | Primary | 952
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Falling Short | 12.823 | 10.889 | 10.884 | 10.839 | 10.755 | 10.638 | 10.504 | 9.961 | 9.503 | 9.193 | 9.072 | Primary | 953
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Falling Short | 9.343 | 9.163 | 15.956 | 15.723 | 15.425 | 15.069 | 14.724 | 13.317 | 12.421 | 11.931 | 11.646 | Primary | 954
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Falling Short | 9.946 | 9.8 | 9.638 | 9.454 | 9.246 | 9.015 | 8.766 | 7.322 | 5.669 | 4.284 | 3.269 | Primary | 955
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Falling Short | 3.364 | 1.833 | 1.559 | 1.292 | 0.957 | 0.561 | 0.173 | -1.467 | -2.644 | -3.421 | -3.99 | Primary | 956
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Falling Short | 12.453 | 12.384 | 12.308 | 12.222 | 12.128 | 12.027 | 11.925 | 11.379 | 10.797 | 10.225 | 9.655 | Primary | 957
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Falling Short | 8.395 | 8.345 | 15.259 | 15.133 | 14.959 | 14.742 | 14.527 | 13.552 | 12.756 | 12.273 | 12.013 | Primary | 958
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Falling Short | 5.218 | 4.2 | 3.845 | 3.495 | 3.06 | 2.548 | 2.033 | -0.238 | -2.177 | -3.545 | -4.388 | Primary | 959
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Falling Short | 10.335 | 10.157 | 9.916 | 9.614 | 9.228 | 8.769 | 8.329 | 6.561 | 5.402 | 4.743 | 4.326 | Primary | 960
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Falling Short | 10.152 | 9.989 | 7.636 | 7.342 | 6.971 | 6.512 | 5.972 | 2.783 | -1.035 | -3.932 | -5.281 | Primary | 961
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Falling Short | 8.38 | 8.115 | 7.785 | 7.392 | 6.913 | 6.353 | 5.801 | 3.323 | 1.364 | 0.047 | -0.817 | Primary | 962
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Falling Short | 6.934 | 5.139 | 4.873 | 4.555 | 4.144 | 3.651 | 3.166 | 1.38 | 0.241 | -0.431 | -0.792 | Primary | 963
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Falling Short | 8.407 | 7.709 | 7.739 | 7.736 | 7.703 | 7.643 | 7.558 | 6.901 | 5.959 | 5.295 | 5.073 | Primary | 964
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Falling Short | 18.732 | 18.714 | 18.678 | 18.615 | 18.52 | 18.389 | 18.224 | 17.077 | 15.549 | 14.475 | 14.147 | Primary | 965
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Falling Short | 8.64 | 8.599 | 8.524 | 8.414 | 8.259 | 8.066 | 7.879 | 7.12 | 6.637 | 6.374 | 6.211 | Primary | 966
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Falling Short | 10.728 | 10.602 | 10.432 | 10.216 | 9.942 | 9.616 | 9.288 | 7.765 | 6.593 | 5.901 | 5.522 | Primary | 967
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Falling Short | 12.095 | 11.991 | 11.842 | 11.644 | 11.387 | 11.082 | 10.789 | 9.64 | 8.909 | 8.519 | 8.287 | Primary | 968
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Falling Short | 12.244 | 12.255 | 12.25 | 12.224 | 12.176 | 12.109 | 12.035 | 11.6 | 11.051 | 10.655 | 10.456 | Primary | 969
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Falling Short | 8.23 | 8.291 | 8.349 | 8.399 | 8.437 | 8.466 | 8.491 | 8.553 | 8.53 | 8.499 | 8.474 | Primary | 970
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Falling Short | 8.026 | 6.267 | 6.222 | 6.154 | 6.051 | 5.916 | 5.767 | 4.97 | 4.127 | 3.538 | 3.246 | Primary | 971
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Falling Short | 9.814 | 8.595 | 8.631 | 8.649 | 8.653 | 8.647 | 8.638 | 8.563 | 8.441 | 8.355 | 8.29 | Primary | 972
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Falling Short | 1.209 | 1.062 | 0.891 | 0.695 | 0.463 | 0.198 | -0.061 | -1.184 | -2.072 | -2.721 | -3.226 | Primary | 973
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 2.841 | 2.833 | 2.819 | 2.801 | 2.775 | 2.742 | 2.71 | 2.542 | 2.371 | 2.239 | 2.128 | Primary | 974
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Falling Short | 12.803 | 12.712 | 12.598 | 12.453 | 12.272 | 12.054 | 11.809 | 10.306 | 8.482 | 7.091 | 6.352 | Primary | 975
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Falling Short | 24.326 | 24.281 | 24.228 | 24.164 | 24.093 | 24.017 | 23.939 | 23.578 | 23.201 | 22.814 | 22.417 | Primary | 976
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Falling Short | 13.74 | 13.757 | 13.761 | 13.752 | 13.726 | 13.688 | 13.65 | 13.495 | 13.378 | 13.299 | 13.235 | Primary | 977
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Falling Short | -2.04 | -2.272 | -2.525 | -2.803 | -3.108 | -3.438 | -3.777 | -5.58 | -7.524 | -9.333 | -10.955 | Primary | 978
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Falling Short | 3.081 | 2.811 | 2.5 | 2.124 | 1.677 | 1.154 | 0.57 | -2.889 | -7.011 | -10.228 | -12.071 | Primary | 979
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Falling Short | 11 | 10.931 | 10.819 | 10.666 | 10.46 | 10.209 | 9.967 | 8.995 | 8.388 | 8.078 | 7.911 | Primary | 980
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Falling Short | 11.231 | 11.285 | 11.328 | 11.359 | 11.376 | 11.379 | 11.369 | 11.173 | 10.796 | 10.516 | 10.437 | Primary | 981
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Falling Short | 8.106 | 7.844 | 7.518 | 7.123 | 6.636 | 6.065 | 5.495 | 2.853 | 0.579 | -0.999 | -1.971 | Primary | 982
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Falling Short | 11.699 | 10.965 | 10.804 | 10.615 | 10.398 | 10.16 | 9.923 | 9.064 | 8.467 | 7.994 | 7.55 | Primary | 983
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Falling Short | 4.199 | 4.008 | 3.794 | 3.56 | 3.268 | 2.925 | 2.597 | 1.315 | 0.602 | 0.241 | 0.018 | Primary | 984
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Falling Short | 11.002 | 10.895 | 10.74 | 10.536 | 10.27 | 9.954 | 9.647 | 8.402 | 7.651 | 7.268 | 7.041 | Primary | 985
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Falling Short | -1.195 | -1.295 | -1.421 | -1.574 | 0.235 | 0.011 | -0.205 | -1.114 | -1.748 | -2.128 | -2.385 | Primary | 986
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Falling Short | 15.221 | 15.152 | 15.068 | 14.958 | 14.822 | 14.661 | 14.48 | 13.398 | 12.099 | 11.112 | 10.575 | Primary | 987
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Falling Short | 14.824 | 14.502 | 14.221 | 13.987 | 13.69 | 13.334 | 12.983 | 11.432 | 10.249 | 9.558 | 9.249 | Primary | 988
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Falling Short | 10.136 | 10.006 | 9.811 | 9.555 | 9.221 | 8.819 | 8.429 | 6.767 | 5.549 | 4.805 | 4.359 | Primary | 989
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Falling Short | 23.71 | 23.734 | 23.756 | 23.775 | 23.79 | 23.8 | 23.809 | 23.83 | 23.818 | 23.804 | 23.793 | Primary | 990
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Falling Short | 8.471 | 8.493 | 8.513 | 8.522 | 8.519 | 8.51 | 8.501 | 8.442 | 8.35 | 8.292 | 8.252 | Primary | 991
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Falling Short | 11.336 | 11.225 | 11.06 | 10.844 | 10.564 | 10.228 | 9.906 | 8.621 | 7.827 | 7.401 | 7.145 | Primary | 992
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Falling Short | 4.285 | 4.239 | 4.19 | 4.138 | 4.083 | 4.024 | 3.964 | 3.644 | 3.301 | 2.951 | 2.598 | Primary | 993
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Falling Short | 8.715 | 8.587 | 8.445 | 8.284 | 8.103 | 7.905 | 7.704 | 6.659 | 5.577 | 4.625 | 3.803 | Primary | 994
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Falling Short | 13.907 | 13.779 | 13.609 | 13.397 | 13.128 | 12.809 | 12.501 | 11.245 | 10.461 | 10.029 | 9.76 | Primary | 995
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Falling Short | 10.765 | 10.535 | 10.268 | 9.96 | 9.596 | 9.182 | 8.773 | 7.049 | 5.661 | 4.64 | 3.873 | Primary | 996
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Falling Short | 7.778 | 7.439 | 7.035 | 6.56 | 5.998 | 5.355 | 4.723 | 1.969 | -0.074 | -1.404 | -2.345 | Primary | 997
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Falling Short | 12.856 | 12.529 | 12.18 | 11.798 | 11.379 | 10.925 | 10.448 | 7.959 | 5.29 | 2.956 | 1.114 | Primary | 998
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Falling Short | 7.656 | 7.638 | 7.587 | 7.496 | 7.36 | 7.183 | 6.984 | 5.807 | 4.463 | 3.558 | 3.203 | Primary | 999
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Falling Short | 13.817 | 13.725 | 13.591 | 13.418 | 13.192 | 12.921 | 12.661 | 11.597 | 10.872 | 10.452 | 10.2 | Primary | 1000
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Falling Short | 7.36 | 7.133 | 6.874 | 6.583 | 6.214 | 5.778 | 5.355 | 20.692 | 19.649 | 19.065 | 18.705 | Primary | 1001
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Falling Short | 7.294 | 7.111 | 6.906 | 6.669 | 6.4 | 6.106 | 5.8 | 4.136 | 2.303 | 0.737 | -0.517 | Primary | 1002
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Leading the Way | 13.095 | 12.842 | 12.59 | 12.496 | 12.477 | 12.453 | 12.341 | 10.626 | 9.188 | 8.133 | 8.455 | Primary | 1003
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Leading the Way | 12.273 | 10.634 | 10.518 | 10.33 | 10.197 | 10.009 | 9.661 | 6.175 | 3.673 | 2.162 | 2.42 | Primary | 1004
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Leading the Way | 11.529 | 11.234 | 10.841 | 10.387 | 9.931 | 9.451 | 8.801 | 3.433 | -0.851 | -4.105 | -4.434 | Primary | 1005
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Leading the Way | 6.037 | 4.683 | 4.689 | 4.641 | 4.605 | 4.536 | 4.369 | 1.373 | -0.552 | -1.884 | -1.419 | Primary | 1006
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 15.39 | 15.001 | 14.492 | 14.007 | 13.661 | 13.302 | 12.735 | 8.368 | 5.101 | 2.8 | 2.997 | Primary | 1007
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 17.148 | 17.141 | 17.11 | 17.075 | 17.071 | 17.064 | 17.014 | 16.268 | 15.676 | 15.242 | 15.388 | Primary | 1008
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Leading the Way | 9.029 | 8.476 | 7.73 | 6.903 | 6.331 | 5.737 | 4.893 | -1.945 | -7.156 | -10.85 | -10.975 | Primary | 1009
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Leading the Way | 17.217 | 17.249 | 17.248 | 17.23 | 17.254 | 17.273 | 17.234 | 15.618 | 14.434 | 13.502 | 13.854 | Primary | 1010
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Leading the Way | 1.046 | 0.845 | 0.55 | 0.197 | -0.107 | -0.43 | -0.92 | -5.496 | -9.189 | -12.046 | -12.105 | Primary | 1011
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Leading the Way | 3.406 | 2.921 | 3.059 | 3.169 | 3.306 | 3.432 | 3.518 | 2.754 | 2.216 | 1.836 | 2.34 | Primary | 1012
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Leading the Way | 12.006 | 11.757 | 11.378 | 10.926 | 10.628 | 10.313 | 9.843 | 6.902 | 3.975 | 1.855 | 1.84 | Primary | 1013
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Leading the Way | 2.652 | 2.332 | 1.899 | 1.48 | 1.158 | 0.787 | 0.26 | -4.728 | -8.148 | -10.332 | -10 | Primary | 1014
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Leading the Way | 3.331 | 3.325 | 3.307 | 3.282 | 3.262 | 3.238 | 3.2 | 2.811 | 2.518 | 2.3 | 2.284 | Primary | 1015
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Leading the Way | 15.738 | 15.547 | 15.244 | 14.885 | 14.689 | 14.484 | 14.129 | 10.494 | 7.716 | 5.731 | 6.052 | Primary | 1016
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Leading the Way | 13.072 | 12.558 | 12.516 | 12.455 | 12.44 | 12.42 | 12.358 | 11.362 | 10.564 | 9.934 | 9.995 | Primary | 1017
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Leading the Way | 10.64 | 10.636 | 10.578 | 10.484 | 10.439 | 10.377 | 10.243 | 7.862 | 6.14 | 4.984 | 5.452 | Primary | 1018
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Leading the Way | 15.586 | 15.247 | 14.753 | 14.178 | 13.747 | 13.283 | 12.627 | 7.863 | 4.389 | 2.157 | 2.135 | Primary | 1019
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Leading the Way | 8.361 | 8.384 | 8.379 | 8.35 | 8.336 | 8.307 | 8.217 | 6.762 | 5.612 | 4.836 | 5.106 | Primary | 1020
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Leading the Way | 5.848 | 5.708 | 5.497 | 5.234 | 5.067 | 4.89 | 4.589 | 0.605 | -2.774 | -5.547 | -5.648 | Primary | 1021
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Leading the Way | 21.438 | 21.4 | 21.299 | 21.155 | 21.061 | 20.959 | 20.771 | 19.213 | 18.054 | 17.253 | 17.428 | Primary | 1022
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Leading the Way | 3.691 | 3.559 | 3.389 | 3.196 | 3.078 | 2.954 | 2.761 | 0.737 | -1.031 | -2.497 | -2.763 | Primary | 1023
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Leading the Way | 11.549 | 11.065 | 10.38 | 9.592 | 9.034 | 8.433 | 7.56 | 0.36 | -5.064 | -8.771 | -8.855 | Primary | 1024
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Leading the Way | 9.399 | 8.956 | 8.332 | 7.669 | 7.195 | 6.692 | 5.904 | -0.131 | -4.337 | -7.25 | -6.976 | Primary | 1025
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Leading the Way | 14.705 | 14.455 | 14.105 | 13.753 | 13.494 | 13.221 | 12.82 | 10.004 | 7.988 | 6.655 | 6.779 | Primary | 1026
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Leading the Way | 3.007 | 2.944 | 2.762 | 2.495 | 2.373 | 2.205 | 1.86 | -2.358 | -5.519 | -7.548 | -7.036 | Primary | 1027
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Leading the Way | 5.395 | 5.172 | 4.85 | 4.469 | 4.168 | 3.839 | 3.39 | 0.121 | -2.287 | -3.874 | -4.035 | Primary | 1028
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 15.168 | 15.121 | 15.039 | 14.939 | 14.871 | 14.789 | 14.629 | 12.638 | 11.34 | 10.379 | 10.55 | Primary | 1029
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 4.298 | 1.3 | 1.203 | 1.043 | 0.926 | 0.748 | 0.377 | -4.694 | -8.362 | -10.833 | -10.22 | Primary | 1030
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Leading the Way | 7.451 | 7.331 | 7.108 | 6.805 | 6.581 | 6.303 | 5.867 | 1.345 | -2.169 | -4.502 | -4.4 | Primary | 1031
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Leading the Way | 11.699 | 11.408 | 10.949 | 10.392 | 10.041 | 9.671 | 9.034 | 3.311 | -1.086 | -4.269 | -3.973 | Primary | 1032
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Leading the Way | 5.81 | 5.369 | 4.692 | 3.877 | 3.275 | 2.621 | 1.613 | -6.773 | -13.111 | -17.492 | -17.371 | Primary | 1033
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Leading the Way | 6.881 | 6.864 | 6.842 | 6.816 | 6.796 | 6.774 | 6.747 | 6.4 | 6.094 | 5.829 | 5.8 | Primary | 1034
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Leading the Way | 3.704 | 3.668 | 3.614 | 3.549 | 3.492 | 3.427 | 3.338 | 2.489 | 1.838 | 1.357 | 1.313 | Primary | 1035
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Leading the Way | 11.589 | 11.188 | 10.599 | 9.91 | 9.495 | 9.055 | 8.368 | 2.462 | -1.883 | -4.911 | -4.752 | Primary | 1036
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 13.548 | 13.454 | 13.356 | 13.252 | 13.146 | 13.039 | 12.931 | 11.699 | 10.46 | 9.239 | 8.716 | Primary | 1037
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Leading the Way | 4.62 | 4.504 | 4.342 | 4.158 | 4.022 | 3.881 | 3.684 | 2.247 | 1.237 | 0.563 | 0.569 | Primary | 1038
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 9.432 | 9.103 | 8.588 | 7.986 | 7.605 | 7.202 | 6.542 | 0.417 | -4.064 | -7.192 | -6.744 | Primary | 1039
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Leading the Way | 11.554 | 11.283 | 10.852 | 10.342 | 9.954 | 9.533 | 8.873 | 3.508 | -0.398 | -3.052 | -2.805 | Primary | 1040
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Leading the Way | 9.324 | 9.347 | 9.314 | 9.244 | 9.252 | 9.242 | 9.14 | 7.076 | 5.522 | 4.441 | 4.828 | Primary | 1041
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Leading the Way | 10.227 | 10.216 | 10.139 | 10.026 | 9.956 | 9.872 | 9.711 | 7.944 | 6.867 | 6.17 | 6.46 | Primary | 1042
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Leading the Way | 17.46 | 17.28 | 17.022 | 16.719 | 16.478 | 16.213 | 15.852 | 13.456 | 11.837 | 10.904 | 10.909 | Primary | 1043
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Leading the Way | 7.685 | 22.197 | 21.914 | 21.59 | 21.351 | 21.099 | 20.676 | 16.625 | 13.507 | 11.225 | 11.498 | Primary | 1044
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Leading the Way | 10.144 | 9.715 | 9.077 | 8.308 | 7.723 | 7.121 | 6.213 | 16.099 | 10.294 | 5.854 | 5.626 | Primary | 1045
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Leading the Way | 3.861 | 3.732 | 3.558 | 3.391 | 3.285 | 3.174 | 3.009 | 1.862 | 1.086 | 0.579 | 0.651 | Primary | 1046
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Leading the Way | 5.887 | 4.93 | 3.719 | 2.527 | 1.571 | 0.561 | -0.874 | -9.911 | -15.898 | -19.87 | -19.685 | Primary | 1047
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Leading the Way | 3.756 | 3.349 | 2.778 | 2.103 | 1.43 | 0.713 | -0.294 | -9.056 | -15.864 | -21.192 | -21.706 | Primary | 1048
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Leading the Way | 5.039 | 4.453 | 3.6 | 2.582 | 1.806 | 0.994 | -0.207 | 14.284 | 6.807 | 1.215 | 0.887 | Primary | 1049
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Leading the Way | 4.091 | 4.156 | 4.211 | 4.256 | 4.297 | 4.329 | 4.348 | 4.102 | 3.93 | 3.851 | 4.015 | Primary | 1050
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Leading the Way | 7.943 | 7.472 | 6.746 | 5.852 | 5.167 | 4.393 | 3.256 | 11.495 | 5.088 | 1.06 | 1.044 | Primary | 1051
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Leading the Way | 12.825 | 12.907 | 12.975 | 13.026 | 13.072 | 13.107 | 13.126 | 12.244 | 11.549 | 11.07 | 11.414 | Primary | 1052
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Leading the Way | 9.528 | 9.676 | 9.816 | 9.946 | 10.07 | 10.188 | 10.299 | 10.471 | 10.594 | 10.705 | 11.032 | Primary | 1053
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Leading the Way | 11.125 | 11.218 | 11.277 | 11.348 | 11.446 | 11.529 | 11.544 | 9.588 | 8.06 | 6.93 | 7.639 | Primary | 1054
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Leading the Way | 9.029 | 9.097 | 9.135 | 9.161 | 9.213 | 9.257 | 9.262 | 8.35 | 7.671 | 7.191 | 7.576 | Primary | 1055
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Leading the Way | 10.773 | 10.468 | 9.995 | 9.439 | 9.037 | 8.58 | 7.899 | 2.774 | -0.806 | -2.89 | -2.689 | Primary | 1056
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Leading the Way | 5.106 | 5.048 | 4.96 | 4.86 | 4.76 | 4.656 | 4.529 | 3.988 | 3.696 | 3.547 | 3.483 | Primary | 1057
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Leading the Way | 7.663 | 7.65 | 7.616 | 7.569 | 7.532 | 7.49 | 7.426 | 6.876 | 6.387 | 5.965 | 5.795 | Primary | 1058
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Leading the Way | 13.062 | 12.572 | 11.924 | 11.286 | 10.811 | 10.31 | 9.527 | 3.173 | -1.491 | -4.68 | -4.326 | Primary | 1059
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Leading the Way | 0.818 | 0.817 | 0.806 | 0.786 | 0.771 | 0.751 | 0.718 | 0.339 | 0.03 | -0.205 | -0.227 | Primary | 1060
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Leading the Way | 2.421 | 2.193 | 1.89 | 1.558 | 1.302 | 1.036 | 0.687 | -1.888 | -3.695 | -4.946 | -4.997 | Primary | 1061
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 9.585 | 9.348 | 8.975 | 8.522 | 8.233 | 7.907 | 7.415 | 3.114 | 0.023 | -1.888 | -1.659 | Primary | 1062
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Leading the Way | 8.408 | 8.26 | 8.056 | 7.891 | 7.792 | 7.679 | 7.448 | 4.479 | 2.329 | 0.785 | 1.234 | Primary | 1063
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Leading the Way | 5.205 | 4.889 | 4.454 | 3.963 | 3.616 | 3.247 | 2.711 | -2.1 | -5.859 | -8.689 | -8.894 | Primary | 1064
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Leading the Way | 4.2 | 4.226 | 4.244 | 4.254 | 4.264 | 4.269 | 4.258 | 3.94 | 3.702 | 3.554 | 3.648 | Primary | 1065
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Leading the Way | 21.926 | 21.743 | 21.478 | 21.199 | 21.038 | 20.869 | 20.564 | 17.456 | 15.081 | 13.392 | 13.733 | Primary | 1066
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Leading the Way | 7.451 | 7.501 | 7.52 | 7.539 | 7.599 | 7.652 | 7.652 | 6.266 | 5.228 | 4.452 | 4.9 | Primary | 1067
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Leading the Way | 12.99 | 12.644 | 12.201 | 11.804 | 11.517 | 11.214 | 10.721 | 6.691 | 3.755 | 1.747 | 2.089 | Primary | 1068
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Leading the Way | 8.455 | 8.422 | 8.307 | 8.139 | 8.028 | 7.899 | 7.642 | 4.401 | 2.008 | 0.285 | 0.695 | Primary | 1069
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Leading the Way | 2.177 | 1.4 | 0.309 | -0.845 | -1.592 | -2.383 | -3.626 | -13.551 | -20.774 | -25.622 | -25.07 | Primary | 1070
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Leading the Way | 0.989 | 0.847 | 0.669 | 0.463 | 0.267 | 0.054 | -0.209 | -1.876 | -2.662 | -3.312 | -3.441 | Primary | 1071
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Leading the Way | 2.862 | 2.739 | 2.56 | 2.336 | 2.137 | 1.906 | 1.587 | -1.579 | -4.176 | -6.098 | -6.394 | Primary | 1072
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Leading the Way | 12.961 | 12.893 | 12.741 | 12.531 | 12.367 | 12.19 | 11.89 | 10.483 | 8.852 | 7.738 | 8.007 | Primary | 1073
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Leading the Way | 14.476 | 14.265 | 14.912 | 14.474 | 14.194 | 13.899 | 13.399 | 8.82 | 5.39 | 2.94 | 3.238 | Primary | 1074
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Leading the Way | 22.157 | 22.112 | 21.951 | 21.669 | 21.359 | 20.934 | 20.299 | 13.788 | 9.138 | 6.473 | 6.884 | Primary | 1075
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Leading the Way | 9.798 | 9.501 | 9.084 | 8.598 | 8.217 | 7.815 | 7.24 | 9.322 | 5.413 | 2.455 | 2.174 | Primary | 1076
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Leading the Way | 1.897 | 1.556 | 1.099 | 0.578 | 0.236 | -0.129 | -0.649 | -4.608 | -7.295 | -9.225 | -9.33 | Primary | 1077
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Leading the Way | 7.982 | 7.598 | 6.957 | 6.167 | 5.75 | 5.313 | 4.509 | -3.194 | -9.223 | -13.602 | -13.091 | Primary | 1078
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Leading the Way | 5.242 | 2.93 | 2.896 | 2.831 | 2.782 | 2.715 | 2.569 | 0.729 | -0.549 | -1.458 | -1.273 | Primary | 1079
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Leading the Way | 7.479 | 7.012 | 6.318 | 5.527 | 4.979 | 4.401 | 3.516 | -3.414 | -8.342 | -11.653 | -11.277 | Primary | 1080
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Leading the Way | 3.365 | 3.089 | 17.358 | 16.848 | 16.446 | 16.012 | 15.31 | 9.148 | 4.509 | 1.294 | 1.677 | Primary | 1081
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Leading the Way | -0.459 | -0.603 | -0.811 | -1.056 | -1.252 | -1.455 | -1.75 | -4.312 | -6.37 | -7.99 | -8.122 | Primary | 1082
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Leading the Way | 2.558 | 2.562 | 2.543 | 2.506 | 2.493 | 2.471 | 2.418 | 1.437 | 0.732 | 0.27 | 0.465 | Primary | 1083
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Leading the Way | 10.365 | 10.077 | 9.61 | 9.049 | 8.665 | 8.26 | 7.623 | 2.596 | -1.152 | -3.747 | -3.425 | Primary | 1084
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Leading the Way | 8.243 | 7.862 | 7.279 | 6.599 | 6.194 | 5.755 | 5.049 | -1.261 | -5.83 | -8.885 | -8.522 | Primary | 1085
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Leading the Way | 11.231 | 11.105 | 10.896 | 10.641 | 10.457 | 10.252 | 9.952 | 7.584 | 5.903 | 4.848 | 4.9 | Primary | 1086
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Leading the Way | 3.616 | 2.692 | 2.683 | 2.614 | 2.589 | 2.526 | 2.329 | -0.517 | -2.703 | -4.149 | -3.694 | Primary | 1087
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Leading the Way | 14.894 | 14.796 | 14.657 | 14.482 | 14.315 | 14.116 | 13.859 | 11.12 | 8.904 | 7.32 | 7.136 | Primary | 1088
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Leading the Way | 4.445 | 4.353 | 4.22 | 4.067 | 3.957 | 3.842 | 3.672 | 2.197 | 1.021 | 0.139 | 0.111 | Primary | 1089
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Leading the Way | 2.056 | 1.985 | 1.869 | 1.731 | 1.641 | 1.546 | 1.383 | -0.173 | -1.353 | -2.193 | -2.051 | Primary | 1090
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Leading the Way | 14.965 | 14.604 | 14.063 | 13.418 | 12.96 | 12.458 | 11.703 | 5.166 | 0.224 | -3.255 | -3.315 | Primary | 1091
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Leading the Way | 2.746 | 2.579 | 4.274 | 3.885 | 3.59 | 3.267 | 2.698 | -3.275 | -7.734 | -11.021 | -10.594 | Primary | 1092
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Leading the Way | 14.811 | 14.732 | 14.58 | 14.385 | 14.324 | 14.252 | 14.07 | 11.488 | 9.458 | 8.049 | 8.423 | Primary | 1093
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Leading the Way | 4.419 | 4.308 | 4.155 | 3.981 | 3.834 | 3.681 | 3.471 | 1.773 | 0.449 | -0.547 | -0.627 | Primary | 1094
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Leading the Way | 4.622 | 4.109 | 3.364 | 2.508 | 1.864 | 1.179 | 0.247 | -6.823 | -11.945 | -15.48 | -15.569 | Primary | 1095
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Leading the Way | 11.569 | 11.192 | 10.653 | 10.043 | 9.625 | 9.189 | 8.566 | 3.651 | -0.016 | -2.639 | -2.691 | Primary | 1096
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Leading the Way | 12.116 | 10.474 | 10.297 | 10.007 | 9.76 | 9.403 | 8.844 | 4.004 | 0.86 | -0.71 | -0.331 | Primary | 1097
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Leading the Way | 0.86 | 0.487 | 0.059 | -0.261 | -0.522 | -0.793 | -1.148 | -3.187 | -4.493 | -5.231 | -5.11 | Primary | 1098
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Leading the Way | 7.293 | 6.502 | 5.443 | 4.276 | 3.471 | 2.635 | 1.464 | -6.745 | -12.709 | -16.715 | -16.905 | Primary | 1099
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Leading the Way | 9.177 | 9.175 | 9.166 | 9.152 | 9.14 | 9.125 | 9.102 | 8.927 | 8.758 | 8.594 | 8.471 | Primary | 1100
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Leading the Way | 1.656 | 1.419 | 1.049 | 0.557 | 0.015 | -0.656 | -1.558 | -8.024 | -12.52 | -14.763 | -14.973 | Primary | 1101
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Leading the Way | 10.373 | 9.948 | 9.392 | 8.857 | 8.516 | 8.15 | 7.532 | 1.62 | -2.988 | -6.296 | -5.974 | Primary | 1102
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Leading the Way | 8.73 | 8.317 | 7.68 | 6.907 | 6.398 | 5.842 | 4.991 | -1.807 | -6.798 | -10.073 | -9.925 | Primary | 1103
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Leading the Way | 1.32 | 1.212 | 1.054 | 0.854 | 0.658 | 0.423 | 0.118 | -2.054 | -3.608 | -4.472 | -4.671 | Primary | 1104
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Leading the Way | 7.196 | 6.844 | 6.308 | 5.675 | 5.23 | 4.767 | 4.039 | -2.409 | -7.441 | -11.199 | -11.053 | Primary | 1105
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Leading the Way | 0.951 | 0.9 | 0.76 | 0.572 | 0.505 | 0.418 | 0.203 | -2.806 | -4.896 | -6.337 | -5.846 | Primary | 1106
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Leading the Way | 1.499 | 1.499 | 1.498 | 1.497 | 1.496 | 1.495 | 1.494 | 1.477 | 1.461 | 1.446 | 1.44 | Primary | 1107
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 24.097 | 24.128 | 24.109 | 24.057 | 24.075 | 24.084 | 24.028 | 22.143 | 20.71 | 19.637 | 20.107 | Primary | 1108
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 33.854 | 33.8 | 33.702 | 33.583 | 33.519 | 33.449 | 33.324 | 31.901 | 30.955 | 30.283 | 30.434 | Primary | 1109
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 20.499 | 20.417 | 20.295 | 20.15 | 20.024 | 19.893 | 19.72 | 18.609 | 17.819 | 17.274 | 17.241 | Primary | 1110
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 14.621 | 14.381 | 14.039 | 13.655 | 13.38 | 13.073 | 12.617 | 9.067 | 6.393 | 4.633 | 4.552 | Primary | 1111
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Leading the Way | 13.548 | 13.203 | 12.733 | 13.197 | 12.717 | 12.222 | 11.559 | 6.887 | 3.345 | 0.845 | 0.701 | Primary | 1112
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Leading the Way | 10.376 | 9.283 | 8.788 | 8.188 | 7.827 | 7.446 | 6.826 | 1.676 | -1.956 | -4.571 | -4.374 | Primary | 1113
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Leading the Way | 1.424 | 15.166 | 14.811 | 14.392 | 13.985 | 13.525 | 12.906 | 8.251 | 4.792 | 2.424 | 2.025 | Primary | 1114
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Leading the Way | 10.584 | 9.891 | 9.125 | 8.611 | 8.296 | 7.964 | 7.404 | 2.332 | -1.589 | -4.371 | -4.01 | Primary | 1115
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Leading the Way | 15.372 | 15.337 | 15.288 | 15.229 | 15.195 | 15.158 | 15.096 | 14.181 | 13.331 | 12.582 | 12.452 | Primary | 1116
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Leading the Way | 3.682 | 2.637 | 1.15 | -0.559 | -1.835 | -3.169 | -5.093 | -17.845 | -26.368 | -32.498 | -32.752 | Primary | 1117
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Leading the Way | 6.057 | 5.346 | 4.409 | 3.488 | 2.883 | 2.255 | 1.336 | -5.085 | -9.565 | -12.339 | -11.853 | Primary | 1118
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Leading the Way | 4.406 | 4.411 | 4.315 | 4.15 | 4.194 | 4.221 | 4.069 | 0.652 | -2.199 | -4.376 | -3.829 | Primary | 1119
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 17.143 | 14.113 | 13.815 | 13.478 | 13.219 | 12.953 | 12.604 | 9.608 | 7.425 | 5.605 | 5.339 | Primary | 1120
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Leading the Way | 14.753 | 14.715 | 14.652 | 14.567 | 14.482 | 14.378 | 14.241 | 12.757 | 11.541 | 10.67 | 10.543 | Primary | 1121
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Leading the Way | 9.232 | 9.009 | 8.721 | 8.368 | 7.997 | 7.561 | 7.02 | 2.675 | -0.799 | -3.177 | -3.956 | Primary | 1122
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Leading the Way | 11.726 | 11.702 | 11.617 | 11.494 | 11.472 | 11.444 | 11.332 | 8.82 | 6.771 | 5.206 | 5.624 | Primary | 1123
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Leading the Way | 11.293 | 11.336 | 11.34 | 11.318 | 11.342 | 11.359 | 11.327 | 10.404 | 9.704 | 9.246 | 9.574 | Primary | 1124
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 3.761 | 3.573 | 3.342 | 3.06 | 2.746 | 2.373 | 1.928 | -1.504 | -4.258 | -6.132 | -6.931 | Primary | 1125
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Leading the Way | 14.723 | 14.635 | 14.492 | 14.311 | 14.224 | 14.12 | 13.923 | 11.574 | 9.66 | 8.294 | 8.347 | Primary | 1126
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Leading the Way | 10.625 | 10.306 | 9.804 | 9.207 | 8.886 | 8.545 | 7.969 | 2.592 | -1.367 | -4.096 | -3.668 | Primary | 1127
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Leading the Way | 9.493 | 9.362 | 9.113 | 8.79 | 8.667 | 8.521 | 8.197 | 4.023 | 0.803 | -1.412 | -0.892 | Primary | 1128
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Leading the Way | 7.107 | 6.753 | 6.185 | 5.492 | 5.023 | 4.505 | 3.706 | -2.755 | -7.34 | -10.249 | -9.814 | Primary | 1129
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Leading the Way | 4.394 | 3.906 | 3.208 | 2.415 | 1.811 | 1.144 | 0.201 | 10.329 | 5.583 | 2.446 | 2.446 | Primary | 1130
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Leading the Way | 10.982 | 10.965 | 10.889 | 10.774 | 10.633 | 10.435 | 10.145 | 8.103 | 6.875 | 6.419 | 6.559 | Primary | 1131
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Leading the Way | 15.371 | 15.052 | 14.55 | 13.941 | 13.616 | 13.277 | 12.702 | 7.594 | 3.739 | 1.028 | 1.336 | Primary | 1132
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Leading the Way | 8.816 | 8.328 | 7.602 | 6.72 | 6.024 | 5.24 | 4.122 | -4.462 | -10.655 | -14.588 | -14.722 | Primary | 1133
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Leading the Way | 3.275 | 3.158 | 2.994 | 3.306 | 3.159 | 3.005 | 2.79 | 1.127 | -0.132 | -1.056 | -1.153 | Primary | 1134
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Leading the Way | 7.103 | 6.872 | 6.485 | 6.026 | 5.675 | 5.307 | 4.674 | 5.857 | 1.348 | -1.962 | -1.461 | Primary | 1135
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Leading the Way | 4.143 | 3.943 | 3.642 | 3.296 | 3.093 | 2.882 | 2.542 | -0.187 | -2.221 | -3.634 | -3.528 | Primary | 1136
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 12.31 | 12.293 | 12.247 | 12.181 | 12.149 | 12.109 | 12.029 | 10.809 | 9.801 | 8.997 | 8.999 | Primary | 1137
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 25.325 | 25.282 | 25.216 | 25.133 | 25.083 | 25.028 | 24.941 | 23.564 | 22.399 | 21.466 | 21.501 | Primary | 1138
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Leading the Way | 14.643 | 14.485 | 14.255 | 13.976 | 13.719 | 13.438 | 13.067 | 10.827 | 9.335 | 8.443 | 8.354 | Primary | 1139
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Leading the Way | 12.69 | 12.743 | 12.772 | 12.783 | 12.812 | 12.836 | 12.829 | 11.675 | 10.773 | 10.089 | 10.428 | Primary | 1140
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Leading the Way | 19.977 | 19.932 | 19.868 | 19.788 | 19.737 | 19.684 | 19.608 | 18.515 | 17.81 | 17.186 | 17.132 | Primary | 1141
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Leading the Way | 6.898 | 6.556 | 6.018 | 5.376 | 4.993 | 4.588 | 3.956 | -0.739 | -3.785 | -5.768 | -5.414 | Primary | 1142
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 21.099 | 21.089 | 20.997 | 20.85 | 20.809 | 20.75 | 20.572 | 17.583 | 15.261 | 13.602 | 14.124 | Primary | 1143
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Leading the Way | 14.006 | 13.926 | 13.784 | 13.615 | 13.586 | 13.552 | 13.408 | 10.574 | 8.271 | 6.563 | 7.037 | Primary | 1144
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Leading the Way | 4.252 | 4.153 | 3.998 | 3.813 | 3.704 | 3.586 | 3.391 | 1.72 | 0.502 | -0.317 | -0.214 | Primary | 1145
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Leading the Way | 0.965 | 0.925 | 0.872 | 0.807 | 0.748 | 0.68 | 0.592 | -0.024 | -0.524 | -0.879 | -1.062 | Primary | 1146
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Leading the Way | 16.228 | 16.138 | 15.987 | 15.791 | 15.654 | 15.492 | 15.241 | 12.258 | 9.909 | 8.163 | 8.164 | Primary | 1147
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 22.162 | 21.96 | 21.641 | 21.257 | 20.964 | 20.654 | 20.161 | 16.226 | 13.371 | 11.44 | 11.727 | Primary | 1148
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 26.324 | 26.224 | 26.063 | 25.87 | 25.751 | 25.626 | 25.403 | 23.272 | 21.648 | 20.494 | 20.69 | Primary | 1149
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Leading the Way | 2.373 | 2.227 | 2.034 | 1.82 | 1.623 | 1.419 | 1.134 | -0.941 | -2.574 | -3.854 | -4.08 | Primary | 1150
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Leading the Way | 2.282 | 2.048 | 1.719 | 1.326 | 1.098 | 0.837 | 0.417 | -4.828 | -9.117 | -12.369 | -12.438 | Primary | 1151
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Leading the Way | 14.335 | 14.278 | 14.167 | 14.016 | 13.891 | 13.727 | 13.481 | 11.627 | 10.431 | 9.734 | 9.73 | Primary | 1152
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Leading the Way | 4.592 | 4.502 | 4.365 | 4.207 | 4.099 | 3.986 | 3.791 | 2.051 | 0.724 | -0.238 | -0.124 | Primary | 1153
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Leading the Way | 14.496 | 14.473 | 14.421 | 14.368 | 14.343 | 14.304 | 14.188 | 12.665 | 11.62 | 10.872 | 11.049 | Primary | 1154
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Leading the Way | 9.126 | 9.249 | 9.349 | 9.428 | 9.517 | 9.592 | 9.634 | 10.172 | 9.82 | 9.647 | 10.02 | Primary | 1155
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Leading the Way | 1.179 | 0.83 | 0.327 | -0.263 | -0.737 | -1.241 | -1.921 | -6.319 | -9.376 | -11.276 | -11.391 | Primary | 1156
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 16.836 | 16.798 | 16.728 | 16.637 | 16.588 | 16.531 | 16.427 | 15.072 | 13.98 | 13.169 | 13.244 | Primary | 1157
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 16.764 | 16.719 | 16.639 | 16.533 | 16.457 | 16.363 | 16.215 | 14.804 | 13.723 | 13.037 | 13.043 | Primary | 1158
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Leading the Way | 4.394 | 3.972 | 3.367 | 2.662 | 2.121 | 1.544 | 0.707 | 9.172 | 4.656 | 1.454 | 1.293 | Primary | 1159
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Leading the Way | 14.347 | 14.24 | 14.079 | 13.881 | 13.769 | 13.646 | 13.44 | 10.942 | 8.982 | 7.508 | 7.584 | Primary | 1160
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Leading the Way | 7.842 | 7.269 | 6.511 | 5.771 | 5.179 | 4.561 | 3.624 | 13.507 | 8.317 | 4.658 | 4.891 | Primary | 1161
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Leading the Way | 4.915 | 4.82 | 4.649 | 4.455 | 4.341 | 4.195 | 3.888 | -0.172 | -3.236 | -5.427 | -4.985 | Primary | 1162
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Leading the Way | 10.372 | 10.062 | 9.555 | 8.927 | 8.536 | 8.127 | 7.415 | 0.546 | -4.954 | -9.094 | -8.811 | Primary | 1163
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Leading the Way | 0.143 | 0.044 | -0.09 | -0.247 | -0.352 | -0.468 | -0.648 | -2.59 | -4.106 | -5.262 | -5.319 | Primary | 1164
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Leading the Way | 13.28 | 12.971 | 12.502 | 11.967 | 11.589 | 11.185 | 10.555 | 5.508 | 1.786 | -0.749 | -0.534 | Primary | 1165
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Leading the Way | 17.504 | 17.494 | 17.464 | 17.42 | 17.392 | 17.356 | 17.288 | 16.037 | 15.061 | 14.348 | 14.533 | Primary | 1166
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Leading the Way | 12.598 | 12.37 | 12.062 | 11.713 | 11.544 | 11.364 | 11.065 | 7.811 | 5.103 | 2.999 | 2.816 | Primary | 1167
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Leading the Way | 6.93 | 6.806 | 6.621 | 6.389 | 6.205 | 6.003 | 5.673 | 2.381 | -0.356 | -2.445 | -2.545 | Primary | 1168
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Leading the Way | 9.393 | 9.257 | 9.024 | 8.711 | 8.492 | 8.222 | 7.759 | 2.962 | -0.921 | -3.655 | -3.728 | Primary | 1169
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Leading the Way | 15.303 | 15.287 | 15.27 | 15.25 | 15.227 | 15.203 | 15.177 | 15.997 | 15.791 | 15.569 | 15.365 | Primary | 1170
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Leading the Way | 16.384 | 16.286 | 16.119 | 15.914 | 15.749 | 15.572 | 15.296 | 12.734 | 10.859 | 9.524 | 9.699 | Primary | 1171
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Leading the Way | 12.83 | 12.666 | 12.414 | 12.11 | 11.904 | 11.691 | 11.325 | 7.777 | 5.219 | 3.203 | 3.308 | Primary | 1172
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Leading the Way | 10.391 | 9.896 | 9.294 | 8.792 | 8.506 | 8.204 | 7.712 | 3.208 | -0.175 | -2.53 | -2.184 | Primary | 1173
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Leading the Way | 9.445 | 8.942 | 8.236 | 7.495 | 7.007 | 6.493 | 5.68 | -0.864 | -5.467 | -8.591 | -8.207 | Primary | 1174
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Leading the Way | 2.197 | 2.243 | 2.279 | 2.306 | 2.334 | 2.355 | 2.361 | 2.161 | 2.023 | 1.968 | 2.115 | Primary | 1175
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Leading the Way | 9.704 | 9.013 | 8.179 | 7.478 | 7.001 | 6.505 | 5.699 | 15.684 | 10.309 | 6.425 | 6.796 | Primary | 1176
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Leading the Way | 4.558 | 4.342 | 4.002 | 3.563 | 3.255 | 2.886 | 2.306 | -4.292 | -9.395 | -13.051 | -12.991 | Primary | 1177
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Leading the Way | 3.317 | 2.901 | 2.313 | 1.633 | 1.133 | 0.618 | -0.112 | -5.986 | -10.447 | -13.783 | -13.914 | Primary | 1178
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Leading the Way | 23.141 | 23.105 | 22.982 | 22.799 | 22.765 | 22.719 | 22.54 | 18.865 | 16.048 | 13.956 | 14.577 | Primary | 1179
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Leading the Way | 6.326 | 6.13 | 5.858 | 5.546 | 5.312 | 5.057 | 4.709 | 1.703 | -0.696 | -2.462 | -2.75 | Primary | 1180
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Leading the Way | 6.75 | 6.741 | 6.725 | 6.703 | 6.692 | 6.679 | 6.656 | 6.42 | 6.257 | 6.153 | 6.185 | Primary | 1181
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Leading the Way | 11.54 | 10.856 | 9.833 | 8.625 | 7.894 | 7.124 | 5.929 | -3.522 | -10.408 | -15.299 | -15.247 | Primary | 1182
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Leading the Way | 21.154 | 21.167 | 21.124 | 21.016 | 20.849 | 20.599 | 20.249 | 17.822 | 16.337 | 15.86 | 15.939 | Primary | 1183
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Leading the Way | 11.218 | 10.967 | 10.575 | 10.119 | 9.846 | 9.553 | 9.065 | 4.393 | 0.875 | -1.561 | -1.184 | Primary | 1184
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Leading the Way | 12.609 | 12.43 | 12.145 | 11.747 | 11.292 | 10.713 | 9.904 | 3.714 | -0.645 | -3.154 | -3.348 | Primary | 1185
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Leading the Way | 0.144 | 0.045 | -0.103 | -0.283 | -0.443 | -0.623 | -0.874 | -3.087 | -4.781 | -6.003 | -6.127 | Primary | 1186
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Leading the Way | 6.903 | 1.037 | 0.68 | 0.265 | -0.049 | -0.38 | -0.846 | 4.457 | 1.943 | 0.239 | 0.173 | Primary | 1187
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 1188
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Leading the Way | 3.587 | 3.291 | 2.874 | 2.395 | 2.063 | 1.716 | 1.221 | -2.881 | -6.049 | -8.404 | -8.642 | Primary | 1189
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Leading the Way | 12.37 | 12.138 | 11.778 | 11.326 | 10.881 | 10.319 | 9.53 | 3.135 | -1.341 | -3.641 | -3.514 | Primary | 1190
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Leading the Way | 5.489 | 5.231 | 4.831 | 4.394 | 4.132 | 3.837 | 3.355 | -0.443 | -2.924 | -4.468 | -4.115 | Primary | 1191
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Leading the Way | 1.002 | 0.772 | 0.479 | 0.226 | 0.073 | -0.088 | -0.335 | -2.205 | -3.554 | -4.423 | -4.261 | Primary | 1192
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Leading the Way | 12.67 | 12.513 | 12.238 | 11.897 | 11.73 | 11.548 | 11.199 | 7.633 | 5.044 | 3.309 | 3.723 | Primary | 1193
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Leading the Way | 7.197 | 7.25 | 7.281 | 7.314 | 7.36 | 7.398 | 7.404 | 5.85 | 4.716 | 3.863 | 4.351 | Primary | 1194
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Leading the Way | 13.483 | 13.399 | 13.246 | 13.05 | 12.992 | 12.923 | 12.743 | 9.933 | 7.717 | 6.141 | 6.526 | Primary | 1195
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Leading the Way | 6.932 | 6.538 | 5.986 | 5.35 | 4.818 | 4.257 | 3.496 | -1.972 | -5.993 | -8.89 | -9.321 | Primary | 1196
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Leading the Way | 9.714 | 9.642 | 9.459 | 9.178 | 8.958 | 8.646 | 8.143 | 3.762 | 0.781 | -0.747 | -0.512 | Primary | 1197
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Leading the Way | 14.74 | 14.775 | 14.806 | 14.832 | 14.86 | 14.885 | 14.906 | 14.78 | 14.678 | 14.604 | 14.717 | Primary | 1198
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Leading the Way | 5.554 | 5.534 | 5.496 | 5.453 | 5.431 | 5.407 | 5.361 | 4.957 | 4.689 | 4.518 | 4.557 | Primary | 1199
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Leading the Way | 14.011 | 14.04 | 14.044 | 14.03 | 14.036 | 14.039 | 14.015 | 12.67 | 11.641 | 10.882 | 11.244 | Primary | 1200
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Leading the Way | 4.001 | 3.684 | 3.183 | 2.571 | 2.214 | 1.835 | 1.217 | -3.833 | -7.427 | -9.803 | -9.445 | Primary | 1201
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Leading the Way | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary | 1202
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Leading the Way | 8.712 | 7.598 | 6.886 | 6.057 | 5.493 | 4.907 | 3.993 | -3.602 | -9.347 | -13.543 | -13.362 | Primary | 1203
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Leading the Way | 8.674 | 8.06 | 7.183 | 6.237 | 22.772 | 22.18 | 21.241 | 13.639 | 8.148 | 4.455 | 4.852 | Primary | 1204
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Leading the Way | 3.249 | 3.331 | 3.381 | 3.402 | 3.425 | 3.437 | 3.374 | 1.352 | -0.327 | -1.64 | -1.217 | Primary | 1205
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Leading the Way | 1.839 | 1.51 | 1.04 | 0.484 | -0.053 | -0.608 | -1.408 | -7.713 | -12.65 | -16.516 | -16.71 | Primary | 1206
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Leading the Way | 14.388 | 14.197 | 13.904 | 13.572 | 13.337 | 13.09 | 12.679 | 8.839 | 5.857 | 3.665 | 3.898 | Primary | 1207
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Leading the Way | 5.601 | 5.074 | 4.274 | 3.325 | 2.722 | 2.076 | 1.112 | -6.778 | -12.619 | -16.608 | -16.57 | Primary | 1208
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Leading the Way | 4.917 | 3.928 | 3.535 | 3.12 | 2.853 | 2.549 | 2.013 | -2.769 | -6.31 | -8.7 | -8.329 | Primary | 1209
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Leading the Way | 14.926 | 14.714 | 14.388 | 14.018 | 13.817 | 13.605 | 13.235 | 10.114 | 7.932 | 6.373 | 6.554 | Primary | 1210
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Leading the Way | 3.493 | 3.163 | 2.65 | 2.046 | 1.671 | 1.26 | 0.599 | 9.524 | 5.361 | 2.592 | 2.909 | Primary | 1211
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Leading the Way | 6.743 | 6.452 | 6.052 | 5.579 | 5.249 | 4.88 | 4.352 | -0.745 | -4.79 | -7.676 | -7.885 | Primary | 1212
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Leading the Way | 8.228 | 7.735 | 7.03 | 6.231 | 5.72 | 5.184 | 4.386 | -1.762 | -6.105 | -8.87 | -8.528 | Primary | 1213
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Leading the Way | 5.937 | 5.58 | 5.064 | 4.465 | 3.964 | 3.441 | 2.735 | -1.725 | -4.898 | -6.961 | -7.037 | Primary | 1214
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Leading the Way | 1.106 | 0.326 | -0.652 | -1.518 | -2.182 | -2.876 | -4.005 | -13.217 | -19.997 | -24.696 | -23.969 | Primary | 1215
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Leading the Way | 9.687 | 9.148 | 8.416 | 7.681 | 7.272 | 6.843 | 6.122 | -0.159 | -4.8 | -7.984 | -7.526 | Primary | 1216
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Leading the Way | 10.623 | 10.112 | 9.422 | 8.731 | 8.211 | 7.637 | 6.774 | 0.134 | -4.618 | -7.597 | -7.357 | Primary | 1217
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Leading the Way | 12.36 | 12.348 | 12.275 | 12.147 | 12.041 | 11.89 | 11.643 | 8.598 | 6.38 | 5.127 | 5.506 | Primary | 1218
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Leading the Way | 8.59 | 8.463 | 8.263 | 8.027 | 7.865 | 7.692 | 7.4 | 4.508 | 2.375 | 0.862 | 1.087 | Primary | 1219
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Leading the Way | 2.883 | 2.806 | 2.655 | 2.452 | 2.324 | 2.158 | 1.885 | -0.771 | -2.699 | -3.77 | -3.551 | Primary | 1220
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Leading the Way | 12.841 | 12.616 | 12.257 | 11.83 | 11.566 | 11.289 | 10.83 | 6.723 | 3.658 | 1.504 | 1.795 | Primary | 1221
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Leading the Way | 18.286 | 18.196 | 18.032 | 17.82 | 17.658 | 17.486 | 17.208 | 15.002 | 13.373 | 12.223 | 12.332 | Primary | 1222
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Leading the Way | 15.454 | 15.34 | 15.165 | 14.952 | 14.858 | 14.758 | 14.568 | 12.085 | 9.992 | 8.398 | 8.48 | Primary | 1223
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Leading the Way | 2.74 | 2.38 | 1.835 | 1.112 | 0.431 | -0.426 | -1.619 | -9.836 | -14.866 | -17.878 | -18.119 | Primary | 1224
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Leading the Way | 9.819 | 9.86 | 9.863 | 9.838 | 9.844 | 9.833 | 9.768 | 7.844 | 6.418 | 5.431 | 5.863 | Primary | 1225
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Leading the Way | 6.129 | 5.973 | 5.738 | 5.448 | 5.261 | 5.038 | 4.685 | 1.406 | -0.926 | -2.523 | -2.52 | Primary | 1226
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Leading the Way | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary | 1227
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Leading the Way | 6.776 | 6.194 | 5.411 | 4.602 | 4.09 | 3.533 | 2.689 | -3.808 | -8.252 | -11.163 | -10.967 | Primary | 1228
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Leading the Way | 14.34 | 14.015 | 13.529 | 12.943 | 12.621 | 12.282 | 11.709 | 6.66 | 2.853 | 0.147 | 0.355 | Primary | 1229
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Leading the Way | 3.108 | 2.937 | 2.699 | 2.429 | 2.237 | 2.039 | 1.753 | -0.604 | -2.362 | -3.693 | -3.773 | Primary | 1230
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Leading the Way | 8.762 | 8.407 | 7.89 | 7.213 | 6.564 | 5.75 | 4.663 | -4.578 | -11.468 | -15.478 | -15.979 | Primary | 1231
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Leading the Way | 13.065 | 12.57 | 11.946 | 11.364 | 10.968 | 10.553 | 9.925 | 4.534 | 0.627 | -2.092 | -1.85 | Primary | 1232
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Leading the Way | 4.983 | 4.891 | 4.758 | 4.607 | 4.492 | 4.374 | 4.193 | 2.725 | 1.566 | 0.693 | 0.661 | Primary | 1233
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Leading the Way | 6.033 | 5.538 | 4.829 | 4.009 | 3.448 | 2.865 | 2 | -5.648 | -11.485 | -15.922 | -15.958 | Primary | 1234
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Leading the Way | 9.941 | 9.617 | 9.095 | 8.464 | 8.067 | 7.648 | 6.933 | 0.738 | -3.776 | -6.962 | -6.468 | Primary | 1235
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Leading the Way | 15.547 | 15.241 | 14.835 | 14.436 | 14.143 | 13.841 | 13.378 | 9.832 | 7.144 | 5.227 | 5.395 | Primary | 1236
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Leading the Way | 6.061 | 5.823 | 5.409 | 4.89 | 4.611 | 4.304 | 3.766 | -1.531 | -5.321 | -7.912 | -7.412 | Primary | 1237
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Leading the Way | 12.895 | 12.434 | 11.814 | 11.111 | 10.448 | 9.738 | 8.79 | 1.982 | -3.017 | -6.656 | -7.173 | Primary | 1238
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Leading the Way | 12.783 | 12.713 | 12.596 | 12.448 | 12.388 | 12.322 | 12.185 | 10.282 | 8.892 | 7.842 | 7.999 | Primary | 1239
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Leading the Way | 9.278 | 8.889 | 8.329 | 7.698 | 7.266 | 6.79 | 6.109 | 1.189 | -2.253 | -4.441 | -4.465 | Primary | 1240
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Leading the Way | 11.371 | 11.379 | 11.327 | 11.22 | 11.132 | 11.001 | 10.781 | 8.422 | 6.776 | 5.878 | 6.149 | Primary | 1241
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Leading the Way | 5.568 | 5.472 | 5.262 | 4.968 | 4.794 | 4.561 | 4.156 | -0.173 | -3.242 | -5.066 | -4.644 | Primary | 1242
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Leading the Way | 28.572 | 28.484 | 28.34 | 28.153 | 27.996 | 27.809 | 27.547 | 25.357 | 23.718 | 22.689 | 22.602 | Primary | 1243
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Leading the Way | 3.153 | 2.93 | 2.645 | 2.313 | 2.07 | 1.811 | 1.408 | -2.8 | -6.543 | -9.684 | -10.365 | Primary | 1244
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Leading the Way | 1.901 | 1.863 | 1.802 | 1.73 | 1.672 | 1.61 | 1.527 | 0.969 | 0.553 | 0.245 | 0.173 | Primary | 1245
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Leading the Way | 11.63 | 11.296 | 10.836 | 10.327 | 9.98 | 9.614 | 9.079 | 4.239 | 0.552 | -2.165 | -2.195 | Primary | 1246
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Leading the Way | 9.904 | 9.903 | 9.854 | 9.771 | 9.752 | 9.717 | 9.606 | 7.652 | 6.235 | 5.245 | 5.55 | Primary | 1247
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Leading the Way | 10.723 | 10.637 | 10.456 | 10.205 | 10.084 | 9.951 | 9.607 | 4.286 | -0.199 | -3.717 | -3.213 | Primary | 1248
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Leading the Way | 1.805 | 1.728 | 1.615 | 1.475 | 1.361 | 1.227 | 1.043 | -0.656 | -1.909 | -2.812 | -2.904 | Primary | 1249
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Leading the Way | 11.862 | 11.847 | 11.764 | 11.604 | 11.379 | 11.059 | 10.608 | 6.373 | 3.367 | 1.889 | 2.113 | Primary | 1250
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Leading the Way | 15.675 | 15.626 | 15.542 | 15.457 | 15.406 | 15.343 | 15.225 | 13.753 | 12.668 | 11.951 | 12.152 | Primary | 1251
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Leading the Way | 7.731 | 6.506 | 5.803 | 4.986 | 4.376 | 3.737 | 2.805 | -4.96 | -10.753 | -15.123 | -15.311 | Primary | 1252
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Leading the Way | 11.965 | 11.861 | 11.667 | 11.427 | 11.273 | 11.107 | 10.803 | 8.135 | 6.15 | 4.778 | 5.084 | Primary | 1253
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Leading the Way | 15.91 | 15.941 | 15.852 | 15.635 | 15.317 | 14.845 | 14.165 | 8.789 | 5.246 | 3.963 | 4.259 | Primary | 1254
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Leading the Way | 8.721 | 8.318 | 7.672 | 6.901 | 6.485 | 6.033 | 5.237 | -2.148 | -7.624 | -11.302 | -10.672 | Primary | 1255
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Leading the Way | 4.247 | 4.189 | 4.1 | 3.994 | 3.922 | 3.845 | 3.729 | 2.803 | 2.103 | 1.595 | 1.564 | Primary | 1256
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Leading the Way | 8.799 | 8.395 | 7.831 | 7.249 | 6.942 | 6.614 | 6.029 | 0.531 | -3.304 | -5.856 | -5.24 | Primary | 1257
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 14.483 | 14.309 | 14.033 | 13.686 | 13.458 | 13.201 | 12.806 | 8.44 | 4.931 | 2.265 | 2.154 | Primary | 1258
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 13.457 | 13.316 | 13.085 | 12.783 | 12.577 | 12.343 | 11.98 | 6.9 | 2.569 | -0.865 | -0.97 | Primary | 1259
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Leading the Way | 12.317 | 12.319 | 12.282 | 12.222 | 12.192 | 12.145 | 12.046 | 10.174 | 8.799 | 7.923 | 8.34 | Primary | 1260
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Leading the Way | 8.13 | 8.162 | 8.15 | 8.104 | 8.139 | 8.167 | 8.121 | 6.655 | 5.459 | 4.562 | 4.922 | Primary | 1261
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Leading the Way | 17.514 | 17.383 | 17.175 | 16.925 | 16.77 | 16.603 | 16.351 | 14.361 | 12.924 | 12.009 | 12.13 | Primary | 1262
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Leading the Way | 4.956 | 4.953 | 4.932 | 4.894 | 4.844 | 4.777 | 4.683 | 3.747 | 2.913 | 2.258 | 1.976 | Primary | 1263
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Leading the Way | 2.194 | 1.708 | 1.055 | 0.412 | 0.029 | -0.373 | -1.043 | -6.969 | -11.357 | -14.36 | -13.865 | Primary | 1264
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Leading the Way | 11.473 | 11.068 | 10.522 | 9.969 | 9.592 | 9.2 | 8.575 | 3.31 | -0.625 | -3.355 | -2.982 | Primary | 1265
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Leading the Way | 10.023 | 9.506 | 8.771 | 7.98 | 7.478 | 6.921 | 6.042 | -1.237 | -6.461 | -9.637 | -9.094 | Primary | 1266
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 13.004 | 13.014 | 12.978 | 12.899 | 12.813 | 12.685 | 12.493 | 10.505 | 9.129 | 8.463 | 8.698 | Primary | 1267
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Leading the Way | 16.045 | 15.832 | 15.492 | 15.084 | 14.844 | 14.591 | 14.175 | 10.78 | 8.339 | 6.722 | 6.983 | Primary | 1268
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Leading the Way | 12.848 | 12.736 | 12.529 | 12.261 | 12.053 | 11.829 | 11.44 | 7.539 | 4.699 | 2.695 | 3.132 | Primary | 1269
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Leading the Way | 9.39 | 9.129 | 8.705 | 8.193 | 7.858 | 7.478 | 6.883 | 1.711 | -2.01 | -4.349 | -3.993 | Primary | 1270
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Leading the Way | 11.547 | 9.837 | 9.588 | 9.267 | 9.09 | 8.902 | 8.539 | 5.152 | 2.658 | 0.822 | 1.102 | Primary | 1271
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Leading the Way | 4.124 | 4.001 | 3.83 | 3.643 | 3.49 | 3.33 | 3.105 | 1.394 | 0.14 | -0.753 | -0.763 | Primary | 1272
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Leading the Way | 13.927 | 13.474 | 12.811 | 12.059 | 11.544 | 11.002 | 10.182 | 3.807 | -0.79 | -3.965 | -3.879 | Primary | 1273
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Leading the Way | 2.165 | 1.804 | 1.211 | 0.498 | -0.005 | -0.536 | -1.43 | -9.263 | -15.15 | -19.33 | -18.717 | Primary | 1274
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Leading the Way | 14.589 | 14.306 | 13.883 | 13.411 | 13.1 | 12.767 | 12.249 | 8.19 | 5.234 | 3.248 | 3.414 | Primary | 1275
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Leading the Way | 7.622 | 7.171 | 6.507 | 5.768 | 5.321 | 4.851 | 4.104 | -2.764 | -7.937 | -11.624 | -11.28 | Primary | 1276
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Leading the Way | 18.617 | 18.657 | 18.608 | 18.489 | 18.448 | 18.382 | 18.155 | 13.967 | 10.56 | 8.028 | 8.668 | Primary | 1277
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Leading the Way | 12.575 | 12.433 | 12.218 | 11.977 | 11.781 | 11.567 | 11.263 | 8.87 | 7.176 | 6.129 | 6.342 | Primary | 1278
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Leading the Way | 3.323 | 2.976 | 2.461 | 1.85 | 1.421 | 0.959 | 0.275 | -5.627 | -10.042 | -13.175 | -13.218 | Primary | 1279
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Leading the Way | 3.388 | 2.441 | 1.179 | -0.24 | -1.617 | -3.06 | -4.99 | -17.273 | -26.349 | -32.866 | -33.934 | Primary | 1280
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Leading the Way | 3.907 | 3.457 | 2.818 | 2.149 | 1.664 | 1.151 | 0.288 | 10.081 | 4.893 | 1.056 | 1.382 | Primary | 1281
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Leading the Way | 12.492 | 11.98 | 11.27 | 10.468 | 9.95 | 9.415 | 8.63 | 2.68 | -1.813 | -5.033 | -5.179 | Primary | 1282
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Leading the Way | 21.734 | 18.772 | 18.871 | 18.957 | 19.037 | 19.114 | 19.189 | 18.768 | 18.582 | 18.435 | 18.561 | Primary | 1283
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Leading the Way | 3.44 | 3.1 | 2.617 | 2.017 | 1.464 | 0.781 | -0.117 | -6.691 | -11.17 | -13.909 | -14.408 | Primary | 1284
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Leading the Way | 12.606 | 12.468 | 12.235 | 11.958 | 11.893 | 11.819 | 11.582 | 7.855 | 4.828 | 2.552 | 2.95 | Primary | 1285
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Leading the Way | 14.047 | 14.114 | 14.161 | 14.196 | 14.26 | 14.319 | 14.352 | 14.026 | 13.781 | 13.62 | 13.857 | Primary | 1286
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Leading the Way | 15.002 | 15.042 | 15.057 | 15.053 | 15.078 | 15.099 | 15.085 | 14.109 | 13.382 | 12.841 | 13.112 | Primary | 1287
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Leading the Way | 9.65 | 9.081 | 8.244 | 7.266 | 6.611 | 5.923 | 4.909 | -2.486 | -7.892 | -11.58 | -11.567 | Primary | 1288
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Leading the Way | 15.789 | 15.692 | 15.544 | 15.362 | 15.276 | 15.18 | 14.995 | 12.344 | 10.105 | 8.358 | 8.393 | Primary | 1289
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Leading the Way | 5.507 | 5.416 | 5.237 | 5.003 | 4.92 | 4.825 | 4.587 | 0.552 | -2.679 | -5.069 | -4.514 | Primary | 1290
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Leading the Way | 14.008 | 13.826 | 13.537 | 13.193 | 12.951 | 12.69 | 12.297 | 8.868 | 6.409 | 4.779 | 5.031 | Primary | 1291
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Leading the Way | 18.295 | 14.835 | 14.759 | 14.672 | 14.612 | 14.544 | 14.428 | 13.797 | 13.483 | 13.328 | 13.438 | Primary | 1292
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Leading the Way | 11.563 | 11.326 | 10.993 | 10.626 | 10.385 | 10.129 | 9.75 | 6.71 | 4.429 | 2.859 | 2.813 | Primary | 1293
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Leading the Way | 2.504 | 2.289 | 1.974 | 1.594 | 1.302 | 0.967 | 0.498 | -3.082 | -5.697 | -7.27 | -7.336 | Primary | 1294
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Leading the Way | 10.901 | 10.526 | 9.989 | 9.414 | 9.08 | 8.729 | 8.182 | 4.033 | 1.026 | -0.979 | -0.801 | Primary | 1295
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Leading the Way | 10.039 | 9.717 | 9.207 | 8.601 | 8.249 | 7.87 | 7.237 | 3.015 | -0.57 | -2.976 | -2.592 | Primary | 1296
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Leading the Way | 5.736 | 5.486 | 5.111 | 4.615 | 4.15 | 3.59 | 2.774 | -4.128 | -9.108 | -12.545 | -12.886 | Primary | 1297
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Leading the Way | 16.369 | 16.22 | 16.009 | 15.759 | 15.558 | 15.346 | 15.041 | 12.626 | 10.728 | 9.308 | 9.149 | Primary | 1298
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Leading the Way | 8.836 | 6.995 | 6.462 | 5.798 | 5.305 | 4.728 | 3.813 | 2.502 | -3.777 | -8.109 | -8.287 | Primary | 1299
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Leading the Way | 3.8 | 3.649 | 3.438 | 3.197 | 3.009 | 2.815 | 2.549 | 0.614 | -0.803 | -1.826 | -1.931 | Primary | 1300
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Leading the Way | 14.363 | 14.052 | 13.573 | 13.005 | 12.618 | 12.21 | 11.609 | 7.188 | 4.115 | 2.157 | 2.417 | Primary | 1301
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Leading the Way | -0.322 | -0.562 | -0.901 | -0.292 | -0.617 | -0.967 | -1.47 | -5.511 | -8.371 | -10.43 | -10.447 | Primary | 1302
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Leading the Way | 9.189 | 8.839 | 8.327 | 7.733 | 7.303 | 6.846 | 6.177 | 0.319 | -4.261 | -7.655 | -7.733 | Primary | 1303
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Leading the Way | 7.728 | 7.412 | 6.905 | 6.297 | 5.916 | 5.503 | 4.837 | -1.246 | -5.666 | -8.653 | -8.212 | Primary | 1304
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Leading the Way | 4.997 | 4.495 | 3.772 | 2.933 | 2.344 | 1.723 | 0.824 | -7.529 | -13.93 | -18.787 | -18.903 | Primary | 1305
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Leading the Way | 16.081 | 15.749 | 15.24 | 14.642 | 14.23 | 13.783 | 13.117 | 7.791 | 4.19 | 1.876 | 2.169 | Primary | 1306
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Leading the Way | 7.888 | 7.923 | 7.899 | 7.829 | 7.816 | 7.778 | 7.657 | 5.375 | 3.705 | 2.623 | 3.099 | Primary | 1307
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Leading the Way | 13.822 | 14.519 | 14.103 | 5.651 | 4.92 | 4.16 | 3.017 | -4.198 | -8.476 | -11.832 | -11.967 | Primary | 1308
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Leading the Way | 10.958 | 10.506 | 9.859 | 9.103 | 8.503 | 7.869 | 6.976 | 0.446 | -4.418 | -7.784 | -7.96 | Primary | 1309
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Leading the Way | 6.628 | 6.631 | 6.554 | 6.42 | 6.4 | 6.36 | 6.199 | 3.372 | 1.597 | 0.3 | 0.695 | Primary | 1310
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Leading the Way | 11.781 | 11.366 | 10.752 | 10.04 | 9.594 | 9.127 | 8.397 | 2.534 | -1.672 | -4.533 | -4.216 | Primary | 1311
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Leading the Way | 5.082 | 4.54 | 3.788 | 2.899 | 2.15 | 1.33 | 0.233 | -8.871 | -15.934 | -21.085 | -21.955 | Primary | 1312
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Leading the Way | 10.367 | 10.461 | 10.549 | 10.629 | 10.705 | 10.777 | 10.844 | 10.759 | 10.682 | 10.63 | 10.9 | Primary | 1313
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Leading the Way | 11.306 | 11.406 | 11.478 | 11.521 | 11.533 | 11.512 | 11.454 | 10.365 | 9.653 | 9.398 | 9.714 | Primary | 1314
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Leading the Way | 2.513 | 2.596 | 2.667 | 2.73 | 2.791 | 2.846 | 2.889 | 2.636 | 2.45 | 2.351 | 2.628 | Primary | 1315
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Leading the Way | 6.401 | 6.183 | 5.862 | 5.525 | 5.323 | 5.104 | 4.743 | 1.857 | 0.085 | -1.023 | -0.65 | Primary | 1316
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Leading the Way | 0.606 | 0.407 | 0.142 | -0.147 | -0.395 | -0.66 | -1.022 | -3.573 | -5.461 | -6.755 | -6.913 | Primary | 1317
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Leading the Way | 12.457 | 12.186 | 11.784 | 11.302 | 10.928 | 10.521 | 9.945 | 5.241 | 1.843 | -0.311 | -0.029 | Primary | 1318
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Leading the Way | 12.912 | 10.99 | 10.963 | 10.895 | 10.815 | 10.695 | 10.481 | 7.598 | 6.183 | 5.203 | 5.516 | Primary | 1319
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Leading the Way | 9.202 | 8.836 | 15.333 | 14.832 | 14.495 | 14.138 | 13.568 | 8.826 | 5.351 | 2.949 | 3.24 | Primary | 1320
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Leading the Way | 10.084 | 9.949 | 9.748 | 9.493 | 9.332 | 9.139 | 8.819 | 5.131 | 2.064 | -0.185 | -0.317 | Primary | 1321
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Leading the Way | 3.213 | 1.494 | 0.912 | 0.449 | 0.133 | -0.206 | -0.805 | -6.605 | -11.105 | -14.426 | -14.066 | Primary | 1322
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Leading the Way | 12.593 | 12.566 | 12.515 | 12.448 | 12.424 | 12.396 | 12.331 | 11.183 | 10.171 | 9.331 | 9.304 | Primary | 1323
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Leading the Way | 8.423 | 8.26 | 14.959 | 14.582 | 14.401 | 14.197 | 13.807 | 9.455 | 6.212 | 4.036 | 4.597 | Primary | 1324
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Leading the Way | 4.967 | 3.676 | 2.921 | 2.301 | 1.813 | 1.275 | 0.501 | -5.8 | -10.36 | -13.571 | -13.584 | Primary | 1325
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Leading the Way | 10.191 | 9.726 | 9.021 | 8.198 | 7.736 | 7.254 | 6.456 | -0.27 | -5.28 | -8.734 | -8.344 | Primary | 1326
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Leading the Way | 10.258 | 10.055 | 7.583 | 7.082 | 6.581 | 5.935 | 5.06 | -1.145 | -5.317 | -7.496 | -7.832 | Primary | 1327
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Leading the Way | 8.341 | 7.884 | 7.222 | 6.454 | 5.926 | 5.357 | 4.532 | -1.493 | -5.802 | -8.655 | -8.723 | Primary | 1328
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Leading the Way | 6.837 | 4.796 | 4.089 | 3.322 | 2.85 | 2.343 | 1.49 | -5.399 | -10.064 | -13.328 | -12.93 | Primary | 1329
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Leading the Way | 8.556 | 7.894 | 7.943 | 7.943 | 7.912 | 7.836 | 7.708 | 5.224 | 3.507 | 2.485 | 2.95 | Primary | 1330
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Leading the Way | 18.747 | 18.702 | 18.608 | 18.463 | 18.288 | 18.052 | 17.734 | 15.087 | 13.295 | 12.457 | 12.542 | Primary | 1331
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Leading the Way | 8.668 | 8.55 | 8.312 | 8.011 | 7.863 | 7.703 | 7.374 | 4.043 | 1.466 | -0.388 | -0.036 | Primary | 1332
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Leading the Way | 10.697 | 10.506 | 10.22 | 9.88 | 9.562 | 9.217 | 8.71 | 4.613 | 1.552 | -0.599 | -0.508 | Primary | 1333
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Leading the Way | 12.041 | 11.759 | 11.313 | 10.774 | 10.471 | 10.153 | 9.617 | 4.243 | 0.333 | -2.428 | -1.944 | Primary | 1334
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Leading the Way | 12.303 | 12.274 | 12.19 | 12.071 | 12.029 | 11.969 | 11.833 | 9.817 | 8.295 | 7.294 | 7.612 | Primary | 1335
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Leading the Way | 8.387 | 8.508 | 8.617 | 8.73 | 8.842 | 8.946 | 9.03 | 8.678 | 8.408 | 8.227 | 8.669 | Primary | 1336
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Leading the Way | 8.067 | 6.232 | 6.019 | 5.754 | 5.676 | 5.565 | 5.27 | 1.525 | -1.286 | -3.175 | -2.698 | Primary | 1337
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Leading the Way | 9.965 | 8.795 | 8.871 | 8.928 | 8.992 | 9.049 | 9.083 | 8.127 | 7.437 | 6.929 | 7.339 | Primary | 1338
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Leading the Way | 1.203 | 0.99 | 0.694 | 0.355 | 0.106 | -0.156 | -0.532 | -3.68 | -6.035 | -7.809 | -7.95 | Primary | 1339
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 2.861 | 2.817 | 2.744 | 2.668 | 2.657 | 2.643 | 2.59 | 1.556 | 0.696 | 0.049 | 0.176 | Primary | 1340
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Leading the Way | 12.891 | 12.785 | 12.609 | 12.374 | 12.166 | 11.906 | 11.549 | 8.443 | 6.125 | 4.767 | 4.702 | Primary | 1341
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Leading the Way | 24.496 | 24.539 | 24.575 | 24.6 | 24.618 | 24.634 | 24.646 | 23.9 | 23.292 | 22.73 | 22.76 | Primary | 1342
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Leading the Way | 13.819 | 13.848 | 13.839 | 13.806 | 13.815 | 13.819 | 13.768 | 12.658 | 11.777 | 11.111 | 11.383 | Primary | 1343
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Leading the Way | -1.725 | -1.841 | -2.011 | -2.221 | -2.391 | -2.581 | -2.847 | -5.459 | -7.653 | -9.35 | -9.69 | Primary | 1344
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Leading the Way | 3.242 | 2.941 | 2.508 | 1.95 | 1.443 | 0.821 | -0.028 | -8.062 | -14.208 | -18.331 | -18.779 | Primary | 1345
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Leading the Way | 10.995 | 10.813 | 10.493 | 10.099 | 9.869 | 9.625 | 9.203 | 5.31 | 2.398 | 0.385 | 0.781 | Primary | 1346
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Leading the Way | 11.361 | 11.469 | 11.558 | 11.628 | 11.679 | 11.709 | 11.715 | 11.354 | 11.167 | 11.2 | 11.47 | Primary | 1347
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Leading the Way | 8.099 | 7.665 | 7.011 | 6.233 | 5.691 | 5.099 | 4.191 | -3.536 | -9.311 | -13.263 | -13.076 | Primary | 1348
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Leading the Way | 11.761 | 10.999 | 10.757 | 10.467 | 10.309 | 10.144 | 9.825 | 6.125 | 3.544 | 1.384 | 1.384 | Primary | 1349
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Leading the Way | 4.051 | 3.713 | 3.264 | 2.825 | 2.494 | 2.152 | 1.611 | -2.585 | -5.807 | -8.136 | -7.952 | Primary | 1350
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Leading the Way | 10.988 | 10.798 | 10.458 | 10.021 | 9.726 | 9.415 | 8.871 | 3.87 | -0.023 | -2.904 | -2.652 | Primary | 1351
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Leading the Way | -1.241 | -1.447 | -1.749 | -2.094 | -0.311 | -0.538 | -0.913 | -4.623 | -7.504 | -9.624 | -9.43 | Primary | 1352
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Leading the Way | 15.288 | 15.22 | 15.109 | 14.952 | 14.795 | 14.6 | 14.327 | 11.274 | 8.889 | 7.236 | 7.238 | Primary | 1353
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Leading the Way | 14.374 | 13.705 | 12.981 | 12.503 | 12.122 | 11.712 | 11.095 | 5.956 | 2.133 | -0.475 | -0.278 | Primary | 1354
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Leading the Way | 10.068 | 9.678 | 9.072 | 8.361 | 7.947 | 7.507 | 6.823 | 1.31 | -2.663 | -5.267 | -5.003 | Primary | 1355
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Leading the Way | 23.772 | 23.818 | 23.858 | 23.9 | 23.943 | 23.983 | 24.013 | 23.796 | 23.621 | 23.492 | 23.674 | Primary | 1356
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Leading the Way | 8.541 | 8.575 | 8.6 | 8.631 | 8.66 | 8.686 | 8.697 | 7.409 | 6.536 | 5.846 | 6.152 | Primary | 1357
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Leading the Way | 11.273 | 10.971 | 10.491 | 9.91 | 9.582 | 9.239 | 8.678 | 3.995 | 0.537 | -1.852 | -1.596 | Primary | 1358
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Leading the Way | 4.364 | 4.352 | 4.329 | 4.299 | 4.288 | 4.274 | 4.245 | 3.857 | 3.501 | 3.2 | 3.14 | Primary | 1359
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Leading the Way | 8.842 | 8.73 | 8.568 | 8.373 | 8.241 | 8.097 | 7.883 | 5.456 | 3.379 | 1.722 | 1.53 | Primary | 1360
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Leading the Way | 13.847 | 13.564 | 13.126 | 12.612 | 12.309 | 11.99 | 11.447 | 6.68 | 3.028 | 0.379 | 0.557 | Primary | 1361
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Leading the Way | 10.76 | 10.424 | 9.955 | 9.418 | 9.04 | 8.639 | 8.043 | 3.412 | 0.093 | -2.226 | -2.201 | Primary | 1362
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Leading the Way | 7.836 | 7.459 | 6.903 | 6.24 | 5.658 | 5.037 | 4.182 | -1.729 | -6.016 | -8.998 | -9.223 | Primary | 1363
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Leading the Way | 13.078 | 12.822 | 12.498 | 12.118 | 11.767 | 11.373 | 10.856 | 6.329 | 2.656 | -0.161 | -0.849 | Primary | 1364
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Leading the Way | 7.737 | 7.695 | 7.56 | 7.35 | 7.198 | 6.999 | 6.607 | 1.852 | -1.875 | -4.421 | -3.962 | Primary | 1365
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Leading the Way | 13.762 | 13.499 | 13.088 | 12.604 | 12.333 | 12.047 | 11.578 | 7.545 | 4.538 | 2.461 | 2.678 | Primary | 1366
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Leading the Way | 7.195 | 6.745 | 6.133 | 5.521 | 5.109 | 4.674 | 3.953 | 14.56 | 9.826 | 6.393 | 6.766 | Primary | 1367
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Leading the Way | 7.474 | 7.294 | 7.045 | 6.744 | 6.526 | 6.283 | 5.941 | 1.596 | -2.051 | -4.937 | -5.194 | Primary | 1368
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - System Transformation | 12.952 | 12.66 | 12.454 | 12.393 | 12.336 | 12.271 | 12.199 | 11.762 | 10.882 | 9.519 | 7.432 | Primary | 1369
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - System Transformation | 12.224 | 10.584 | 10.505 | 10.385 | 10.253 | 10.08 | 9.859 | 8.357 | 6.144 | 4.177 | 1.764 | Primary | 1370
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - System Transformation | 11.416 | 11.146 | 10.811 | 10.413 | 9.928 | 9.417 | 8.884 | 6.205 | 3.104 | -0.373 | -4.769 | Primary | 1371
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - System Transformation | 5.954 | 4.576 | 4.577 | 4.535 | 4.471 | 4.376 | 4.233 | 3.458 | 1.463 | -0.166 | -1.928 | Primary | 1372
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 15.301 | 14.897 | 14.461 | 14.063 | 13.672 | 13.273 | 12.863 | 10.983 | 8.863 | 6.285 | 2.468 | Primary | 1373
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 17.117 | 17.105 | 17.085 | 17.064 | 17.04 | 17.011 | 16.978 | 16.788 | 16.473 | 16.077 | 15.504 | Primary | 1374
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - System Transformation | 8.928 | 8.424 | 7.821 | 7.166 | 6.513 | 5.838 | 5.133 | 1.724 | -1.816 | -6.125 | -12.046 | Primary | 1375
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - System Transformation | 17.161 | 17.175 | 17.171 | 17.155 | 17.14 | 17.117 | 17.076 | 16.877 | 15.794 | 14.673 | 13.234 | Primary | 1376
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - System Transformation | 0.974 | 0.765 | 0.498 | 0.187 | -0.15 | -0.504 | -0.876 | -2.743 | -5.63 | -8.767 | -12.888 | Primary | 1377
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - System Transformation | 3.294 | 2.763 | 2.859 | 2.929 | 2.989 | 3.033 | 3.054 | 3.031 | 2.257 | 1.478 | 0.528 | Primary | 1378
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - System Transformation | 11.964 | 11.735 | 11.425 | 11.066 | 10.709 | 10.338 | 9.943 | 9.126 | 6.934 | 4.497 | 1.187 | Primary | 1379
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - System Transformation | 2.516 | 2.184 | 1.832 | 1.503 | 1.14 | 0.736 | 0.275 | -2.088 | -5.288 | -8.047 | -11.184 | Primary | 1380
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - System Transformation | 3.306 | 3.287 | 3.261 | 3.228 | 3.191 | 3.149 | 3.1 | 2.85 | 2.494 | 2.17 | 1.833 | Primary | 1381
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - System Transformation | 15.697 | 15.523 | 15.287 | 15.022 | 14.779 | 14.53 | 14.263 | 13.007 | 11.106 | 8.829 | 5.524 | Primary | 1382
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - System Transformation | 12.996 | 12.453 | 12.392 | 12.318 | 12.249 | 12.173 | 12.086 | 11.625 | 10.776 | 9.781 | 8.512 | Primary | 1383
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - System Transformation | 10.563 | 10.556 | 10.518 | 10.454 | 10.38 | 10.289 | 10.169 | 9.499 | 7.853 | 6.351 | 4.618 | Primary | 1384
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - System Transformation | 15.525 | 15.22 | 14.826 | 14.379 | 13.909 | 13.415 | 12.895 | 10.293 | 7.815 | 5.127 | 1.558 | Primary | 1385
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - System Transformation | 8.324 | 8.336 | 8.33 | 8.308 | 8.281 | 8.242 | 8.188 | 7.766 | 6.704 | 5.673 | 4.368 | Primary | 1386
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - System Transformation | 5.727 | 5.572 | 5.377 | 5.147 | 4.91 | 4.658 | 4.382 | 2.919 | 0.13 | -3.08 | -7.269 | Primary | 1387
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - System Transformation | 21.389 | 21.331 | 21.23 | 21.097 | 20.968 | 20.832 | 20.687 | 19.995 | 19.141 | 18.101 | 16.565 | Primary | 1388
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - System Transformation | 3.624 | 3.474 | 3.306 | 3.128 | 2.961 | 2.788 | 2.604 | 1.601 | 0.036 | -1.805 | -4.227 | Primary | 1389
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - System Transformation | 11.425 | 10.977 | 10.42 | 9.795 | 9.155 | 8.479 | 7.754 | 4.008 | -0.013 | -4.525 | -10.515 | Primary | 1390
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - System Transformation | 9.295 | 8.838 | 8.307 | 7.77 | 7.247 | 6.702 | 6.127 | 3.6 | 0.656 | -2.585 | -7.15 | Primary | 1391
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - System Transformation | 14.593 | 14.35 | 14.062 | 13.777 | 13.467 | 13.148 | 12.822 | 11.325 | 10.052 | 8.45 | 6.142 | Primary | 1392
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - System Transformation | 2.925 | 2.879 | 2.765 | 2.598 | 2.421 | 2.208 | 1.945 | 0.292 | -2.281 | -4.953 | -8.494 | Primary | 1393
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - System Transformation | 5.323 | 5.09 | 4.795 | 4.457 | 4.111 | 3.743 | 3.35 | 1.326 | -0.855 | -2.99 | -5.552 | Primary | 1394
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 15.131 | 15.089 | 15.036 | 14.972 | 14.896 | 14.807 | 14.699 | 14.203 | 13.176 | 12.129 | 10.808 | Primary | 1395
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 4.192 | 1.186 | 1.128 | 1.03 | 0.886 | 0.69 | 0.429 | -1.24 | -4.589 | -7.655 | -11.297 | Primary | 1396
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - System Transformation | 7.357 | 7.24 | 7.065 | 6.838 | 6.585 | 6.292 | 5.947 | 3.807 | 0.63 | -2.339 | -5.889 | Primary | 1397
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - System Transformation | 11.614 | 11.328 | 10.949 | 10.514 | 10.101 | 9.672 | 9.225 | 7.019 | 4.18 | 0.584 | -4.796 | Primary | 1398
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - System Transformation | 5.695 | 5.24 | 4.646 | 3.968 | 3.304 | 2.601 | 1.85 | -2.016 | -6.967 | -12.095 | -18.984 | Primary | 1399
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - System Transformation | 6.871 | 6.852 | 6.829 | 6.804 | 6.778 | 6.752 | 6.723 | 6.583 | 6.285 | 5.981 | 5.626 | Primary | 1400
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - System Transformation | 3.671 | 3.625 | 3.567 | 3.501 | 3.429 | 3.35 | 3.262 | 2.782 | 2.073 | 1.444 | 0.755 | Primary | 1401
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - System Transformation | 11.531 | 11.173 | 10.716 | 10.203 | 9.711 | 9.201 | 8.66 | 6.075 | 3.132 | -0.389 | -5.441 | Primary | 1402
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 13.449 | 13.305 | 13.156 | 12.998 | 12.833 | 12.663 | 12.483 | 11.548 | 9.891 | 8.221 | 6.476 | Primary | 1403
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - System Transformation | 4.597 | 4.483 | 4.341 | 4.183 | 4.028 | 3.87 | 3.705 | 2.928 | 2.141 | 1.307 | 0.205 | Primary | 1404
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 9.331 | 9.007 | 8.583 | 8.109 | 7.655 | 7.181 | 6.675 | 4.244 | 1.062 | -2.507 | -7.54 | Primary | 1405
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - System Transformation | 11.479 | 11.187 | 10.802 | 10.37 | 9.945 | 9.494 | 9.014 | 6.643 | 3.626 | 0.61 | -3.479 | Primary | 1406
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - System Transformation | 9.247 | 9.26 | 9.245 | 9.207 | 9.166 | 9.107 | 9.023 | 8.443 | 7.137 | 5.685 | 3.722 | Primary | 1407
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - System Transformation | 10.156 | 10.116 | 10.03 | 9.915 | 9.793 | 9.656 | 9.494 | 8.75 | 7.606 | 6.649 | 5.526 | Primary | 1408
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - System Transformation | 17.416 | 17.243 | 17.026 | 16.78 | 16.524 | 16.25 | 15.957 | 14.479 | 13.149 | 11.886 | 10.356 | Primary | 1409
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - System Transformation | 7.626 | 22.129 | 21.882 | 21.611 | 21.342 | 21.062 | 20.767 | 19.323 | 17.011 | 14.483 | 10.975 | Primary | 1410
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - System Transformation | 10.039 | 9.579 | 8.981 | 8.3 | 7.641 | 6.967 | 6.279 | 20.192 | 15.979 | 11.081 | 4.203 | Primary | 1411
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - System Transformation | 3.84 | 3.716 | 3.577 | 3.448 | 3.319 | 3.187 | 3.048 | 2.482 | 1.976 | 1.35 | 0.437 | Primary | 1412
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - System Transformation | 5.732 | 4.801 | 3.807 | 2.864 | 1.87 | 0.829 | -0.248 | -4.819 | -8.567 | -12.941 | -19.01 | Primary | 1413
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - System Transformation | 3.632 | 3.193 | 2.638 | 1.991 | 1.264 | 0.495 | -0.319 | -4.411 | -10.342 | -16.043 | -22.978 | Primary | 1414
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - System Transformation | 4.909 | 4.296 | 3.513 | 2.624 | 1.751 | 0.851 | -0.082 | 19.518 | 13.824 | 7.498 | -1.086 | Primary | 1415
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - System Transformation | 4.048 | 4.092 | 4.127 | 4.152 | 4.169 | 4.177 | 4.174 | 4.066 | 3.712 | 3.432 | 3.161 | Primary | 1416
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - System Transformation | 7.899 | 7.475 | 6.895 | 6.209 | 5.502 | 4.734 | 3.894 | 16.311 | 11.21 | 6.363 | 0.155 | Primary | 1417
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - System Transformation | 12.769 | 12.831 | 12.881 | 12.916 | 12.938 | 12.95 | 12.944 | 12.813 | 11.908 | 11.19 | 10.494 | Primary | 1418
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - System Transformation | 9.452 | 9.559 | 9.656 | 9.74 | 9.815 | 9.88 | 9.935 | 10.101 | 9.913 | 9.738 | 9.567 | Primary | 1419
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - System Transformation | 10.983 | 11.019 | 11.051 | 11.091 | 11.116 | 11.122 | 11.098 | 10.837 | 9.137 | 7.505 | 5.558 | Primary | 1420
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - System Transformation | 8.953 | 8.994 | 9.019 | 9.034 | 9.039 | 9.034 | 9.013 | 8.857 | 8.128 | 7.471 | 6.728 | Primary | 1421
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - System Transformation | 10.723 | 10.446 | 10.078 | 9.662 | 9.236 | 8.771 | 8.262 | 5.528 | 2.801 | 0.158 | -3.302 | Primary | 1422
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - System Transformation | 5.075 | 4.998 | 4.897 | 4.784 | 4.664 | 4.54 | 4.413 | 3.841 | 3.419 | 3.133 | 2.902 | Primary | 1423
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - System Transformation | 7.542 | 7.476 | 7.392 | 7.295 | 7.185 | 7.066 | 6.937 | 6.224 | 5.341 | 4.423 | 3.458 | Primary | 1424
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - System Transformation | 12.956 | 12.448 | 11.892 | 11.367 | 10.851 | 10.315 | 9.754 | 7.063 | 3.727 | 0.114 | -4.941 | Primary | 1425
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - System Transformation | 0.781 | 0.764 | 0.738 | 0.705 | 0.667 | 0.623 | 0.573 | 0.28 | -0.156 | -0.555 | -0.961 | Primary | 1426
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - System Transformation | 2.356 | 2.128 | 1.863 | 1.577 | 1.285 | 0.984 | 0.667 | -0.8 | -2.331 | -3.895 | -5.815 | Primary | 1427
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 9.553 | 9.392 | 9.152 | 8.854 | 8.515 | 8.146 | 7.74 | 5.578 | 3.508 | 1.134 | -2.075 | Primary | 1428
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - System Transformation | 8.297 | 8.112 | 7.926 | 7.779 | 7.629 | 7.464 | 7.275 | 6.347 | 4.432 | 2.546 | 0.121 | Primary | 1429
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - System Transformation | 5.105 | 4.78 | 4.396 | 3.983 | 3.575 | 3.148 | 2.691 | 0.441 | -2.642 | -5.928 | -10.16 | Primary | 1430
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - System Transformation | 4.179 | 4.197 | 4.209 | 4.215 | 4.216 | 4.211 | 4.2 | 4.08 | 3.79 | 3.543 | 3.259 | Primary | 1431
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - System Transformation | 21.856 | 21.666 | 21.445 | 21.228 | 21.027 | 20.819 | 20.598 | 19.537 | 17.862 | 15.85 | 12.945 | Primary | 1432
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - System Transformation | 7.364 | 7.382 | 7.389 | 7.397 | 7.404 | 7.399 | 7.373 | 7.174 | 6.08 | 4.99 | 3.627 | Primary | 1433
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - System Transformation | 12.888 | 12.514 | 12.128 | 11.794 | 11.46 | 11.114 | 10.754 | 9.064 | 6.951 | 4.572 | 1.191 | Primary | 1434
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - System Transformation | 8.38 | 8.323 | 8.211 | 8.061 | 7.907 | 7.733 | 7.531 | 6.457 | 4.306 | 2.299 | -0.261 | Primary | 1435
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - System Transformation | 2.009 | 1.23 | 0.321 | -0.587 | -1.437 | -2.317 | -3.245 | -7.596 | -12.501 | -18.187 | -26.426 | Primary | 1436
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - System Transformation | 0.948 | 0.792 | 0.612 | 0.411 | 0.198 | -0.03 | -0.28 | -1.053 | -1.823 | -2.53 | -3.3 | Primary | 1437
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - System Transformation | 2.758 | 2.605 | 2.419 | 2.202 | 1.961 | 1.693 | 1.392 | -0.374 | -3.014 | -5.333 | -7.741 | Primary | 1438
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - System Transformation | 12.911 | 12.824 | 12.677 | 12.487 | 12.289 | 12.081 | 11.858 | 11.901 | 10.61 | 9.261 | 7.441 | Primary | 1439
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - System Transformation | 14.438 | 14.242 | 14.959 | 14.621 | 14.292 | 13.951 | 13.59 | 11.853 | 9.507 | 6.791 | 2.833 | Primary | 1440
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - System Transformation | 22.1 | 22.066 | 21.961 | 21.776 | 21.532 | 21.203 | 20.776 | 17.788 | 12.993 | 9.629 | 6.379 | Primary | 1441
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - System Transformation | 9.711 | 9.405 | 9.027 | 8.602 | 8.162 | 7.703 | 7.219 | 11.791 | 8.599 | 5.156 | 0.724 | Primary | 1442
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - System Transformation | 1.82 | 1.511 | 1.16 | 0.774 | 0.384 | -0.024 | -0.458 | -2.371 | -4.22 | -6.341 | -9.238 | Primary | 1443
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - System Transformation | 7.912 | 7.572 | 7.078 | 6.5 | 5.969 | 5.423 | 4.851 | 2.106 | -1.539 | -6.463 | -14.092 | Primary | 1444
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - System Transformation | 5.204 | 2.885 | 2.858 | 2.809 | 2.743 | 2.661 | 2.557 | 1.971 | 0.829 | -0.247 | -1.577 | Primary | 1445
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - System Transformation | 7.372 | 6.908 | 6.322 | 5.68 | 5.053 | 4.405 | 3.725 | 0.549 | -2.956 | -6.843 | -12.359 | Primary | 1446
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - System Transformation | 3.285 | 2.996 | 17.317 | 16.89 | 16.456 | 15.997 | 15.509 | 13.029 | 9.531 | 5.867 | 0.888 | Primary | 1447
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - System Transformation | -0.501 | -0.662 | -0.864 | -1.093 | -1.316 | -1.544 | -1.783 | -2.924 | -4.638 | -6.436 | -8.783 | Primary | 1448
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - System Transformation | 2.528 | 2.528 | 2.516 | 2.492 | 2.466 | 2.431 | 2.384 | 2.096 | 1.414 | 0.787 | 0.055 | Primary | 1449
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - System Transformation | 10.289 | 10.012 | 9.625 | 9.176 | 8.722 | 8.254 | 7.771 | 5.532 | 2.992 | -0.174 | -4.811 | Primary | 1450
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - System Transformation | 8.188 | 7.858 | 7.423 | 6.934 | 6.459 | 5.957 | 5.415 | 2.743 | -0.334 | -3.906 | -9.014 | Primary | 1451
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - System Transformation | 11.155 | 11.015 | 10.821 | 10.594 | 10.354 | 10.096 | 9.816 | 8.357 | 6.792 | 5.229 | 3.308 | Primary | 1452
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - System Transformation | 3.514 | 2.554 | 2.537 | 2.481 | 2.413 | 2.312 | 2.173 | 1.162 | -0.891 | -2.857 | -5.351 | Primary | 1453
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - System Transformation | 14.831 | 14.726 | 14.597 | 14.44 | 14.263 | 14.06 | 13.825 | 12.374 | 10.017 | 8.008 | 5.944 | Primary | 1454
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - System Transformation | 4.425 | 4.335 | 4.221 | 4.094 | 3.966 | 3.833 | 3.695 | 3.031 | 2.162 | 1.157 | -0.205 | Primary | 1455
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - System Transformation | 2.028 | 1.953 | 1.853 | 1.74 | 1.632 | 1.519 | 1.399 | 0.832 | -0.025 | -1.001 | -2.381 | Primary | 1456
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - System Transformation | 14.858 | 14.49 | 14.024 | 13.498 | 12.986 | 12.439 | 11.847 | 8.768 | 4.834 | 0.8 | -4.496 | Primary | 1457
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - System Transformation | 2.656 | 2.481 | 4.22 | 3.898 | 3.547 | 3.17 | 2.756 | 0.663 | -2.776 | -6.365 | -11.207 | Primary | 1458
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - System Transformation | 14.768 | 14.707 | 14.611 | 14.494 | 14.392 | 14.279 | 14.149 | 13.393 | 12.007 | 10.227 | 7.62 | Primary | 1459
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - System Transformation | 4.397 | 4.288 | 4.154 | 4.003 | 3.842 | 3.676 | 3.502 | 2.67 | 1.602 | 0.489 | -0.915 | Primary | 1460
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - System Transformation | 4.518 | 4.014 | 3.37 | 2.653 | 1.926 | 1.169 | 0.367 | -3.407 | -7.626 | -11.866 | -17.246 | Primary | 1461
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - System Transformation | 11.491 | 11.141 | 10.698 | 10.212 | 9.722 | 9.22 | 8.692 | 6.269 | 3.62 | 0.61 | -3.501 | Primary | 1462
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - System Transformation | 12.055 | 10.43 | 10.327 | 10.155 | 9.932 | 9.63 | 9.239 | 6.732 | 3.56 | 1.231 | -1.124 | Primary | 1463
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - System Transformation | 0.747 | 0.339 | -0.042 | -0.328 | -0.62 | -0.92 | -1.229 | -2.562 | -3.604 | -4.645 | -5.954 | Primary | 1464
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - System Transformation | 7.175 | 6.478 | 5.651 | 4.754 | 3.839 | 2.896 | 1.92 | -2.655 | -6.171 | -10.957 | -17.818 | Primary | 1465
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - System Transformation | 9.114 | 9.079 | 9.036 | 8.987 | 8.933 | 8.874 | 8.81 | 8.435 | 7.982 | 7.515 | 7.033 | Primary | 1466
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - System Transformation | 1.656 | 1.442 | 1.148 | 0.776 | 0.34 | -0.183 | -0.799 | -4.874 | -9.555 | -12.498 | -15.061 | Primary | 1467
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - System Transformation | 10.257 | 9.828 | 9.379 | 8.976 | 8.589 | 8.183 | 7.749 | 5.553 | 2.369 | -1.343 | -6.663 | Primary | 1468
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - System Transformation | 8.648 | 8.255 | 7.732 | 7.131 | 6.556 | 5.949 | 5.299 | 1.978 | -1.7 | -5.711 | -11.271 | Primary | 1469
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - System Transformation | 1.284 | 1.171 | 1.027 | 0.853 | 0.657 | 0.432 | 0.176 | -1.395 | -3.136 | -4.421 | -5.62 | Primary | 1470
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - System Transformation | 7.093 | 6.728 | 6.254 | 5.719 | 5.199 | 4.663 | 4.103 | 1.472 | -2.199 | -6.408 | -12.296 | Primary | 1471
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - System Transformation | 0.86 | 0.797 | 0.688 | 0.553 | 0.427 | 0.282 | 0.107 | -0.758 | -2.542 | -4.42 | -6.871 | Primary | 1472
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - System Transformation | 1.496 | 1.494 | 1.492 | 1.489 | 1.486 | 1.483 | 1.479 | 1.458 | 1.429 | 1.4 | 1.371 | Primary | 1473
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 23.988 | 24.01 | 24.005 | 23.973 | 23.929 | 23.874 | 23.799 | 23.396 | 22.129 | 20.719 | 18.875 | Primary | 1474
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 33.829 | 33.781 | 33.707 | 33.62 | 33.528 | 33.43 | 33.317 | 32.833 | 32.068 | 31.285 | 30.262 | Primary | 1475
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 20.471 | 20.381 | 20.264 | 20.128 | 19.986 | 19.84 | 19.69 | 19.024 | 18.388 | 17.823 | 17.192 | Primary | 1476
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 14.567 | 14.331 | 14.046 | 13.741 | 13.431 | 13.098 | 12.738 | 10.809 | 8.71 | 6.511 | 3.608 | Primary | 1477
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - System Transformation | 13.459 | 13.163 | 12.781 | 13.331 | 12.811 | 12.274 | 11.725 | 9.138 | 6.917 | 4.136 | 0.424 | Primary | 1478
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - System Transformation | 10.323 | 9.254 | 8.861 | 8.404 | 7.965 | 7.511 | 7.029 | 4.955 | 2.522 | -0.387 | -4.617 | Primary | 1479
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - System Transformation | 1.368 | 15.098 | 14.768 | 14.395 | 13.99 | 13.547 | 13.06 | 10.389 | 7.062 | 4.281 | 1.212 | Primary | 1480
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - System Transformation | 10.355 | 9.604 | 8.962 | 8.566 | 8.196 | 7.813 | 7.411 | 5.493 | 2.921 | -0.259 | -4.94 | Primary | 1481
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - System Transformation | 15.31 | 15.25 | 15.182 | 15.107 | 15.033 | 14.953 | 14.867 | 14.371 | 13.454 | 12.406 | 11.118 | Primary | 1482
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - System Transformation | 3.499 | 2.445 | 1.135 | -0.311 | -1.738 | -3.211 | -4.74 | -10.87 | -17.072 | -23.915 | -33.175 | Primary | 1483
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - System Transformation | 5.905 | 5.23 | 4.489 | 3.791 | 3.087 | 2.365 | 1.626 | -1.672 | -4.188 | -7.81 | -13.239 | Primary | 1484
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - System Transformation | 4.293 | 4.29 | 4.24 | 4.157 | 4.106 | 4.037 | 3.941 | 3.189 | 1.365 | -1.299 | -5.538 | Primary | 1485
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 17.086 | 14.043 | 13.758 | 13.444 | 13.134 | 12.815 | 12.476 | 11.115 | 9.114 | 7.047 | 4.572 | Primary | 1486
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - System Transformation | 14.686 | 14.632 | 14.56 | 14.471 | 14.361 | 14.235 | 14.088 | 13.17 | 11.74 | 10.498 | 9.25 | Primary | 1487
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - System Transformation | 9.125 | 8.87 | 8.574 | 8.233 | 7.849 | 7.416 | 6.926 | 3.902 | -0.087 | -3.197 | -6.051 | Primary | 1488
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - System Transformation | 11.674 | 11.659 | 11.609 | 11.535 | 11.465 | 11.386 | 11.287 | 10.755 | 9.139 | 7.288 | 4.755 | Primary | 1489
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - System Transformation | 11.239 | 11.271 | 11.28 | 11.271 | 11.257 | 11.233 | 11.198 | 10.976 | 10.434 | 9.853 | 9.107 | Primary | 1490
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 3.644 | 3.409 | 3.145 | 2.844 | 2.505 | 2.121 | 1.687 | -1.04 | -4.586 | -7.362 | -9.867 | Primary | 1491
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - System Transformation | 14.658 | 14.564 | 14.444 | 14.306 | 14.179 | 14.038 | 13.876 | 12.866 | 11.261 | 9.429 | 6.985 | Primary | 1492
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - System Transformation | 10.588 | 10.318 | 9.947 | 9.523 | 9.13 | 8.723 | 8.287 | 6.271 | 3.68 | 0.496 | -4.187 | Primary | 1493
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - System Transformation | 9.428 | 9.323 | 9.158 | 8.956 | 8.78 | 8.585 | 8.359 | 7.063 | 4.8 | 2.046 | -1.922 | Primary | 1494
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - System Transformation | 6.984 | 6.632 | 6.159 | 5.611 | 5.077 | 4.511 | 3.901 | 0.8 | -2.756 | -6.516 | -11.671 | Primary | 1495
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - System Transformation | 4.269 | 3.774 | 3.173 | 2.524 | 1.867 | 1.163 | 0.406 | 13.859 | 9.951 | 6.055 | 1.21 | Primary | 1496
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - System Transformation | 10.933 | 10.9 | 10.835 | 10.744 | 10.614 | 10.443 | 10.227 | 8.84 | 7.365 | 6.591 | 6.114 | Primary | 1497
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - System Transformation | 15.333 | 15.055 | 14.675 | 14.236 | 13.839 | 13.433 | 13.008 | 11.021 | 8.761 | 5.649 | 0.804 | Primary | 1498
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - System Transformation | 8.744 | 8.277 | 7.67 | 6.968 | 6.254 | 5.478 | 4.63 | 0.026 | -5.228 | -9.948 | -15.75 | Primary | 1499
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - System Transformation | 3.243 | 3.118 | 2.963 | 3.292 | 3.122 | 2.946 | 2.762 | 1.866 | 0.785 | -0.312 | -1.709 | Primary | 1500
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - System Transformation | 6.995 | 6.731 | 6.374 | 5.969 | 5.559 | 5.133 | 4.689 | 9.59 | 6.271 | 2.509 | -2.795 | Primary | 1501
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - System Transformation | 4.102 | 3.931 | 3.704 | 3.452 | 3.201 | 2.945 | 2.68 | 1.448 | 0.287 | -1.334 | -3.836 | Primary | 1502
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 12.232 | 12.186 | 12.122 | 12.043 | 11.959 | 11.864 | 11.755 | 11.141 | 10.045 | 8.869 | 7.442 | Primary | 1503
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 25.296 | 25.255 | 25.201 | 25.135 | 25.069 | 24.998 | 24.917 | 24.482 | 23.458 | 22.388 | 21.065 | Primary | 1504
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - System Transformation | 14.534 | 14.385 | 14.192 | 13.958 | 13.67 | 13.363 | 13.039 | 11.466 | 10.261 | 9.053 | 7.659 | Primary | 1505
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - System Transformation | 12.633 | 12.668 | 12.688 | 12.691 | 12.688 | 12.676 | 12.65 | 12.474 | 11.516 | 10.622 | 9.578 | Primary | 1506
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - System Transformation | 19.931 | 19.865 | 19.785 | 19.691 | 19.595 | 19.492 | 19.376 | 18.959 | 18.208 | 17.426 | 16.524 | Primary | 1507
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - System Transformation | 6.806 | 6.531 | 6.146 | 5.689 | 5.201 | 4.695 | 4.168 | 1.977 | 0.228 | -2.251 | -5.933 | Primary | 1508
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 20.989 | 20.959 | 20.881 | 20.767 | 20.659 | 20.532 | 20.376 | 19.466 | 17.426 | 15.24 | 12.325 | Primary | 1509
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - System Transformation | 13.946 | 13.873 | 13.779 | 13.679 | 13.608 | 13.53 | 13.435 | 12.874 | 11.271 | 9.231 | 6.256 | Primary | 1510
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - System Transformation | 4.226 | 4.129 | 4.003 | 3.862 | 3.731 | 3.594 | 3.449 | 2.731 | 1.906 | 0.937 | -0.493 | Primary | 1511
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - System Transformation | 0.913 | 0.849 | 0.775 | 0.693 | 0.605 | 0.507 | 0.401 | -0.23 | -0.95 | -1.595 | -2.219 | Primary | 1512
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - System Transformation | 16.15 | 16.048 | 15.911 | 15.743 | 15.565 | 15.366 | 15.134 | 13.852 | 11.595 | 9.399 | 6.812 | Primary | 1513
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 22.118 | 21.909 | 21.626 | 21.298 | 20.973 | 20.635 | 20.281 | 18.602 | 16.495 | 14.22 | 11.058 | Primary | 1514
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 26.301 | 26.204 | 26.073 | 25.922 | 25.78 | 25.634 | 25.48 | 24.737 | 23.641 | 22.305 | 20.341 | Primary | 1515
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - System Transformation | 2.328 | 2.165 | 1.973 | 1.764 | 1.542 | 1.312 | 1.075 | -0.078 | -1.448 | -2.907 | -4.777 | Primary | 1516
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - System Transformation | 2.195 | 1.986 | 1.737 | 1.456 | 1.181 | 0.878 | 0.531 | -1.512 | -5.084 | -8.883 | -13.746 | Primary | 1517
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - System Transformation | 14.29 | 14.224 | 14.128 | 14.007 | 13.868 | 13.699 | 13.498 | 12.403 | 11.166 | 10.144 | 9.037 | Primary | 1518
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - System Transformation | 4.57 | 4.479 | 4.362 | 4.233 | 4.108 | 3.98 | 3.846 | 3.202 | 2.285 | 1.199 | -0.389 | Primary | 1519
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - System Transformation | 14.451 | 14.41 | 14.365 | 14.326 | 14.282 | 14.225 | 14.15 | 13.721 | 12.843 | 11.949 | 10.766 | Primary | 1520
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - System Transformation | 9.049 | 9.139 | 9.212 | 9.267 | 9.312 | 9.341 | 9.354 | 10.236 | 9.661 | 9.114 | 8.464 | Primary | 1521
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - System Transformation | 1.126 | 0.788 | 0.352 | -0.145 | -0.656 | -1.188 | -1.745 | -4.439 | -6.805 | -9.158 | -12.149 | Primary | 1522
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 16.799 | 16.759 | 16.702 | 16.632 | 16.562 | 16.484 | 16.394 | 15.89 | 14.986 | 13.973 | 12.647 | Primary | 1523
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 16.729 | 16.681 | 16.613 | 16.53 | 16.44 | 16.336 | 16.214 | 15.446 | 14.433 | 13.474 | 12.323 | Primary | 1524
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - System Transformation | 4.328 | 3.909 | 3.381 | 2.79 | 2.2 | 1.584 | 0.933 | 12.593 | 9.074 | 5.428 | 0.636 | Primary | 1525
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - System Transformation | 14.287 | 14.174 | 14.035 | 13.878 | 13.732 | 13.575 | 13.4 | 12.491 | 10.823 | 8.995 | 6.653 | Primary | 1526
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - System Transformation | 7.703 | 7.094 | 6.424 | 5.786 | 5.135 | 4.462 | 3.765 | 17.551 | 13.835 | 9.8 | 4.165 | Primary | 1527
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - System Transformation | 4.816 | 4.717 | 4.595 | 4.466 | 4.317 | 4.138 | 3.922 | 2.663 | 0.16 | -2.454 | -5.862 | Primary | 1528
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - System Transformation | 10.287 | 9.979 | 9.552 | 9.055 | 8.587 | 8.105 | 7.603 | 5.158 | 1.469 | -3.081 | -9.785 | Primary | 1529
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - System Transformation | 0.092 | -0.008 | -0.125 | -0.259 | -0.397 | -0.547 | -0.714 | -1.61 | -2.939 | -4.393 | -6.211 | Primary | 1530
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - System Transformation | 13.236 | 12.938 | 12.553 | 12.13 | 11.708 | 11.267 | 10.803 | 8.564 | 5.94 | 3.065 | -0.994 | Primary | 1531
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - System Transformation | 17.469 | 17.458 | 17.438 | 17.406 | 17.366 | 17.32 | 17.26 | 16.914 | 15.994 | 15.149 | 14.168 | Primary | 1532
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - System Transformation | 12.548 | 12.364 | 12.15 | 11.916 | 11.679 | 11.43 | 11.164 | 9.745 | 8.047 | 5.588 | 2.003 | Primary | 1533
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - System Transformation | 6.874 | 6.743 | 6.578 | 6.382 | 6.174 | 5.948 | 5.706 | 4.32 | 2.226 | -0.163 | -3.374 | Primary | 1534
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - System Transformation | 9.313 | 9.17 | 8.976 | 8.737 | 8.492 | 8.209 | 7.881 | 5.719 | 2.392 | -0.963 | -5.287 | Primary | 1535
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - System Transformation | 15.237 | 15.186 | 15.131 | 15.071 | 15.006 | 14.937 | 14.864 | 15.438 | 14.91 | 14.364 | 13.817 | Primary | 1536
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - System Transformation | 16.346 | 16.244 | 16.096 | 15.918 | 15.728 | 15.527 | 15.311 | 14.263 | 12.724 | 11.222 | 9.28 | Primary | 1537
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - System Transformation | 12.777 | 12.615 | 12.406 | 12.168 | 11.931 | 11.685 | 11.425 | 10.404 | 8.782 | 7.075 | 4.9 | Primary | 1538
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - System Transformation | 10.259 | 9.759 | 9.281 | 8.913 | 8.566 | 8.208 | 7.829 | 6.08 | 3.888 | 1.146 | -2.867 | Primary | 1539
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - System Transformation | 9.345 | 8.844 | 8.259 | 7.673 | 7.109 | 6.525 | 5.91 | 3.088 | -0.104 | -3.681 | -8.81 | Primary | 1540
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - System Transformation | 2.165 | 2.197 | 2.221 | 2.238 | 2.249 | 2.253 | 2.25 | 2.173 | 1.949 | 1.772 | 1.595 | Primary | 1541
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - System Transformation | 9.526 | 8.803 | 8.105 | 7.552 | 7.016 | 6.464 | 5.892 | 20.213 | 16.62 | 12.349 | 6.142 | Primary | 1542
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - System Transformation | 4.448 | 4.24 | 3.969 | 3.639 | 3.298 | 2.908 | 2.451 | -0.246 | -4.841 | -9.192 | -14.427 | Primary | 1543
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - System Transformation | 3.246 | 2.839 | 2.33 | 1.762 | 1.202 | 0.631 | 0.039 | -2.634 | -5.931 | -9.588 | -14.501 | Primary | 1544
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - System Transformation | 23.066 | 23.034 | 22.955 | 22.842 | 22.747 | 22.639 | 22.501 | 21.755 | 19.529 | 17.044 | 13.673 | Primary | 1545
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - System Transformation | 6.194 | 5.966 | 5.694 | 5.389 | 5.07 | 4.73 | 4.362 | 2.399 | -0.011 | -2.542 | -5.534 | Primary | 1546
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - System Transformation | 6.746 | 6.736 | 6.722 | 6.705 | 6.69 | 6.673 | 6.655 | 6.564 | 6.432 | 6.298 | 6.112 | Primary | 1547
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - System Transformation | 11.489 | 10.901 | 10.116 | 9.223 | 8.362 | 7.473 | 6.539 | 2.362 | -2.005 | -7.468 | -15.472 | Primary | 1548
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - System Transformation | 21.13 | 21.143 | 21.122 | 21.056 | 20.941 | 20.768 | 20.533 | 18.818 | 16.918 | 15.97 | 15.451 | Primary | 1549
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - System Transformation | 11.136 | 10.893 | 10.577 | 10.228 | 9.901 | 9.558 | 9.19 | 7.372 | 4.913 | 2.079 | -1.959 | Primary | 1550
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - System Transformation | 12.576 | 12.42 | 12.203 | 11.913 | 11.542 | 11.084 | 10.534 | 7.06 | 2.752 | -0.413 | -3.546 | Primary | 1551
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - System Transformation | 0.091 | -0.028 | -0.179 | -0.354 | -0.538 | -0.738 | -0.958 | -2.167 | -3.898 | -5.411 | -7.113 | Primary | 1552
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - System Transformation | 6.82 | 1.018 | 0.72 | 0.381 | 0.017 | -0.362 | -0.754 | 6.036 | 4.279 | 2.221 | -0.539 | Primary | 1553
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - System Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 1554
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - System Transformation | 3.515 | 3.222 | 2.857 | 2.453 | 2.047 | 1.626 | 1.182 | -0.975 | -3.518 | -6.359 | -10.1 | Primary | 1555
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - System Transformation | 12.321 | 12.112 | 11.843 | 11.525 | 11.156 | 10.705 | 10.162 | 6.53 | 2.095 | -0.957 | -3.911 | Primary | 1556
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - System Transformation | 5.4 | 5.15 | 4.837 | 4.51 | 4.179 | 3.822 | 3.431 | 1.674 | -0.11 | -2.158 | -5 | Primary | 1557
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - System Transformation | 0.951 | 0.724 | 0.491 | 0.3 | 0.106 | -0.094 | -0.302 | -1.228 | -2.077 | -3.226 | -4.947 | Primary | 1558
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - System Transformation | 12.611 | 12.457 | 12.24 | 11.989 | 11.766 | 11.531 | 11.274 | 9.971 | 8.159 | 5.995 | 2.819 | Primary | 1559
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - System Transformation | 7.101 | 7.119 | 7.13 | 7.141 | 7.142 | 7.132 | 7.098 | 6.9 | 5.572 | 4.425 | 3.198 | Primary | 1560
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - System Transformation | 13.43 | 13.373 | 13.284 | 13.171 | 13.069 | 12.955 | 12.821 | 12.015 | 10.551 | 8.634 | 5.838 | Primary | 1561
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - System Transformation | 6.798 | 6.353 | 5.805 | 5.195 | 4.574 | 3.93 | 3.254 | -0.054 | -3.781 | -7.369 | -11.719 | Primary | 1562
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - System Transformation | 9.671 | 9.62 | 9.508 | 9.341 | 9.145 | 8.885 | 8.55 | 6.252 | 3.412 | 1.238 | -1.144 | Primary | 1563
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - System Transformation | 14.714 | 14.738 | 14.757 | 14.772 | 14.784 | 14.793 | 14.798 | 14.793 | 14.599 | 14.419 | 14.224 | Primary | 1564
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - System Transformation | 5.541 | 5.519 | 5.489 | 5.455 | 5.42 | 5.382 | 5.34 | 5.13 | 4.931 | 4.7 | 4.359 | Primary | 1565
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - System Transformation | 13.956 | 13.977 | 13.982 | 13.971 | 13.953 | 13.927 | 13.887 | 13.668 | 12.617 | 11.66 | 10.591 | Primary | 1566
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - System Transformation | 3.944 | 3.66 | 3.271 | 2.818 | 2.393 | 1.952 | 1.487 | -0.662 | -2.905 | -5.79 | -10.094 | Primary | 1567
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - System Transformation | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary | 1568
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - System Transformation | 8.603 | 7.497 | 6.895 | 6.224 | 5.579 | 4.916 | 4.229 | 1.07 | -2.837 | -7.563 | -14.329 | Primary | 1569
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - System Transformation | 8.603 | 8.047 | 7.369 | 6.668 | 23.096 | 22.407 | 21.684 | 18.328 | 14.93 | 10.664 | 4.23 | Primary | 1570
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - System Transformation | 3.172 | 3.23 | 3.266 | 3.276 | 3.263 | 3.236 | 3.189 | 2.816 | 1.271 | -0.326 | -2.35 | Primary | 1571
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - System Transformation | 1.767 | 1.425 | 0.981 | 0.461 | -0.112 | -0.703 | -1.305 | -4.08 | -7.8 | -11.854 | -17.229 | Primary | 1572
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - System Transformation | 14.335 | 14.14 | 13.891 | 13.621 | 13.353 | 13.075 | 12.784 | 11.393 | 9.263 | 6.851 | 3.437 | Primary | 1573
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - System Transformation | 5.557 | 5.113 | 4.503 | 3.793 | 3.083 | 2.34 | 1.547 | -2.328 | -6.35 | -11.039 | -17.617 | Primary | 1574
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - System Transformation | 4.78 | 3.763 | 3.431 | 3.101 | 2.773 | 2.414 | 2.022 | -0.039 | -2.612 | -5.555 | -9.735 | Primary | 1575
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - System Transformation | 14.881 | 14.679 | 14.421 | 14.144 | 13.89 | 13.628 | 13.349 | 12.168 | 10.782 | 9.026 | 6.37 | Primary | 1576
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - System Transformation | 3.451 | 3.154 | 2.756 | 2.308 | 1.876 | 1.418 | 0.923 | 13.156 | 10.181 | 6.97 | 2.451 | Primary | 1577
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - System Transformation | 6.642 | 6.38 | 6.066 | 5.703 | 5.319 | 4.9 | 4.438 | 1.844 | -1.472 | -5.071 | -9.567 | Primary | 1578
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - System Transformation | 8.154 | 7.751 | 7.237 | 6.654 | 6.057 | 5.436 | 4.785 | 1.682 | -0.803 | -4.188 | -9.2 | Primary | 1579
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - System Transformation | 5.82 | 5.492 | 5.061 | 4.565 | 4.011 | 3.441 | 2.862 | 0.198 | -1.857 | -4.272 | -7.504 | Primary | 1580
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - System Transformation | 0.871 | 0.015 | -0.856 | -1.603 | -2.346 | -3.115 | -3.91 | -7.648 | -12.477 | -17.939 | -25.673 | Primary | 1581
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - System Transformation | 9.575 | 9.055 | 8.477 | 7.936 | 7.44 | 6.93 | 6.395 | 3.905 | 1.054 | -2.659 | -8.299 | Primary | 1582
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - System Transformation | 10.531 | 10.025 | 9.459 | 8.919 | 8.371 | 7.784 | 7.15 | 3.878 | 0.309 | -3.2 | -7.873 | Primary | 1583
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - System Transformation | 12.312 | 12.304 | 12.261 | 12.182 | 12.084 | 11.95 | 11.772 | 10.467 | 8.173 | 6.435 | 4.665 | Primary | 1584
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - System Transformation | 8.554 | 8.424 | 8.252 | 8.059 | 7.869 | 7.67 | 7.455 | 6.387 | 4.724 | 3.008 | 0.681 | Primary | 1585
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - System Transformation | 2.857 | 2.81 | 2.723 | 2.602 | 2.464 | 2.296 | 2.094 | 0.769 | -0.826 | -2.323 | -4.17 | Primary | 1586
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - System Transformation | 12.779 | 12.553 | 12.252 | 11.913 | 11.6 | 11.276 | 10.935 | 9.333 | 7.213 | 4.733 | 1.133 | Primary | 1587
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - System Transformation | 18.255 | 18.155 | 18.005 | 17.82 | 17.635 | 17.442 | 17.24 | 16.28 | 15.111 | 13.83 | 11.989 | Primary | 1588
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - System Transformation | 15.389 | 15.317 | 15.216 | 15.089 | 14.938 | 14.776 | 14.606 | 13.664 | 12.493 | 10.564 | 7.705 | Primary | 1589
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - System Transformation | 2.652 | 2.353 | 1.961 | 1.459 | 0.856 | 0.129 | -0.738 | -5.112 | -9.77 | -13.429 | -17.225 | Primary | 1590
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - System Transformation | 9.742 | 9.77 | 9.778 | 9.762 | 9.735 | 9.689 | 9.617 | 9.136 | 7.698 | 6.382 | 4.882 | Primary | 1591
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - System Transformation | 6.06 | 5.899 | 5.697 | 5.465 | 5.24 | 4.987 | 4.697 | 3.16 | 1.033 | -1.075 | -3.661 | Primary | 1592
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - System Transformation | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary | 1593
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - System Transformation | 6.66 | 6.119 | 5.521 | 4.934 | 4.344 | 3.721 | 3.052 | -0.084 | -3.013 | -6.405 | -11.235 | Primary | 1594
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - System Transformation | 14.27 | 13.972 | 13.596 | 13.166 | 12.779 | 12.38 | 11.958 | 9.881 | 7.599 | 4.553 | -0.181 | Primary | 1595
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - System Transformation | 3.067 | 2.891 | 2.679 | 2.446 | 2.223 | 1.993 | 1.752 | 0.648 | -0.753 | -2.253 | -4.237 | Primary | 1596
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - System Transformation | 8.714 | 8.42 | 8.047 | 7.578 | 7.026 | 6.359 | 5.56 | 0.167 | -6.731 | -11.853 | -16.857 | Primary | 1597
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - System Transformation | 12.943 | 12.433 | 11.911 | 11.45 | 11.009 | 10.553 | 10.071 | 7.807 | 5.004 | 1.978 | -2.226 | Primary | 1598
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - System Transformation | 4.956 | 4.855 | 4.73 | 4.593 | 4.462 | 4.327 | 4.188 | 3.527 | 2.662 | 1.67 | 0.286 | Primary | 1599
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - System Transformation | 5.904 | 5.406 | 4.791 | 4.11 | 3.458 | 2.787 | 2.081 | -1.13 | -5.534 | -10.435 | -17.077 | Primary | 1600
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - System Transformation | 9.853 | 9.526 | 9.084 | 8.582 | 8.117 | 7.636 | 7.132 | 4.869 | 1.777 | -1.878 | -7.192 | Primary | 1601
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - System Transformation | 15.475 | 15.158 | 14.809 | 14.479 | 14.153 | 13.821 | 13.482 | 11.978 | 10.226 | 8.081 | 4.953 | Primary | 1602
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - System Transformation | 5.986 | 5.774 | 5.463 | 5.089 | 4.735 | 4.358 | 3.945 | 1.993 | -0.683 | -3.763 | -8.119 | Primary | 1603
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - System Transformation | 12.778 | 12.298 | 11.721 | 11.078 | 10.368 | 9.618 | 8.827 | 5.037 | 0.71 | -3.431 | -8.354 | Primary | 1604
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - System Transformation | 12.72 | 12.655 | 12.569 | 12.464 | 12.361 | 12.248 | 12.12 | 11.514 | 10.44 | 9.126 | 7.364 | Primary | 1605
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - System Transformation | 9.239 | 8.901 | 8.475 | 8.006 | 7.52 | 7.003 | 6.446 | 3.775 | 1.261 | -1.424 | -4.996 | Primary | 1606
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - System Transformation | 11.317 | 11.319 | 11.284 | 11.21 | 11.115 | 10.986 | 10.817 | 9.667 | 7.939 | 6.618 | 5.239 | Primary | 1607
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - System Transformation | 5.505 | 5.448 | 5.331 | 5.157 | 4.954 | 4.705 | 4.397 | 2.465 | -0.098 | -2.545 | -5.571 | Primary | 1608
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - System Transformation | 28.522 | 28.431 | 28.306 | 28.152 | 27.979 | 27.782 | 27.558 | 26.238 | 24.642 | 23.362 | 22.094 | Primary | 1609
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - System Transformation | 3.003 | 2.718 | 2.4 | 2.057 | 1.722 | 1.368 | 0.991 | -1.173 | -4.653 | -8.579 | -13.607 | Primary | 1610
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - System Transformation | 1.859 | 1.802 | 1.729 | 1.646 | 1.558 | 1.466 | 1.369 | 0.898 | 0.402 | -0.075 | -0.583 | Primary | 1611
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - System Transformation | 11.531 | 11.212 | 10.836 | 10.435 | 10.029 | 9.607 | 9.157 | 6.998 | 4.236 | 1.154 | -2.945 | Primary | 1612
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - System Transformation | 9.854 | 9.846 | 9.812 | 9.759 | 9.708 | 9.643 | 9.555 | 9.01 | 7.768 | 6.532 | 4.933 | Primary | 1613
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - System Transformation | 10.655 | 10.582 | 10.46 | 10.297 | 10.136 | 9.959 | 9.759 | 8.58 | 5.464 | 1.657 | -3.817 | Primary | 1614
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - System Transformation | 1.764 | 1.683 | 1.581 | 1.459 | 1.328 | 1.18 | 1.01 | 0.129 | -1.142 | -2.305 | -3.591 | Primary | 1615
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - System Transformation | 11.826 | 11.819 | 11.77 | 11.668 | 11.509 | 11.282 | 10.979 | 8.637 | 5.181 | 3.074 | 1.41 | Primary | 1616
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - System Transformation | 15.621 | 15.558 | 15.485 | 15.416 | 15.344 | 15.259 | 15.159 | 14.579 | 13.573 | 12.642 | 11.498 | Primary | 1617
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - System Transformation | 7.632 | 6.406 | 5.79 | 5.102 | 4.419 | 3.71 | 2.965 | -0.405 | -4.877 | -9.665 | -15.969 | Primary | 1618
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - System Transformation | 11.896 | 11.771 | 11.592 | 11.384 | 11.182 | 10.97 | 10.747 | 9.672 | 8.254 | 6.517 | 3.964 | Primary | 1619
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - System Transformation | 15.828 | 15.841 | 15.774 | 15.619 | 15.373 | 15.017 | 14.546 | 10.851 | 6.343 | 3.921 | 2.336 | Primary | 1620
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - System Transformation | 8.616 | 8.238 | 7.735 | 7.169 | 6.653 | 6.112 | 5.531 | 2.581 | -1.07 | -5.508 | -12.106 | Primary | 1621
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - System Transformation | 4.223 | 4.158 | 4.073 | 3.978 | 3.885 | 3.787 | 3.684 | 3.175 | 2.577 | 1.922 | 1.048 | Primary | 1622
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - System Transformation | 8.67 | 8.262 | 7.81 | 7.38 | 6.995 | 6.592 | 6.16 | 4.139 | 1.546 | -1.624 | -6.251 | Primary | 1623
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 14.301 | 14.108 | 13.857 | 13.555 | 13.226 | 12.867 | 12.47 | 10.321 | 7.184 | 3.706 | -0.613 | Primary | 1624
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 13.282 | 13.105 | 12.874 | 12.593 | 12.297 | 11.972 | 11.601 | 9.473 | 5.294 | 1.012 | -4.096 | Primary | 1625
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - System Transformation | 12.248 | 12.247 | 12.223 | 12.181 | 12.128 | 12.059 | 11.966 | 11.37 | 9.971 | 8.758 | 7.414 | Primary | 1626
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - System Transformation | 8.061 | 8.078 | 8.07 | 8.042 | 8.026 | 8.002 | 7.964 | 7.688 | 6.782 | 5.569 | 3.764 | Primary | 1627
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - System Transformation | 17.496 | 17.388 | 17.234 | 17.054 | 16.87 | 16.677 | 16.474 | 15.504 | 14.594 | 13.437 | 11.752 | Primary | 1628
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - System Transformation | 4.814 | 4.738 | 4.645 | 4.533 | 4.405 | 4.257 | 4.09 | 3.012 | 1.499 | 0.103 | -1.274 | Primary | 1629
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - System Transformation | 2.058 | 1.564 | 1.03 | 0.536 | 0.078 | -0.395 | -0.891 | -3.246 | -6.116 | -9.679 | -14.948 | Primary | 1630
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - System Transformation | 11.372 | 10.97 | 10.521 | 10.087 | 9.655 | 9.209 | 8.75 | 6.602 | 4.056 | 0.873 | -3.768 | Primary | 1631
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - System Transformation | 9.912 | 9.428 | 8.859 | 8.28 | 7.716 | 7.113 | 6.461 | 3.018 | -0.69 | -4.766 | -10.414 | Primary | 1632
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 12.957 | 12.962 | 12.938 | 12.884 | 12.804 | 12.693 | 12.546 | 11.473 | 9.863 | 8.75 | 7.742 | Primary | 1633
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - System Transformation | 16.002 | 15.796 | 15.517 | 15.2 | 14.911 | 14.614 | 14.303 | 12.844 | 11.28 | 9.326 | 6.366 | Primary | 1634
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - System Transformation | 12.796 | 12.666 | 12.472 | 12.233 | 11.994 | 11.742 | 11.467 | 10.141 | 7.778 | 5.458 | 2.413 | Primary | 1635
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - System Transformation | 9.32 | 9.07 | 8.731 | 8.342 | 7.963 | 7.553 | 7.1 | 4.71 | 1.754 | -1.179 | -5.068 | Primary | 1636
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - System Transformation | 11.491 | 9.776 | 9.571 | 9.322 | 9.088 | 8.844 | 8.584 | 7.439 | 5.823 | 3.762 | 0.656 | Primary | 1637
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - System Transformation | 4.095 | 3.968 | 3.814 | 3.65 | 3.482 | 3.307 | 3.124 | 2.271 | 1.256 | 0.253 | -1.031 | Primary | 1638
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - System Transformation | 13.885 | 13.468 | 12.934 | 12.349 | 11.771 | 11.174 | 10.548 | 7.616 | 4.564 | 1.148 | -3.802 | Primary | 1639
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - System Transformation | 2.064 | 1.693 | 1.18 | 0.589 | 0.002 | -0.608 | -1.25 | -4.258 | -8.485 | -13.317 | -20.185 | Primary | 1640
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - System Transformation | 14.546 | 14.28 | 13.941 | 13.577 | 13.216 | 12.839 | 12.442 | 10.552 | 8.595 | 6.318 | 3.004 | Primary | 1641
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - System Transformation | 7.541 | 7.125 | 6.607 | 6.054 | 5.52 | 4.969 | 4.385 | 1.653 | -1.798 | -5.891 | -11.794 | Primary | 1642
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - System Transformation | 18.511 | 18.526 | 18.486 | 18.398 | 18.307 | 18.19 | 18.035 | 17 | 14.092 | 11.098 | 7.137 | Primary | 1643
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - System Transformation | 12.486 | 12.344 | 12.165 | 11.967 | 11.748 | 11.515 | 11.264 | 10.046 | 8.673 | 7.271 | 5.507 | Primary | 1644
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - System Transformation | 3.206 | 2.841 | 2.377 | 1.854 | 1.345 | 0.81 | 0.235 | -2.677 | -6.427 | -10.253 | -15.188 | Primary | 1645
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - System Transformation | 3.168 | 2.184 | 1.008 | -0.298 | -1.77 | -3.3 | -4.863 | -12.279 | -19.142 | -26.464 | -35.758 | Primary | 1646
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - System Transformation | 3.765 | 3.286 | 2.738 | 2.193 | 1.647 | 1.074 | 0.474 | 14.857 | 11.309 | 7.183 | 1.297 | Primary | 1647
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - System Transformation | 12.421 | 11.955 | 11.389 | 10.773 | 10.174 | 9.562 | 8.932 | 6.013 | 3.334 | -0.264 | -5.62 | Primary | 1648
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - System Transformation | 21.698 | 18.719 | 18.792 | 18.851 | 18.899 | 18.941 | 18.968 | 19.035 | 18.779 | 18.561 | 18.349 | Primary | 1649
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - System Transformation | 3.381 | 3.079 | 2.696 | 2.238 | 1.692 | 1.051 | 0.302 | -3.756 | -8.362 | -12.044 | -15.714 | Primary | 1650
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - System Transformation | 12.554 | 12.449 | 12.304 | 12.145 | 12.018 | 11.881 | 11.723 | 10.806 | 8.97 | 6.384 | 2.383 | Primary | 1651
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - System Transformation | 13.996 | 14.045 | 14.08 | 14.106 | 14.129 | 14.145 | 14.151 | 14.112 | 13.823 | 13.437 | 12.88 | Primary | 1652
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - System Transformation | 14.957 | 14.982 | 14.991 | 14.985 | 14.979 | 14.966 | 14.94 | 14.774 | 14.047 | 13.322 | 12.414 | Primary | 1653
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - System Transformation | 9.564 | 9.046 | 8.376 | 7.62 | 6.872 | 6.102 | 5.302 | 1.6 | -1.786 | -6.037 | -12.235 | Primary | 1654
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - System Transformation | 15.727 | 15.623 | 15.496 | 15.354 | 15.23 | 15.095 | 14.942 | 14.033 | 12.15 | 10.028 | 7.22 | Primary | 1655
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - System Transformation | 5.433 | 5.359 | 5.244 | 5.1 | 4.965 | 4.816 | 4.641 | 3.649 | 1.273 | -1.515 | -5.387 | Primary | 1656
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - System Transformation | 13.954 | 13.776 | 13.536 | 13.261 | 12.984 | 12.691 | 12.377 | 10.853 | 8.965 | 7.001 | 4.395 | Primary | 1657
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - System Transformation | 18.266 | 14.797 | 14.725 | 14.646 | 14.56 | 14.466 | 14.364 | 13.989 | 13.734 | 13.513 | 13.253 | Primary | 1658
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - System Transformation | 11.532 | 11.317 | 11.054 | 10.774 | 10.493 | 10.2 | 9.888 | 8.349 | 6.758 | 4.915 | 2.349 | Primary | 1659
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - System Transformation | 2.5 | 2.318 | 2.08 | 1.805 | 1.517 | 1.199 | 0.848 | -1.137 | -3.219 | -5.117 | -7.442 | Primary | 1660
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - System Transformation | 10.858 | 10.542 | 10.152 | 9.744 | 9.325 | 8.894 | 8.445 | 6.407 | 4.785 | 2.37 | -1.409 | Primary | 1661
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - System Transformation | 9.969 | 9.665 | 9.26 | 8.805 | 8.379 | 7.933 | 7.456 | 6.315 | 3.915 | 1.092 | -3.03 | Primary | 1662
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - System Transformation | 5.597 | 5.316 | 4.962 | 4.529 | 4.042 | 3.48 | 2.833 | -0.735 | -5.58 | -9.932 | -14.832 | Primary | 1663
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - System Transformation | 16.327 | 16.163 | 15.959 | 15.731 | 15.505 | 15.27 | 15.024 | 13.787 | 12.191 | 10.539 | 8.407 | Primary | 1664
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - System Transformation | 8.75 | 6.962 | 6.572 | 6.108 | 5.605 | 5.036 | 4.396 | 7.659 | 2.931 | -2.152 | -8.761 | Primary | 1665
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - System Transformation | 3.769 | 3.612 | 3.419 | 3.205 | 2.993 | 2.775 | 2.548 | 1.488 | 0.342 | -0.836 | -2.362 | Primary | 1666
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - System Transformation | 14.328 | 14.037 | 13.643 | 13.194 | 12.762 | 12.315 | 11.846 | 9.724 | 7.554 | 5.205 | 1.925 | Primary | 1667
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - System Transformation | -0.383 | -0.636 | -0.948 | -0.294 | -0.644 | -1.014 | -1.41 | -3.232 | -5.645 | -7.953 | -10.811 | Primary | 1668
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - System Transformation | 9.126 | 8.79 | 8.356 | 7.867 | 7.37 | 6.853 | 6.304 | 3.649 | 0.053 | -3.815 | -8.909 | Primary | 1669
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - System Transformation | 7.646 | 7.339 | 6.923 | 6.449 | 6.001 | 5.529 | 5.018 | 2.5 | -0.838 | -4.365 | -9.244 | Primary | 1670
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - System Transformation | 4.889 | 4.399 | 3.784 | 3.096 | 2.422 | 1.72 | 0.968 | -2.554 | -7.684 | -13.019 | -19.921 | Primary | 1671
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - System Transformation | 16.009 | 15.704 | 15.301 | 14.84 | 14.375 | 13.883 | 13.351 | 10.85 | 8.185 | 5.459 | 1.819 | Primary | 1672
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - System Transformation | 7.81 | 7.835 | 7.825 | 7.782 | 7.732 | 7.66 | 7.556 | 6.867 | 5.275 | 3.765 | 1.944 | Primary | 1673
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - System Transformation | 13.753 | 14.441 | 14.066 | 5.667 | 4.883 | 4.072 | 3.238 | 0.398 | -2.547 | -5.834 | -10.31 | Primary | 1674
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - System Transformation | 10.86 | 10.442 | 9.906 | 9.289 | 8.628 | 7.939 | 7.223 | 3.74 | 0.446 | -3.373 | -8.564 | Primary | 1675
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - System Transformation | 6.551 | 6.545 | 6.494 | 6.407 | 6.332 | 6.237 | 6.106 | 5.49 | 3.965 | 2.424 | 0.43 | Primary | 1676
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - System Transformation | 11.659 | 11.299 | 10.831 | 10.302 | 9.767 | 9.217 | 8.644 | 5.977 | 3.435 | 0.139 | -4.768 | Primary | 1677
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - System Transformation | 4.958 | 4.405 | 3.72 | 2.94 | 2.128 | 1.261 | 0.32 | -4.698 | -11.276 | -17.335 | -24.367 | Primary | 1678
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - System Transformation | 10.314 | 10.383 | 10.445 | 10.497 | 10.542 | 10.581 | 10.611 | 10.702 | 10.4 | 10.143 | 9.895 | Primary | 1679
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - System Transformation | 11.241 | 11.314 | 11.366 | 11.391 | 11.39 | 11.361 | 11.301 | 10.678 | 9.506 | 8.843 | 8.422 | Primary | 1680
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - System Transformation | 2.456 | 2.514 | 2.562 | 2.601 | 2.632 | 2.654 | 2.667 | 2.648 | 2.252 | 1.915 | 1.572 | Primary | 1681
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - System Transformation | 6.321 | 6.086 | 5.816 | 5.548 | 5.294 | 5.026 | 4.735 | 3.549 | 2.198 | 0.698 | -1.34 | Primary | 1682
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - System Transformation | 0.547 | 0.332 | 0.084 | -0.177 | -0.45 | -0.737 | -1.036 | -2.546 | -4.113 | -5.689 | -7.648 | Primary | 1683
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - System Transformation | 12.425 | 12.167 | 11.828 | 11.436 | 11.046 | 10.628 | 10.175 | 7.852 | 5.034 | 2.463 | -0.73 | Primary | 1684
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - System Transformation | 12.837 | 10.897 | 10.876 | 10.821 | 10.73 | 10.604 | 10.425 | 9.708 | 8.276 | 7.138 | 5.972 | Primary | 1685
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - System Transformation | 9.088 | 8.699 | 15.268 | 14.861 | 14.466 | 14.056 | 13.623 | 11.58 | 9.126 | 6.322 | 2.308 | Primary | 1686
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - System Transformation | 9.988 | 9.84 | 9.661 | 9.455 | 9.251 | 9.02 | 8.756 | 7.059 | 4.323 | 1.438 | -2.201 | Primary | 1687
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - System Transformation | 3.007 | 1.22 | 0.699 | 0.301 | -0.093 | -0.508 | -0.952 | -3.126 | -6.528 | -10.409 | -15.801 | Primary | 1688
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - System Transformation | 12.513 | 12.458 | 12.39 | 12.31 | 12.232 | 12.147 | 12.052 | 11.491 | 10.422 | 9.186 | 7.633 | Primary | 1689
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - System Transformation | 8.348 | 8.196 | 14.967 | 14.697 | 14.447 | 14.18 | 13.882 | 12.327 | 9.956 | 7.216 | 3.323 | Primary | 1690
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - System Transformation | 4.766 | 3.423 | 2.767 | 2.251 | 1.719 | 1.149 | 0.531 | -2.432 | -6.306 | -10.05 | -14.681 | Primary | 1691
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - System Transformation | 10.126 | 9.713 | 9.174 | 8.574 | 8.017 | 7.446 | 6.852 | 4.079 | 1.183 | -2.81 | -9.016 | Primary | 1692
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - System Transformation | 10.221 | 10.041 | 7.641 | 7.269 | 6.827 | 6.283 | 5.626 | 1.595 | -2.916 | -6.05 | -8.923 | Primary | 1693
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - System Transformation | 8.228 | 7.811 | 7.283 | 6.688 | 6.077 | 5.438 | 4.762 | 1.456 | -1.549 | -4.983 | -9.725 | Primary | 1694
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - System Transformation | 6.757 | 4.736 | 4.177 | 3.605 | 3.052 | 2.472 | 1.851 | -0.753 | -3.812 | -7.429 | -12.667 | Primary | 1695
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - System Transformation | 8.482 | 7.804 | 7.848 | 7.851 | 7.818 | 7.749 | 7.631 | 6.771 | 4.675 | 3.243 | 2.045 | Primary | 1696
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - System Transformation | 18.737 | 18.707 | 18.648 | 18.556 | 18.428 | 18.258 | 18.04 | 16.514 | 14.521 | 13.337 | 12.446 | Primary | 1697
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - System Transformation | 8.591 | 8.465 | 8.271 | 8.038 | 7.822 | 7.594 | 7.349 | 6.147 | 4.49 | 2.294 | -1.092 | Primary | 1698
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - System Transformation | 10.666 | 10.479 | 10.227 | 9.928 | 9.593 | 9.235 | 8.851 | 6.882 | 4.342 | 1.931 | -1.118 | Primary | 1699
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - System Transformation | 11.984 | 11.727 | 11.378 | 10.978 | 10.616 | 10.242 | 9.841 | 8.026 | 5.29 | 2.178 | -2.235 | Primary | 1700
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - System Transformation | 12.263 | 12.252 | 12.21 | 12.147 | 12.071 | 11.979 | 11.864 | 11.178 | 9.982 | 8.666 | 6.933 | Primary | 1701
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - System Transformation | 8.286 | 8.36 | 8.428 | 8.497 | 8.555 | 8.601 | 8.631 | 8.669 | 8.062 | 7.526 | 6.939 | Primary | 1702
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - System Transformation | 7.974 | 6.144 | 6.002 | 5.844 | 5.704 | 5.537 | 5.336 | 4.087 | 2.116 | -0.343 | -3.941 | Primary | 1703
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - System Transformation | 9.876 | 8.683 | 8.739 | 8.773 | 8.789 | 8.794 | 8.781 | 8.668 | 7.79 | 7.013 | 6.182 | Primary | 1704
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - System Transformation | 1.145 | 0.92 | 0.65 | 0.356 | 0.071 | -0.225 | -0.539 | -2.034 | -3.957 | -5.934 | -8.506 | Primary | 1705
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 2.848 | 2.82 | 2.782 | 2.745 | 2.706 | 2.663 | 2.612 | 2.334 | 1.783 | 0.995 | -0.172 | Primary | 1706
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - System Transformation | 12.835 | 12.737 | 12.597 | 12.419 | 12.21 | 11.963 | 11.672 | 9.809 | 7.442 | 5.508 | 3.498 | Primary | 1707
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - System Transformation | 24.413 | 24.412 | 24.402 | 24.377 | 24.341 | 24.298 | 24.241 | 23.961 | 23.086 | 22.251 | 21.393 | Primary | 1708
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - System Transformation | 13.77 | 13.785 | 13.777 | 13.751 | 13.724 | 13.689 | 13.645 | 13.424 | 12.781 | 12.094 | 11.199 | Primary | 1709
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - System Transformation | -1.906 | -2.095 | -2.323 | -2.585 | -2.86 | -3.157 | -3.482 | -5.34 | -7.972 | -10.641 | -13.644 | Primary | 1710
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - System Transformation | 3.12 | 2.823 | 2.459 | 2.018 | 1.528 | 0.952 | 0.273 | -3.944 | -10.116 | -15.221 | -20.611 | Primary | 1711
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - System Transformation | 10.947 | 10.775 | 10.517 | 10.213 | 9.924 | 9.625 | 9.306 | 7.82 | 5.821 | 3.42 | -0.103 | Primary | 1712
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - System Transformation | 11.297 | 11.374 | 11.434 | 11.477 | 11.502 | 11.508 | 11.494 | 11.208 | 10.64 | 10.339 | 10.177 | Primary | 1713
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - System Transformation | 7.988 | 7.56 | 7.01 | 6.387 | 5.774 | 5.124 | 4.427 | 0.873 | -3.599 | -8.345 | -14.666 | Primary | 1714
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - System Transformation | 11.677 | 10.925 | 10.738 | 10.526 | 10.311 | 10.084 | 9.837 | 8.847 | 7.027 | 4.757 | 1.614 | Primary | 1715
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - System Transformation | 3.96 | 3.596 | 3.198 | 2.825 | 2.459 | 2.085 | 1.704 | -0.025 | -2.15 | -4.711 | -8.472 | Primary | 1716
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - System Transformation | 10.926 | 10.724 | 10.426 | 10.067 | 9.725 | 9.368 | 8.994 | 7.18 | 4.548 | 1.439 | -3.156 | Primary | 1717
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - System Transformation | -1.288 | -1.481 | -1.72 | -1.981 | -0.232 | -0.493 | -0.769 | -2.092 | -4.064 | -6.389 | -9.714 | Primary | 1718
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - System Transformation | 15.247 | 15.178 | 15.083 | 14.957 | 14.81 | 14.635 | 14.424 | 13.103 | 10.706 | 8.735 | 6.663 | Primary | 1719
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - System Transformation | 14.206 | 13.482 | 12.864 | 12.476 | 12.087 | 11.676 | 11.237 | 9.046 | 6.107 | 3.24 | -0.526 | Primary | 1720
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - System Transformation | 10.059 | 9.764 | 9.34 | 8.849 | 8.345 | 7.822 | 7.268 | 4.653 | 2.391 | -0.649 | -5.244 | Primary | 1721
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - System Transformation | 23.731 | 23.759 | 23.784 | 23.809 | 23.831 | 23.848 | 23.859 | 23.867 | 23.576 | 23.308 | 22.997 | Primary | 1722
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - System Transformation | 8.482 | 8.499 | 8.516 | 8.534 | 8.542 | 8.543 | 8.525 | 8.448 | 7.496 | 6.695 | 5.874 | Primary | 1723
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - System Transformation | 11.234 | 10.97 | 10.601 | 10.172 | 9.771 | 9.359 | 8.926 | 6.942 | 4.845 | 2.076 | -2.178 | Primary | 1724
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - System Transformation | 4.322 | 4.29 | 4.25 | 4.206 | 4.163 | 4.116 | 4.065 | 3.759 | 3.311 | 2.773 | 2.1 | Primary | 1725
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - System Transformation | 8.764 | 8.634 | 8.476 | 8.296 | 8.115 | 7.921 | 7.708 | 6.535 | 4.6 | 2.527 | -0.031 | Primary | 1726
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - System Transformation | 13.798 | 13.536 | 13.19 | 12.804 | 12.438 | 12.061 | 11.665 | 9.777 | 7.501 | 4.578 | 0.108 | Primary | 1727
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - System Transformation | 10.667 | 10.342 | 9.947 | 9.51 | 9.076 | 8.622 | 8.143 | 5.939 | 3.577 | 0.791 | -3 | Primary | 1728
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - System Transformation | 7.7 | 7.346 | 6.875 | 6.318 | 5.681 | 5.014 | 4.322 | 1.052 | -2.017 | -5.401 | -9.815 | Primary | 1729
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - System Transformation | 12.951 | 12.648 | 12.306 | 11.924 | 11.519 | 11.079 | 10.593 | 7.907 | 4.022 | 0.383 | -3.639 | Primary | 1730
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - System Transformation | 7.67 | 7.632 | 7.54 | 7.399 | 7.232 | 7.029 | 6.782 | 5.131 | 2.052 | -1.007 | -4.961 | Primary | 1731
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - System Transformation | 13.748 | 13.533 | 13.233 | 12.89 | 12.557 | 12.215 | 11.854 | 10.177 | 8.385 | 6.012 | 2.384 | Primary | 1732
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - System Transformation | 7.071 | 6.611 | 6.102 | 5.618 | 5.141 | 4.644 | 4.121 | 18.736 | 15.498 | 11.707 | 6.276 | Primary | 1733
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - System Transformation | 7.368 | 7.18 | 6.956 | 6.694 | 6.42 | 6.121 | 5.781 | 3.869 | 0.345 | -3.126 | -7.162 | Primary | 1734
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NPg Best View | 13.323 | 13.179 | 13.015 | 12.96 | 12.95 | 12.933 | 12.903 | 12.768 | 11.275 | 10.048 | 8.892 | Primary | 1735
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NPg Best View | 12.3 | 10.691 | 10.599 | 10.436 | 10.308 | 10.123 | 9.871 | 8.348 | 5.773 | 4.073 | 2.578 | Primary | 1736
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NPg Best View | 11.53 | 11.299 | 10.957 | 10.556 | 10.112 | 9.657 | 9.149 | 6.807 | 2.484 | -0.926 | -3.974 | Primary | 1737
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NPg Best View | 6.091 | 4.805 | 4.871 | 4.862 | 4.843 | 4.786 | 4.676 | 4.043 | 2.061 | 0.624 | -0.642 | Primary | 1738
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NPg Best View | 15.556 | 15.265 | 14.884 | 14.508 | 14.27 | 14.017 | 13.703 | 12.284 | 9.176 | 6.78 | 4.573 | Primary | 1739
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NPg Best View | 17.183 | 17.201 | 17.194 | 17.18 | 17.189 | 17.192 | 17.184 | 17.117 | 16.499 | 15.996 | 15.508 | Primary | 1740
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NPg Best View | 9.13 | 8.687 | 8.061 | 7.334 | 6.851 | 6.348 | 5.768 | 3.082 | -2.144 | -6.12 | -9.962 | Primary | 1741
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NPg Best View | 17.254 | 17.337 | 17.368 | 17.377 | 17.399 | 17.417 | 17.422 | 17.455 | 16.217 | 15.193 | 14.231 | Primary | 1742
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NPg Best View | 1.105 | 0.965 | 0.741 | 0.457 | 0.209 | -0.059 | -0.378 | -1.923 | -5.604 | -8.603 | -11.342 | Primary | 1743
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NPg Best View | 3.469 | 3.046 | 3.231 | 3.377 | 3.531 | 3.668 | 3.777 | 4.162 | 3.561 | 3.099 | 2.651 | Primary | 1744
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NPg Best View | 12.059 | 11.865 | 11.551 | 11.165 | 10.924 | 10.666 | 10.355 | 9.943 | 7.065 | 4.851 | 2.667 | Primary | 1745
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NPg Best View | 2.766 | 2.543 | 2.198 | 1.845 | 1.561 | 1.23 | 0.81 | -1.33 | -4.782 | -7.067 | -9.158 | Primary | 1746
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NPg Best View | 3.347 | 3.356 | 3.351 | 3.338 | 3.326 | 3.307 | 3.279 | 3.13 | 2.834 | 2.605 | 2.388 | Primary | 1747
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NPg Best View | 15.784 | 15.638 | 15.389 | 15.082 | 14.929 | 14.768 | 14.57 | 13.651 | 10.82 | 8.619 | 6.484 | Primary | 1748
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NPg Best View | 13.1 | 12.618 | 12.596 | 12.557 | 12.542 | 12.522 | 12.49 | 12.348 | 11.49 | 10.759 | 10.039 | Primary | 1749
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NPg Best View | 10.654 | 10.691 | 10.655 | 10.581 | 10.523 | 10.451 | 10.354 | 9.865 | 8.002 | 6.652 | 5.444 | Primary | 1750
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NPg Best View | 15.65 | 15.371 | 14.96 | 14.473 | 14.126 | 13.745 | 13.29 | 11.072 | 7.687 | 5.334 | 3.161 | Primary | 1751
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NPg Best View | 8.382 | 8.427 | 8.439 | 8.426 | 8.415 | 8.39 | 8.344 | 8.016 | 6.78 | 5.853 | 5.044 | Primary | 1752
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NPg Best View | 5.863 | 5.771 | 5.586 | 5.354 | 5.176 | 4.992 | 4.787 | 3.794 | 0.322 | -2.665 | -5.581 | Primary | 1753
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NPg Best View | 21.471 | 21.463 | 21.397 | 21.292 | 21.23 | 21.159 | 21.058 | 20.614 | 19.425 | 18.514 | 17.679 | Primary | 1754
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NPg Best View | 3.713 | 3.607 | 3.455 | 3.284 | 3.168 | 3.047 | 2.914 | 2.236 | 0.43 | -1.148 | -2.727 | Primary | 1755
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NPg Best View | 11.653 | 11.279 | 10.714 | 10.031 | 9.564 | 9.053 | 8.444 | 5.383 | -0.08 | -4.096 | -7.909 | Primary | 1756
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NPg Best View | 9.532 | 9.194 | 8.698 | 8.158 | 7.785 | 7.385 | 6.897 | 4.799 | 0.686 | -2.411 | -5.258 | Primary | 1757
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NPg Best View | 14.775 | 14.576 | 14.295 | 14.007 | 13.807 | 13.596 | 13.338 | 12.206 | 10.211 | 8.786 | 7.482 | Primary | 1758
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NPg Best View | 3.045 | 3.042 | 2.897 | 2.675 | 2.55 | 2.384 | 2.157 | 0.834 | -2.462 | -4.772 | -6.962 | Primary | 1759
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NPg Best View | 5.455 | 5.29 | 5.035 | 4.717 | 4.476 | 4.204 | 3.874 | 2.212 | -0.189 | -1.877 | -3.43 | Primary | 1760
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 15.193 | 15.184 | 15.128 | 15.048 | 14.972 | 14.884 | 14.778 | 14.347 | 13.036 | 12.004 | 11.073 | Primary | 1761
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 4.388 | 1.479 | 1.465 | 1.365 | 1.271 | 1.11 | 0.865 | -0.616 | -4.405 | -7.139 | -9.545 | Primary | 1762
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NPg Best View | 7.469 | 7.397 | 7.197 | 6.931 | 6.687 | 6.397 | 6.045 | 4.087 | 0.478 | -2.064 | -4.396 | Primary | 1763
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NPg Best View | 11.763 | 11.536 | 11.162 | 10.696 | 10.416 | 10.118 | 9.757 | 8.043 | 3.61 | 0.098 | -3.21 | Primary | 1764
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NPg Best View | 5.903 | 5.558 | 4.99 | 4.299 | 3.788 | 3.229 | 2.556 | -0.779 | -7.112 | -11.839 | -16.205 | Primary | 1765
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NPg Best View | 6.885 | 6.873 | 6.855 | 6.833 | 6.814 | 6.795 | 6.773 | 6.671 | 6.361 | 6.087 | 5.82 | Primary | 1766
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NPg Best View | 3.717 | 3.696 | 3.654 | 3.602 | 3.552 | 3.494 | 3.423 | 3.034 | 2.375 | 1.872 | 1.405 | Primary | 1767
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NPg Best View | 11.642 | 11.303 | 10.783 | 10.171 | 9.808 | 9.425 | 8.974 | 6.898 | 2.5 | -0.842 | -4.14 | Primary | 1768
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 13.591 | 13.534 | 13.469 | 13.388 | 13.3 | 13.206 | 13.103 | 12.57 | 11.355 | 10.158 | 8.957 | Primary | 1769
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NPg Best View | 4.638 | 4.544 | 4.408 | 4.25 | 4.138 | 4.023 | 3.888 | 3.259 | 2.235 | 1.487 | 0.787 | Primary | 1770
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 9.532 | 9.295 | 8.89 | 8.394 | 8.108 | 7.801 | 7.417 | 5.547 | 1.049 | -2.355 | -5.585 | Primary | 1771
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NPg Best View | 11.644 | 11.451 | 11.118 | 10.711 | 10.41 | 10.077 | 9.663 | 7.626 | 3.763 | 0.919 | -1.653 | Primary | 1772
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NPg Best View | 9.367 | 9.437 | 9.437 | 9.394 | 9.407 | 9.398 | 9.36 | 9.065 | 7.427 | 6.187 | 4.995 | Primary | 1773
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NPg Best View | 10.299 | 10.351 | 10.345 | 10.293 | 10.286 | 10.26 | 10.19 | 9.745 | 8.642 | 7.87 | 7.152 | Primary | 1774
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NPg Best View | 17.498 | 17.354 | 17.142 | 16.886 | 16.691 | 16.471 | 16.205 | 14.89 | 13.279 | 12.264 | 11.371 | Primary | 1775
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NPg Best View | 7.755 | 22.328 | 22.119 | 21.868 | 21.687 | 21.493 | 21.255 | 20.097 | 16.974 | 14.49 | 12.239 | Primary | 1776
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NPg Best View | 10.221 | 9.873 | 9.347 | 8.707 | 8.226 | 7.731 | 7.155 | 21.736 | 16.07 | 11.439 | 7.1 | Primary | 1777
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NPg Best View | 3.906 | 3.81 | 3.677 | 3.542 | 3.471 | 3.394 | 3.296 | 2.891 | 2.142 | 1.614 | 1.099 | Primary | 1778
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NPg Best View | 6.116 | 5.335 | 4.336 | 3.338 | 2.537 | 1.685 | 0.699 | -3.227 | -8.946 | -13.064 | -16.626 | Primary | 1779
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NPg Best View | 3.838 | 3.54 | 3.08 | 2.529 | 1.931 | 1.299 | 0.561 | -3.085 | -9.793 | -15.231 | -20.19 | Primary | 1780
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NPg Best View | 5.138 | 4.658 | 3.943 | 3.078 | 2.434 | 1.757 | 0.964 | 21.378 | 14.033 | 8.162 | 2.64 | Primary | 1781
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NPg Best View | 4.118 | 4.207 | 4.28 | 4.339 | 4.39 | 4.428 | 4.451 | 4.483 | 4.298 | 4.2 | 4.12 | Primary | 1782
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NPg Best View | 8.03 | 7.642 | 7.025 | 6.251 | 5.67 | 5.003 | 4.186 | 16.872 | 10.554 | 6.256 | 2.351 | Primary | 1783
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NPg Best View | 12.866 | 12.986 | 13.085 | 13.156 | 13.214 | 13.258 | 13.284 | 13.314 | 12.569 | 12.036 | 11.581 | Primary | 1784
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NPg Best View | 9.581 | 9.77 | 9.943 | 10.098 | 10.241 | 10.371 | 10.484 | 10.936 | 11.038 | 11.131 | 11.218 | Primary | 1785
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NPg Best View | 11.257 | 11.452 | 11.593 | 11.717 | 11.838 | 11.938 | 12.002 | 12.198 | 10.565 | 9.28 | 8.109 | Primary | 1786
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NPg Best View | 9.092 | 9.213 | 9.292 | 9.351 | 9.417 | 9.472 | 9.504 | 9.613 | 8.881 | 8.323 | 7.793 | Primary | 1787
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NPg Best View | 10.843 | 10.6 | 10.201 | 9.716 | 9.374 | 8.98 | 8.489 | 5.96 | 2.367 | 0.068 | -2.021 | Primary | 1788
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NPg Best View | 5.137 | 5.103 | 5.045 | 4.975 | 4.907 | 4.833 | 4.738 | 4.309 | 4.031 | 3.887 | 3.788 | Primary | 1789
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NPg Best View | 7.712 | 7.743 | 7.743 | 7.73 | 7.711 | 7.681 | 7.632 | 7.381 | 6.88 | 6.433 | 5.989 | Primary | 1790
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NPg Best View | 13.247 | 12.875 | 12.376 | 11.867 | 11.517 | 11.14 | 10.678 | 8.461 | 3.922 | 0.504 | -2.583 | Primary | 1791
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NPg Best View | 0.842 | 0.861 | 0.866 | 0.862 | 0.857 | 0.845 | 0.823 | 0.676 | 0.364 | 0.12 | -0.113 | Primary | 1792
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NPg Best View | 2.46 | 2.275 | 2.024 | 1.741 | 1.531 | 1.313 | 1.057 | -0.14 | -1.954 | -3.284 | -4.548 | Primary | 1793
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 9.623 | 9.445 | 9.121 | 8.716 | 8.447 | 8.144 | 7.776 | 5.941 | 2.796 | 0.686 | -1.35 | Primary | 1794
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NPg Best View | 8.525 | 8.461 | 8.339 | 8.233 | 8.177 | 8.106 | 7.992 | 7.393 | 5.163 | 3.427 | 1.832 | Primary | 1795
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NPg Best View | 5.263 | 5.009 | 4.63 | 4.196 | 3.879 | 3.542 | 3.15 | 1.321 | -2.436 | -5.409 | -8.298 | Primary | 1796
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NPg Best View | 4.213 | 4.25 | 4.278 | 4.296 | 4.31 | 4.317 | 4.315 | 4.253 | 4.002 | 3.833 | 3.69 | Primary | 1797
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NPg Best View | 21.996 | 21.866 | 21.66 | 21.433 | 21.314 | 21.186 | 21.024 | 20.272 | 17.828 | 15.916 | 14.125 | Primary | 1798
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NPg Best View | 7.521 | 7.633 | 7.7 | 7.749 | 7.821 | 7.88 | 7.918 | 8.023 | 6.912 | 6.028 | 5.184 | Primary | 1799
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NPg Best View | 13.174 | 12.935 | 12.621 | 12.33 | 12.144 | 11.941 | 11.679 | 10.416 | 7.515 | 5.303 | 3.313 | Primary | 1800
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NPg Best View | 8.525 | 8.558 | 8.51 | 8.403 | 8.334 | 8.245 | 8.108 | 7.322 | 4.878 | 3.003 | 1.279 | Primary | 1801
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NPg Best View | 2.436 | 1.833 | 0.971 | 0.017 | -0.519 | -1.105 | -1.832 | -5.265 | -12.398 | -17.655 | -22.615 | Primary | 1802
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NPg Best View | 1.012 | 0.907 | 0.765 | 0.587 | 0.412 | 0.22 | -0.001 | -0.694 | -1.427 | -2.045 | -2.645 | Primary | 1803
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NPg Best View | 2.922 | 2.854 | 2.724 | 2.543 | 2.369 | 2.16 | 1.902 | 0.412 | -2.216 | -4.238 | -6.119 | Primary | 1804
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NPg Best View | 13.006 | 12.984 | 12.886 | 12.734 | 12.619 | 12.488 | 12.314 | 12.596 | 10.947 | 9.71 | 8.63 | Primary | 1805
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NPg Best View | 14.532 | 14.378 | 15.102 | 14.748 | 14.533 | 14.306 | 14.022 | 12.659 | 9.241 | 6.574 | 4.054 | Primary | 1806
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NPg Best View | 22.208 | 22.228 | 22.12 | 21.877 | 21.58 | 21.167 | 20.619 | 17.227 | 12.482 | 9.61 | 7.286 | Primary | 1807
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NPg Best View | 9.844 | 9.603 | 9.241 | 8.817 | 8.471 | 8.105 | 7.685 | 12.691 | 8.775 | 5.646 | 2.675 | Primary | 1808
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NPg Best View | 1.95 | 1.665 | 1.275 | 0.82 | 0.537 | 0.231 | -0.133 | -1.7 | -4.265 | -6.2 | -8.148 | Primary | 1809
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NPg Best View | 8.067 | 7.77 | 7.238 | 6.567 | 6.25 | 5.914 | 5.496 | 3.586 | -2.434 | -7.227 | -11.929 | Primary | 1810
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NPg Best View | 5.265 | 2.98 | 2.975 | 2.938 | 2.897 | 2.837 | 2.746 | 2.25 | 0.941 | -0.053 | -0.939 | Primary | 1811
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NPg Best View | 7.624 | 7.27 | 6.737 | 6.102 | 5.711 | 5.29 | 4.767 | 2.247 | -2.662 | -6.291 | -9.667 | Primary | 1812
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NPg Best View | 3.458 | 3.262 | 17.631 | 17.223 | 16.907 | 16.561 | 16.134 | 14.003 | 9.334 | 5.788 | 2.645 | Primary | 1813
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NPg Best View | -0.428 | -0.542 | -0.71 | -0.915 | -1.076 | -1.242 | -1.436 | -2.357 | -4.373 | -6.049 | -7.641 | Primary | 1814
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NPg Best View | 2.567 | 2.588 | 2.578 | 2.55 | 2.532 | 2.507 | 2.469 | 2.255 | 1.49 | 0.945 | 0.45 | Primary | 1815
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NPg Best View | 10.422 | 10.199 | 9.822 | 9.363 | 9.056 | 8.732 | 8.337 | 6.581 | 2.794 | -0.071 | -2.706 | Primary | 1816
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NPg Best View | 8.323 | 8.018 | 7.527 | 6.934 | 6.605 | 6.244 | 5.8 | 3.617 | -1.003 | -4.384 | -7.666 | Primary | 1817
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NPg Best View | 11.299 | 11.23 | 11.087 | 10.893 | 10.773 | 10.627 | 10.43 | 9.356 | 7.654 | 6.494 | 5.413 | Primary | 1818
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NPg Best View | 3.672 | 2.808 | 2.841 | 2.82 | 2.796 | 2.734 | 2.621 | 1.891 | -0.362 | -1.974 | -3.42 | Primary | 1819
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NPg Best View | 14.923 | 14.861 | 14.75 | 14.593 | 14.432 | 14.237 | 14.004 | 12.643 | 10.402 | 8.76 | 7.247 | Primary | 1820
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NPg Best View | 4.468 | 4.396 | 4.289 | 4.161 | 4.073 | 3.979 | 3.87 | 3.36 | 2.197 | 1.267 | 0.38 | Primary | 1821
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NPg Best View | 2.078 | 2.029 | 1.939 | 1.826 | 1.756 | 1.681 | 1.588 | 1.16 | -0.053 | -0.997 | -1.871 | Primary | 1822
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NPg Best View | 15.048 | 14.763 | 14.312 | 13.756 | 13.377 | 12.953 | 12.438 | 9.786 | 4.887 | 1.228 | -2.255 | Primary | 1823
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NPg Best View | 2.805 | 2.715 | 4.481 | 4.17 | 3.913 | 3.635 | 3.285 | 1.557 | -2.982 | -6.559 | -9.835 | Primary | 1824
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NPg Best View | 14.812 | 14.759 | 14.612 | 14.433 | 14.347 | 14.256 | 14.151 | 13.651 | 11.447 | 9.745 | 8.076 | Primary | 1825
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NPg Best View | 4.441 | 4.355 | 4.233 | 4.089 | 3.967 | 3.839 | 3.69 | 2.995 | 1.703 | 0.684 | -0.264 | Primary | 1826
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NPg Best View | 4.708 | 4.289 | 3.659 | 2.923 | 2.381 | 1.804 | 1.121 | -2.083 | -7.138 | -10.8 | -14.301 | Primary | 1827
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NPg Best View | 11.625 | 11.307 | 10.845 | 10.316 | 9.967 | 9.605 | 9.179 | 7.261 | 3.634 | 0.87 | -1.84 | Primary | 1828
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NPg Best View | 12.157 | 10.568 | 10.425 | 10.17 | 9.918 | 9.557 | 9.075 | 6.368 | 3.134 | 1.362 | -0.074 | Primary | 1829
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NPg Best View | 1.022 | 0.739 | 0.41 | 0.16 | -0.036 | -0.242 | -0.493 | -1.539 | -2.805 | -3.577 | -4.223 | Primary | 1830
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NPg Best View | 7.43 | 6.783 | 5.889 | 4.871 | 4.199 | 3.5 | 2.693 | -0.878 | -6.782 | -11.093 | -15.247 | Primary | 1831
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NPg Best View | 9.201 | 9.216 | 9.217 | 9.21 | 9.199 | 9.181 | 9.15 | 9.007 | 8.836 | 8.667 | 8.495 | Primary | 1832
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NPg Best View | 1.691 | 1.485 | 1.155 | 0.706 | 0.199 | -0.435 | -1.224 | -5.915 | -10.345 | -12.683 | -14.418 | Primary | 1833
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NPg Best View | 10.525 | 10.2 | 9.756 | 9.312 | 9.041 | 8.743 | 8.378 | 6.603 | 2 | -1.579 | -4.936 | Primary | 1834
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NPg Best View | 8.801 | 8.459 | 7.915 | 7.244 | 6.826 | 6.363 | 5.8 | 2.985 | -2.017 | -5.603 | -9.012 | Primary | 1835
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NPg Best View | 1.351 | 1.27 | 1.138 | 0.964 | 0.789 | 0.572 | 0.304 | -1.249 | -2.789 | -3.682 | -4.424 | Primary | 1836
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NPg Best View | 7.287 | 7.022 | 6.591 | 6.066 | 5.709 | 5.336 | 4.888 | 2.861 | -2.147 | -6.146 | -9.928 | Primary | 1837
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NPg Best View | 1.008 | 1.022 | 0.935 | 0.791 | 0.74 | 0.669 | 0.559 | 0.033 | -2.174 | -3.841 | -5.405 | Primary | 1838
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NPg Best View | 1.501 | 1.502 | 1.503 | 1.503 | 1.502 | 1.502 | 1.501 | 1.492 | 1.477 | 1.462 | 1.448 | Primary | 1839
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 24.118 | 24.194 | 24.2 | 24.174 | 24.182 | 24.185 | 24.17 | 24.135 | 22.602 | 21.381 | 20.2 | Primary | 1840
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 33.871 | 33.843 | 33.767 | 33.669 | 33.614 | 33.554 | 33.475 | 33.135 | 32.167 | 31.433 | 30.721 | Primary | 1841
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 20.528 | 20.472 | 20.384 | 20.275 | 20.187 | 20.093 | 19.978 | 19.456 | 18.698 | 18.148 | 17.66 | Primary | 1842
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 14.686 | 14.494 | 14.209 | 13.882 | 13.653 | 13.393 | 13.075 | 11.419 | 8.767 | 6.882 | 5.12 | Primary | 1843
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NPg Best View | 13.603 | 13.348 | 12.986 | 13.545 | 13.156 | 12.756 | 12.297 | 10.241 | 6.768 | 4.175 | 1.88 | Primary | 1844
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NPg Best View | 10.432 | 9.403 | 8.992 | 8.482 | 8.193 | 7.887 | 7.514 | 5.948 | 2.374 | -0.404 | -3.13 | Primary | 1845
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NPg Best View | 1.476 | 15.27 | 14.975 | 14.618 | 14.252 | 13.836 | 13.337 | 10.704 | 7.327 | 4.92 | 2.783 | Primary | 1846
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NPg Best View | 10.888 | 10.349 | 9.742 | 9.325 | 9.09 | 8.835 | 8.518 | 7.096 | 3.232 | 0.251 | -2.564 | Primary | 1847
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NPg Best View | 15.398 | 15.386 | 15.354 | 15.31 | 15.28 | 15.246 | 15.205 | 14.976 | 14.101 | 13.299 | 12.499 | Primary | 1848
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NPg Best View | 3.901 | 3.079 | 1.893 | 0.486 | -0.502 | -1.548 | -2.79 | -7.692 | -15.789 | -22.02 | -27.874 | Primary | 1849
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NPg Best View | 6.281 | 5.715 | 4.964 | 4.196 | 3.752 | 3.283 | 2.717 | 0.257 | -4.233 | -7.36 | -10.29 | Primary | 1850
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NPg Best View | 4.458 | 4.517 | 4.461 | 4.337 | 4.393 | 4.43 | 4.434 | 4.278 | 1.316 | -1.156 | -3.722 | Primary | 1851
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NPg Best View | 17.173 | 14.178 | 13.93 | 13.635 | 13.408 | 13.173 | 12.91 | 11.87 | 9.739 | 7.902 | 6.078 | Primary | 1852
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NPg Best View | 14.777 | 14.766 | 14.724 | 14.655 | 14.576 | 14.475 | 14.349 | 13.597 | 12.369 | 11.468 | 10.642 | Primary | 1853
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NPg Best View | 9.288 | 9.118 | 8.877 | 8.564 | 8.22 | 7.805 | 7.307 | 4.385 | 0.942 | -1.458 | -3.601 | Primary | 1854
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NPg Best View | 11.745 | 11.762 | 11.699 | 11.601 | 11.567 | 11.529 | 11.478 | 11.252 | 9.093 | 7.338 | 5.613 | Primary | 1855
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NPg Best View | 11.328 | 11.406 | 11.435 | 11.439 | 11.471 | 11.494 | 11.499 | 11.51 | 10.745 | 10.177 | 9.624 | Primary | 1856
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 3.817 | 3.676 | 3.484 | 3.233 | 2.941 | 2.585 | 2.158 | -0.395 | -3.12 | -4.99 | -6.639 | Primary | 1857
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NPg Best View | 14.745 | 14.686 | 14.561 | 14.4 | 14.313 | 14.209 | 14.082 | 13.337 | 11.314 | 9.736 | 8.205 | Primary | 1858
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NPg Best View | 10.682 | 10.426 | 10 | 9.478 | 9.221 | 8.945 | 8.607 | 7.08 | 3.062 | 0.022 | -2.96 | Primary | 1859
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NPg Best View | 9.49 | 9.396 | 9.156 | 8.858 | 8.704 | 8.538 | 8.343 | 7.367 | 3.905 | 1.27 | -1.281 | Primary | 1860
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NPg Best View | 7.166 | 6.879 | 6.399 | 5.803 | 5.416 | 4.985 | 4.449 | 1.755 | -2.935 | -6.198 | -9.198 | Primary | 1861
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NPg Best View | 4.495 | 4.106 | 3.521 | 2.832 | 2.319 | 1.742 | 1.046 | 14.904 | 10.195 | 6.863 | 3.81 | Primary | 1862
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NPg Best View | 11.054 | 11.087 | 11.06 | 10.985 | 10.878 | 10.709 | 10.46 | 8.972 | 7.745 | 7.246 | 6.942 | Primary | 1863
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NPg Best View | 15.413 | 15.141 | 14.705 | 14.173 | 13.914 | 13.645 | 13.322 | 11.862 | 7.997 | 5.008 | 2.039 | Primary | 1864
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NPg Best View | 8.904 | 8.499 | 7.879 | 7.113 | 6.516 | 5.834 | 5.004 | 0.611 | -5.482 | -9.626 | -13.405 | Primary | 1865
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NPg Best View | 3.301 | 3.206 | 3.07 | 3.411 | 3.29 | 3.162 | 3.012 | 2.286 | 1.044 | 0.077 | -0.841 | Primary | 1866
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NPg Best View | 7.227 | 7.099 | 6.841 | 6.51 | 6.271 | 6.013 | 5.681 | 11.142 | 6.623 | 3.017 | -0.209 | Primary | 1867
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NPg Best View | 4.177 | 4.009 | 3.751 | 3.453 | 3.292 | 3.124 | 2.921 | 2.026 | 0.018 | -1.509 | -3.021 | Primary | 1868
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 12.345 | 12.365 | 12.347 | 12.305 | 12.283 | 12.25 | 12.199 | 11.912 | 10.878 | 10.017 | 9.164 | Primary | 1869
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 25.335 | 25.311 | 25.257 | 25.185 | 25.135 | 25.081 | 25.019 | 24.705 | 23.507 | 22.51 | 21.535 | Primary | 1870
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NPg Best View | 14.634 | 14.491 | 14.289 | 14.048 | 13.824 | 13.578 | 13.286 | 11.926 | 10.402 | 9.409 | 8.583 | Primary | 1871
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NPg Best View | 12.726 | 12.816 | 12.875 | 12.907 | 12.947 | 12.977 | 12.993 | 13.021 | 12.058 | 11.296 | 10.587 | Primary | 1872
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NPg Best View | 19.999 | 19.991 | 19.956 | 19.897 | 19.858 | 19.813 | 19.757 | 19.557 | 18.861 | 18.23 | 17.599 | Primary | 1873
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NPg Best View | 6.946 | 6.672 | 6.222 | 5.67 | 5.365 | 5.041 | 4.644 | 3.07 | -0.022 | -2.256 | -4.425 | Primary | 1874
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 21.118 | 21.16 | 21.085 | 20.971 | 20.899 | 20.817 | 20.708 | 20.197 | 17.711 | 15.79 | 13.945 | Primary | 1875
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NPg Best View | 14.046 | 14.007 | 13.895 | 13.749 | 13.723 | 13.693 | 13.65 | 13.389 | 10.901 | 8.869 | 6.886 | Primary | 1876
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NPg Best View | 4.274 | 4.195 | 4.065 | 3.906 | 3.82 | 3.726 | 3.608 | 3.04 | 1.814 | 0.906 | 0.028 | Primary | 1877
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NPg Best View | 0.948 | 0.895 | 0.808 | 0.703 | 0.593 | 0.469 | 0.316 | -0.293 | -0.839 | -1.241 | -1.61 | Primary | 1878
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NPg Best View | 16.265 | 16.224 | 16.108 | 15.943 | 15.811 | 15.653 | 15.459 | 14.442 | 12.054 | 10.199 | 8.432 | Primary | 1879
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NPg Best View | 22.226 | 22.077 | 21.837 | 21.534 | 21.325 | 21.1 | 20.818 | 19.453 | 16.584 | 14.414 | 12.49 | Primary | 1880
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NPg Best View | 26.349 | 26.272 | 26.141 | 25.979 | 25.887 | 25.789 | 25.669 | 25.107 | 23.447 | 22.133 | 20.912 | Primary | 1881
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NPg Best View | 2.409 | 2.295 | 2.142 | 1.97 | 1.807 | 1.636 | 1.437 | 0.503 | -1.093 | -2.402 | -3.594 | Primary | 1882
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NPg Best View | 2.315 | 2.131 | 1.837 | 1.473 | 1.245 | 0.986 | 0.68 | -1.059 | -5.459 | -8.975 | -12.457 | Primary | 1883
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NPg Best View | 14.366 | 14.34 | 14.256 | 14.128 | 14.015 | 13.86 | 13.656 | 12.615 | 11.418 | 10.677 | 10.025 | Primary | 1884
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NPg Best View | 4.615 | 4.548 | 4.438 | 4.31 | 4.222 | 4.132 | 4.023 | 3.517 | 2.182 | 1.116 | 0.136 | Primary | 1885
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NPg Best View | 14.544 | 14.562 | 14.546 | 14.517 | 14.506 | 14.478 | 14.422 | 14.094 | 13.03 | 12.204 | 11.45 | Primary | 1886
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NPg Best View | 9.18 | 9.345 | 9.478 | 9.584 | 9.691 | 9.776 | 9.837 | 10.997 | 10.61 | 10.381 | 10.174 | Primary | 1887
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NPg Best View | 1.262 | 0.981 | 0.583 | 0.095 | -0.259 | -0.646 | -1.115 | -3.402 | -6.353 | -8.337 | -10.121 | Primary | 1888
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NPg Best View | 16.84 | 16.819 | 16.753 | 16.671 | 16.609 | 16.542 | 16.466 | 16.095 | 14.957 | 14.066 | 13.205 | Primary | 1889
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NPg Best View | 16.775 | 16.746 | 16.674 | 16.58 | 16.502 | 16.406 | 16.287 | 15.603 | 14.497 | 13.745 | 13.05 | Primary | 1890
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NPg Best View | 4.464 | 4.112 | 3.598 | 2.99 | 2.535 | 2.047 | 1.469 | 13.524 | 9.124 | 5.777 | 2.641 | Primary | 1891
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NPg Best View | 14.361 | 14.284 | 14.141 | 13.962 | 13.846 | 13.721 | 13.58 | 12.898 | 10.837 | 9.173 | 7.57 | Primary | 1892
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NPg Best View | 8.088 | 7.672 | 7.118 | 6.558 | 6.139 | 5.693 | 5.14 | 19.556 | 14.537 | 10.699 | 7.253 | Primary | 1893
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NPg Best View | 4.986 | 4.969 | 4.848 | 4.699 | 4.568 | 4.411 | 4.209 | 3.188 | 0.006 | -2.432 | -4.662 | Primary | 1894
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NPg Best View | 10.453 | 10.226 | 9.824 | 9.31 | 9.005 | 8.684 | 8.293 | 6.477 | 1.026 | -3.403 | -7.621 | Primary | 1895
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NPg Best View | 0.167 | 0.104 | -0.002 | -0.139 | -0.236 | -0.344 | -0.473 | -1.142 | -2.703 | -3.963 | -5.178 | Primary | 1896
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NPg Best View | 13.369 | 13.133 | 12.758 | 12.322 | 12.025 | 11.705 | 11.312 | 9.45 | 5.774 | 3.044 | 0.514 | Primary | 1897
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NPg Best View | 17.515 | 17.524 | 17.508 | 17.475 | 17.445 | 17.409 | 17.361 | 17.095 | 16.064 | 15.274 | 14.556 | Primary | 1898
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NPg Best View | 12.623 | 12.431 | 12.149 | 11.831 | 11.665 | 11.491 | 11.298 | 10.332 | 7.586 | 5.309 | 2.93 | Primary | 1899
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NPg Best View | 6.951 | 6.86 | 6.703 | 6.503 | 6.328 | 6.137 | 5.912 | 4.743 | 1.949 | -0.318 | -2.414 | Primary | 1900
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NPg Best View | 9.438 | 9.349 | 9.161 | 8.897 | 8.695 | 8.441 | 8.121 | 6.149 | 2.203 | -0.772 | -3.535 | Primary | 1901
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NPg Best View | 15.336 | 15.344 | 15.346 | 15.342 | 15.334 | 15.319 | 15.295 | 16.143 | 15.939 | 15.72 | 15.502 | Primary | 1902
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NPg Best View | 16.429 | 16.376 | 16.261 | 16.105 | 15.98 | 15.844 | 15.671 | 14.819 | 12.933 | 11.505 | 10.213 | Primary | 1903
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NPg Best View | 12.875 | 12.771 | 12.578 | 12.337 | 12.166 | 11.991 | 11.788 | 10.994 | 8.479 | 6.369 | 4.38 | Primary | 1904
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NPg Best View | 10.57 | 10.182 | 9.692 | 9.268 | 9.045 | 8.806 | 8.513 | 7.233 | 3.852 | 1.296 | -1.183 | Primary | 1905
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NPg Best View | 9.616 | 9.236 | 8.69 | 8.095 | 7.749 | 7.377 | 6.912 | 4.709 | 0.191 | -3.186 | -6.37 | Primary | 1906
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NPg Best View | 2.22 | 2.285 | 2.335 | 2.375 | 2.41 | 2.437 | 2.451 | 2.476 | 2.323 | 2.243 | 2.183 | Primary | 1907
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NPg Best View | 9.988 | 9.463 | 8.816 | 8.264 | 7.9 | 7.517 | 7.055 | 21.964 | 16.725 | 12.609 | 8.788 | Primary | 1908
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NPg Best View | 4.599 | 4.451 | 4.158 | 3.762 | 3.451 | 3.082 | 2.635 | 0.14 | -5.08 | -9.017 | -12.736 | Primary | 1909
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NPg Best View | 3.38 | 3.037 | 2.54 | 1.96 | 1.54 | 1.111 | 0.617 | -1.538 | -5.859 | -9.286 | -12.576 | Primary | 1910
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NPg Best View | 23.166 | 23.184 | 23.093 | 22.94 | 22.895 | 22.841 | 22.765 | 22.38 | 19.378 | 16.973 | 14.661 | Primary | 1911
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NPg Best View | 6.407 | 6.285 | 6.08 | 5.824 | 5.63 | 5.411 | 5.143 | 3.778 | 1.347 | -0.532 | -2.343 | Primary | 1912
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NPg Best View | 6.753 | 6.747 | 6.733 | 6.715 | 6.705 | 6.694 | 6.681 | 6.61 | 6.435 | 6.307 | 6.186 | Primary | 1913
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NPg Best View | 11.636 | 11.056 | 10.169 | 9.109 | 8.505 | 7.867 | 7.112 | 3.843 | -2.875 | -8.033 | -13.147 | Primary | 1914
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NPg Best View | 21.184 | 21.222 | 21.199 | 21.107 | 20.95 | 20.705 | 20.367 | 18.305 | 16.817 | 16.315 | 16.086 | Primary | 1915
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NPg Best View | 11.287 | 11.105 | 10.785 | 10.398 | 10.173 | 9.931 | 9.635 | 8.238 | 4.66 | 1.976 | -0.58 | Primary | 1916
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NPg Best View | 12.631 | 12.495 | 12.236 | 11.875 | 11.412 | 10.829 | 10.115 | 6.131 | 1.74 | -0.927 | -3.048 | Primary | 1917
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NPg Best View | 0.182 | 0.117 | 0.005 | -0.142 | -0.276 | -0.431 | -0.622 | -1.668 | -3.352 | -4.614 | -5.777 | Primary | 1918
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NPg Best View | 6.952 | 1.123 | 0.831 | 0.483 | 0.232 | -0.036 | -0.356 | 6.825 | 4.306 | 2.474 | 0.77 | Primary | 1919
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NPg Best View | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 1920
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NPg Best View | 3.651 | 3.415 | 3.067 | 2.658 | 2.388 | 2.101 | 1.762 | 0.126 | -3.013 | -5.49 | -7.939 | Primary | 1921
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NPg Best View | 12.421 | 12.239 | 11.92 | 11.503 | 11.073 | 10.527 | 9.841 | 5.745 | 1.208 | -1.286 | -3.243 | Primary | 1922
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NPg Best View | 5.559 | 5.377 | 5.05 | 4.678 | 4.456 | 4.205 | 3.883 | 2.523 | -0.026 | -1.791 | -3.451 | Primary | 1923
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NPg Best View | 1.095 | 0.92 | 0.687 | 0.481 | 0.369 | 0.249 | 0.098 | -0.547 | -1.877 | -2.813 | -3.728 | Primary | 1924
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NPg Best View | 12.709 | 12.593 | 12.362 | 12.067 | 11.932 | 11.784 | 11.592 | 10.635 | 7.901 | 5.835 | 3.843 | Primary | 1925
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NPg Best View | 7.28 | 7.404 | 7.492 | 7.559 | 7.622 | 7.672 | 7.699 | 7.77 | 6.552 | 5.602 | 4.748 | Primary | 1926
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NPg Best View | 13.507 | 13.464 | 13.34 | 13.167 | 13.111 | 13.046 | 12.961 | 12.465 | 10.09 | 8.232 | 6.403 | Primary | 1927
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NPg Best View | 7.058 | 6.764 | 6.344 | 5.84 | 5.441 | 5.012 | 4.493 | 1.874 | -2.044 | -5.029 | -7.808 | Primary | 1928
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NPg Best View | 9.755 | 9.722 | 9.571 | 9.318 | 9.113 | 8.813 | 8.405 | 5.909 | 2.864 | 1.144 | -0.31 | Primary | 1929
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NPg Best View | 14.756 | 14.805 | 14.846 | 14.88 | 14.913 | 14.942 | 14.965 | 15.056 | 14.938 | 14.846 | 14.761 | Primary | 1930
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NPg Best View | 5.571 | 5.562 | 5.539 | 5.508 | 5.499 | 5.487 | 5.465 | 5.338 | 5.074 | 4.888 | 4.692 | Primary | 1931
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NPg Best View | 14.032 | 14.093 | 14.119 | 14.119 | 14.126 | 14.128 | 14.119 | 14.064 | 12.945 | 12.077 | 11.292 | Primary | 1932
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NPg Best View | 4.041 | 3.775 | 3.337 | 2.798 | 2.499 | 2.181 | 1.8 | 0.116 | -3.576 | -6.305 | -8.928 | Primary | 1933
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NPg Best View | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Primary | 1934
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NPg Best View | 8.804 | 7.782 | 7.193 | 6.493 | 6.037 | 5.562 | 5.004 | 2.542 | -3.178 | -7.695 | -11.946 | Primary | 1935
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NPg Best View | 8.847 | 8.354 | 7.64 | 6.849 | 23.537 | 23.101 | 22.564 | 20.03 | 14.653 | 10.655 | 6.73 | Primary | 1936
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NPg Best View | 3.294 | 3.429 | 3.519 | 3.576 | 3.609 | 3.628 | 3.623 | 3.519 | 1.766 | 0.323 | -0.968 | Primary | 1937
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NPg Best View | 1.901 | 1.647 | 1.274 | 0.828 | 0.38 | -0.082 | -0.618 | -2.984 | -7.816 | -11.796 | -15.341 | Primary | 1938
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NPg Best View | 14.46 | 14.33 | 14.112 | 13.853 | 13.676 | 13.487 | 13.253 | 12.166 | 9.199 | 6.843 | 4.674 | Primary | 1939
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NPg Best View | 5.695 | 5.268 | 4.591 | 3.765 | 3.271 | 2.737 | 2.094 | -1.012 | -6.799 | -11.056 | -15.273 | Primary | 1940
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NPg Best View | 5.015 | 4.104 | 3.783 | 3.439 | 3.202 | 2.931 | 2.587 | 0.947 | -2.672 | -5.343 | -7.818 | Primary | 1941
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NPg Best View | 14.981 | 14.818 | 14.552 | 14.241 | 14.089 | 13.927 | 13.725 | 12.881 | 10.729 | 9.053 | 7.4 | Primary | 1942
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NPg Best View | 3.57 | 3.31 | 2.883 | 2.366 | 2.065 | 1.732 | 1.319 | 13.944 | 9.778 | 6.746 | 3.838 | Primary | 1943
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NPg Best View | 6.779 | 6.558 | 6.204 | 5.777 | 5.445 | 5.078 | 4.66 | 2.489 | -1.647 | -4.756 | -7.755 | Primary | 1944
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NPg Best View | 8.332 | 7.956 | 7.381 | 6.694 | 6.284 | 5.851 | 5.334 | 2.966 | -1.41 | -4.473 | -7.448 | Primary | 1945
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NPg Best View | 5.987 | 5.688 | 5.27 | 4.78 | 4.391 | 3.984 | 3.505 | 1.355 | -1.726 | -3.905 | -5.818 | Primary | 1946
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NPg Best View | 1.486 | 0.923 | 0.212 | -0.441 | -0.89 | -1.374 | -1.983 | -4.877 | -11.576 | -16.758 | -21.341 | Primary | 1947
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NPg Best View | 9.844 | 9.412 | 8.805 | 8.178 | 7.863 | 7.531 | 7.126 | 5.291 | 0.634 | -2.907 | -6.359 | Primary | 1948
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NPg Best View | 10.815 | 10.424 | 9.876 | 9.307 | 8.902 | 8.443 | 7.871 | 4.948 | 0.324 | -2.84 | -5.699 | Primary | 1949
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NPg Best View | 12.387 | 12.411 | 12.363 | 12.252 | 12.148 | 11.996 | 11.789 | 10.44 | 8.093 | 6.651 | 5.445 | Primary | 1950
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NPg Best View | 8.619 | 8.526 | 8.358 | 8.159 | 8.016 | 7.867 | 7.686 | 6.795 | 4.587 | 2.875 | 1.29 | Primary | 1951
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NPg Best View | 2.891 | 2.843 | 2.702 | 2.517 | 2.372 | 2.193 | 1.971 | 0.702 | -1.316 | -2.556 | -3.683 | Primary | 1952
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NPg Best View | 12.89 | 12.713 | 12.414 | 12.05 | 11.838 | 11.614 | 11.342 | 10.101 | 6.975 | 4.575 | 2.295 | Primary | 1953
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NPg Best View | 18.322 | 18.267 | 18.151 | 17.993 | 17.879 | 17.756 | 17.599 | 16.841 | 15.243 | 14.017 | 12.902 | Primary | 1954
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NPg Best View | 15.466 | 15.385 | 15.232 | 15.043 | 14.951 | 14.855 | 14.746 | 14.204 | 12.038 | 10.27 | 8.483 | Primary | 1955
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NPg Best View | 2.76 | 2.458 | 1.957 | 1.278 | 0.598 | -0.253 | -1.297 | -6.183 | -11.155 | -14.279 | -16.973 | Primary | 1956
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NPg Best View | 9.86 | 9.952 | 9.99 | 9.987 | 9.994 | 9.982 | 9.944 | 9.677 | 8.16 | 7.048 | 6.04 | Primary | 1957
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NPg Best View | 6.159 | 6.046 | 5.844 | 5.584 | 5.405 | 5.191 | 4.93 | 3.601 | 1.19 | -0.599 | -2.284 | Primary | 1958
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NPg Best View | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | Primary | 1959
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NPg Best View | 6.927 | 6.461 | 5.813 | 5.125 | 4.718 | 4.269 | 3.715 | 1.146 | -3.196 | -6.271 | -9.281 | Primary | 1960
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NPg Best View | 14.389 | 14.112 | 13.689 | 13.172 | 12.91 | 12.632 | 12.298 | 10.728 | 6.935 | 4.004 | 1.089 | Primary | 1961
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NPg Best View | 3.143 | 3.007 | 2.811 | 2.582 | 2.428 | 2.269 | 2.081 | 1.219 | -0.49 | -1.854 | -3.193 | Primary | 1962
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NPg Best View | 8.797 | 8.494 | 8.016 | 7.374 | 6.731 | 5.924 | 4.937 | -1.074 | -7.985 | -12.154 | -15.747 | Primary | 1963
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NPg Best View | 13.226 | 12.833 | 12.326 | 11.839 | 11.524 | 11.193 | 10.796 | 8.929 | 5.09 | 2.215 | -0.506 | Primary | 1964
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NPg Best View | 5 | 4.923 | 4.811 | 4.681 | 4.582 | 4.481 | 4.364 | 3.838 | 2.68 | 1.741 | 0.864 | Primary | 1965
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NPg Best View | 6.135 | 5.743 | 5.158 | 4.456 | 4.001 | 3.524 | 2.963 | 0.459 | -5.254 | -9.821 | -14.282 | Primary | 1966
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NPg Best View | 10.026 | 9.787 | 9.372 | 8.854 | 8.549 | 8.224 | 7.825 | 6.093 | 1.549 | -1.985 | -5.266 | Primary | 1967
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NPg Best View | 15.681 | 15.457 | 15.163 | 14.859 | 14.666 | 14.459 | 14.202 | 13.078 | 10.493 | 8.49 | 6.67 | Primary | 1968
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NPg Best View | 6.104 | 5.931 | 5.574 | 5.119 | 4.864 | 4.589 | 4.25 | 2.749 | -1.165 | -4.093 | -6.917 | Primary | 1969
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NPg Best View | 13.001 | 12.643 | 12.146 | 11.566 | 11.005 | 10.4 | 9.685 | 6.336 | 1.477 | -2.207 | -5.516 | Primary | 1970
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NPg Best View | 12.796 | 12.761 | 12.661 | 12.531 | 12.461 | 12.387 | 12.301 | 11.952 | 10.493 | 9.311 | 8.151 | Primary | 1971
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NPg Best View | 9.355 | 9.037 | 8.558 | 8.005 | 7.638 | 7.229 | 6.734 | 4.434 | 1.048 | -1.268 | -3.503 | Primary | 1972
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NPg Best View | 11.393 | 11.437 | 11.402 | 11.316 | 11.22 | 11.081 | 10.891 | 9.762 | 8.059 | 7.06 | 6.22 | Primary | 1973
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NPg Best View | 5.608 | 5.577 | 5.411 | 5.155 | 4.981 | 4.749 | 4.444 | 2.687 | -0.5 | -2.569 | -4.468 | Primary | 1974
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NPg Best View | 28.601 | 28.549 | 28.433 | 28.277 | 28.135 | 27.962 | 27.746 | 26.524 | 24.862 | 23.761 | 22.77 | Primary | 1975
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NPg Best View | 3.214 | 3.05 | 2.82 | 2.541 | 2.327 | 2.092 | 1.821 | 0.295 | -3.483 | -6.818 | -10.053 | Primary | 1976
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NPg Best View | 1.93 | 1.916 | 1.879 | 1.831 | 1.792 | 1.748 | 1.69 | 1.41 | 0.994 | 0.672 | 0.362 | Primary | 1977
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NPg Best View | 11.693 | 11.425 | 11.042 | 10.603 | 10.316 | 10.012 | 9.652 | 7.94 | 4.26 | 1.385 | -1.413 | Primary | 1978
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NPg Best View | 9.933 | 9.967 | 9.946 | 9.884 | 9.873 | 9.844 | 9.788 | 9.412 | 7.924 | 6.802 | 5.734 | Primary | 1979
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NPg Best View | 10.749 | 10.717 | 10.577 | 10.375 | 10.255 | 10.126 | 9.971 | 9.144 | 4.466 | 0.526 | -3.175 | Primary | 1980
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NPg Best View | 1.823 | 1.772 | 1.678 | 1.554 | 1.443 | 1.311 | 1.154 | 0.379 | -0.876 | -1.814 | -2.701 | Primary | 1981
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NPg Best View | 11.91 | 11.939 | 11.892 | 11.758 | 11.545 | 11.233 | 10.816 | 8.071 | 5.011 | 3.43 | 2.311 | Primary | 1982
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NPg Best View | 15.726 | 15.714 | 15.665 | 15.606 | 15.575 | 15.529 | 15.457 | 15.027 | 13.915 | 13.131 | 12.405 | Primary | 1983
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NPg Best View | 7.823 | 6.693 | 6.112 | 5.417 | 4.908 | 4.374 | 3.749 | 0.954 | -4.716 | -9.251 | -13.567 | Primary | 1984
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NPg Best View | 12.016 | 11.956 | 11.814 | 11.629 | 11.518 | 11.395 | 11.233 | 10.496 | 8.422 | 6.809 | 5.341 | Primary | 1985
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NPg Best View | 15.992 | 16.086 | 16.052 | 15.881 | 15.594 | 15.146 | 14.518 | 10.323 | 6.76 | 5.376 | 4.616 | Primary | 1986
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NPg Best View | 8.829 | 8.518 | 7.983 | 7.322 | 7.004 | 6.649 | 6.199 | 3.961 | -1.595 | -5.741 | -9.761 | Primary | 1987
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NPg Best View | 4.266 | 4.222 | 4.152 | 4.066 | 4.009 | 3.948 | 3.873 | 3.504 | 2.805 | 2.26 | 1.733 | Primary | 1988
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NPg Best View | 8.904 | 8.586 | 8.109 | 7.601 | 7.346 | 7.072 | 6.735 | 5.216 | 1.202 | -1.813 | -4.677 | Primary | 1989
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 14.497 | 14.386 | 14.136 | 13.832 | 13.577 | 13.302 | 12.988 | 11.475 | 7.846 | 4.945 | 2.134 | Primary | 1990
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 13.511 | 13.45 | 13.271 | 13.017 | 12.813 | 12.58 | 12.303 | 10.801 | 6.354 | 2.693 | -0.849 | Primary | 1991
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NPg Best View | 12.335 | 12.372 | 12.353 | 12.306 | 12.261 | 12.202 | 12.122 | 11.667 | 10.157 | 9.113 | 8.192 | Primary | 1992
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NPg Best View | 8.151 | 8.216 | 8.219 | 8.193 | 8.218 | 8.238 | 8.246 | 8.282 | 6.991 | 5.923 | 4.862 | Primary | 1993
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NPg Best View | 17.531 | 17.422 | 17.241 | 17.022 | 16.891 | 16.75 | 16.58 | 15.8 | 14.345 | 13.329 | 12.346 | Primary | 1994
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NPg Best View | 5.028 | 5.079 | 5.102 | 5.1 | 5.077 | 5.029 | 4.947 | 4.377 | 3.541 | 2.871 | 2.254 | Primary | 1995
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NPg Best View | 2.361 | 1.985 | 1.46 | 0.925 | 0.633 | 0.323 | -0.057 | -1.813 | -6.249 | -9.614 | -12.806 | Primary | 1996
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NPg Best View | 11.603 | 11.292 | 10.856 | 10.401 | 10.106 | 9.796 | 9.425 | 7.758 | 3.791 | 0.757 | -2.044 | Primary | 1997
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NPg Best View | 10.179 | 9.775 | 9.17 | 8.493 | 8.093 | 7.637 | 7.069 | 4.17 | -1.108 | -4.729 | -8.074 | Primary | 1998
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 13.007 | 13.038 | 13.005 | 12.935 | 12.83 | 12.686 | 12.497 | 11.34 | 9.885 | 9.125 | 8.556 | Primary | 1999
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NPg Best View | 16.101 | 15.934 | 15.662 | 15.324 | 15.16 | 14.983 | 14.76 | 13.683 | 11.233 | 9.409 | 7.654 | Primary | 2000
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NPg Best View | 12.887 | 12.823 | 12.664 | 12.451 | 12.274 | 12.085 | 11.851 | 10.74 | 7.774 | 5.465 | 3.423 | Primary | 2001
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NPg Best View | 9.461 | 9.265 | 8.915 | 8.475 | 8.199 | 7.88 | 7.477 | 5.391 | 1.604 | -1.002 | -3.429 | Primary | 2002
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NPg Best View | 11.594 | 9.932 | 9.745 | 9.49 | 9.361 | 9.22 | 9.035 | 8.277 | 5.788 | 3.803 | 1.891 | Primary | 2003
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NPg Best View | 4.156 | 4.06 | 3.923 | 3.77 | 3.649 | 3.52 | 3.367 | 2.652 | 1.434 | 0.52 | -0.326 | Primary | 2004
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NPg Best View | 14.043 | 13.68 | 13.152 | 12.536 | 12.162 | 11.763 | 11.275 | 8.895 | 4.524 | 1.259 | -1.884 | Primary | 2005
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NPg Best View | 2.27 | 2.016 | 1.551 | 0.977 | 0.581 | 0.16 | -0.362 | -2.706 | -8.699 | -13.378 | -17.644 | Primary | 2006
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NPg Best View | 14.688 | 14.476 | 14.148 | 13.769 | 13.546 | 13.302 | 12.995 | 11.518 | 8.651 | 6.555 | 4.552 | Primary | 2007
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NPg Best View | 7.748 | 7.4 | 6.86 | 6.238 | 5.895 | 5.531 | 5.086 | 3.023 | -2.082 | -5.987 | -9.808 | Primary | 2008
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NPg Best View | 18.662 | 18.767 | 18.763 | 18.693 | 18.649 | 18.581 | 18.473 | 17.79 | 14.229 | 11.399 | 8.778 | Primary | 2009
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NPg Best View | 12.561 | 12.441 | 12.237 | 12.017 | 11.807 | 11.588 | 11.337 | 10.249 | 8.441 | 7.221 | 6.182 | Primary | 2010
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NPg Best View | 3.384 | 3.108 | 2.662 | 2.127 | 1.743 | 1.332 | 0.844 | -1.549 | -6.035 | -9.439 | -12.704 | Primary | 2011
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NPg Best View | 3.652 | 2.939 | 1.997 | 0.914 | -0.145 | -1.271 | -2.601 | -8.778 | -17.369 | -23.847 | -29.417 | Primary | 2012
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NPg Best View | 4.073 | 3.761 | 3.284 | 2.766 | 2.391 | 1.985 | 1.484 | 16.403 | 11.329 | 7.28 | 3.577 | Primary | 2013
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NPg Best View | 12.57 | 12.135 | 11.523 | 10.825 | 10.399 | 9.961 | 9.454 | 7.211 | 2.835 | -0.533 | -3.874 | Primary | 2014
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NPg Best View | 21.759 | 18.829 | 18.964 | 19.072 | 19.168 | 19.256 | 19.332 | 19.528 | 19.328 | 19.169 | 19.028 | Primary | 2015
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NPg Best View | 3.504 | 3.246 | 2.83 | 2.284 | 1.759 | 1.098 | 0.286 | -3.86 | -8.284 | -11.087 | -13.591 | Primary | 2016
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NPg Best View | 12.647 | 12.556 | 12.36 | 12.112 | 12.055 | 11.99 | 11.902 | 11.383 | 8.222 | 5.627 | 3.001 | Primary | 2017
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NPg Best View | 14.076 | 14.17 | 14.236 | 14.287 | 14.356 | 14.418 | 14.467 | 14.657 | 14.383 | 14.172 | 13.944 | Primary | 2018
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NPg Best View | 15.027 | 15.097 | 15.133 | 15.145 | 15.175 | 15.199 | 15.209 | 15.223 | 14.449 | 13.836 | 13.25 | Primary | 2019
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NPg Best View | 9.748 | 9.274 | 8.572 | 7.742 | 7.228 | 6.685 | 6.04 | 3.123 | -2.125 | -6.004 | -9.754 | Primary | 2020
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NPg Best View | 15.812 | 15.743 | 15.616 | 15.451 | 15.367 | 15.272 | 15.16 | 14.506 | 12.157 | 10.198 | 8.265 | Primary | 2021
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NPg Best View | 5.532 | 5.491 | 5.343 | 5.141 | 5.046 | 4.944 | 4.82 | 4.179 | 0.723 | -2.041 | -4.699 | Primary | 2022
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NPg Best View | 14.057 | 13.924 | 13.692 | 13.403 | 13.206 | 12.993 | 12.73 | 11.464 | 8.952 | 7.156 | 5.5 | Primary | 2023
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NPg Best View | 18.317 | 14.876 | 14.826 | 14.767 | 14.72 | 14.664 | 14.583 | 14.331 | 14.007 | 13.823 | 13.666 | Primary | 2024
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NPg Best View | 11.616 | 11.422 | 11.14 | 10.82 | 10.623 | 10.409 | 10.153 | 8.915 | 6.667 | 5.003 | 3.366 | Primary | 2025
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NPg Best View | 2.533 | 2.345 | 2.065 | 1.722 | 1.461 | 1.158 | 0.795 | -1.162 | -3.74 | -5.403 | -6.908 | Primary | 2026
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NPg Best View | 11.017 | 10.723 | 10.295 | 9.821 | 9.587 | 9.334 | 9.019 | 7.595 | 4.657 | 2.505 | 0.318 | Primary | 2027
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NPg Best View | 10.106 | 9.86 | 9.435 | 8.921 | 8.639 | 8.333 | 7.955 | 7.305 | 3.724 | 1.079 | -1.471 | Primary | 2028
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NPg Best View | 5.802 | 5.637 | 5.332 | 4.901 | 4.461 | 3.92 | 3.258 | -0.164 | -5.176 | -8.83 | -12.093 | Primary | 2029
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NPg Best View | 16.399 | 16.28 | 16.107 | 15.898 | 15.731 | 15.553 | 15.344 | 14.318 | 12.46 | 10.986 | 9.61 | Primary | 2030
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NPg Best View | 8.859 | 7.073 | 6.586 | 5.967 | 5.476 | 4.904 | 4.23 | 7.613 | 1.193 | -3.598 | -8 | Primary | 2031
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NPg Best View | 3.826 | 3.701 | 3.525 | 3.321 | 3.167 | 3.009 | 2.824 | 1.957 | 0.572 | -0.485 | -1.493 | Primary | 2032
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NPg Best View | 14.427 | 14.176 | 13.783 | 13.307 | 13.012 | 12.696 | 12.313 | 10.582 | 7.551 | 5.43 | 3.453 | Primary | 2033
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NPg Best View | -0.265 | -0.446 | -0.719 | -0.048 | -0.316 | -0.607 | -0.956 | -2.556 | -5.353 | -7.493 | -9.462 | Primary | 2034
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NPg Best View | 9.278 | 9.01 | 8.597 | 8.1 | 7.75 | 7.374 | 6.925 | 4.791 | 0.28 | -3.263 | -6.655 | Primary | 2035
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NPg Best View | 7.81 | 7.571 | 7.157 | 6.642 | 6.339 | 6.007 | 5.592 | 3.534 | -0.961 | -4.272 | -7.419 | Primary | 2036
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NPg Best View | 5.106 | 4.716 | 4.125 | 3.407 | 2.927 | 2.416 | 1.808 | -1.054 | -7.306 | -12.268 | -17.127 | Primary | 2037
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NPg Best View | 16.155 | 15.9 | 15.482 | 14.971 | 14.634 | 14.266 | 13.814 | 11.691 | 8.075 | 5.553 | 3.184 | Primary | 2038
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NPg Best View | 7.914 | 7.994 | 7.994 | 7.947 | 7.925 | 7.88 | 7.802 | 7.332 | 5.542 | 4.276 | 3.127 | Primary | 2039
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NPg Best View | 13.903 | 14.676 | 14.358 | 6.006 | 5.409 | 4.789 | 4.061 | 1.665 | -2.303 | -5.581 | -8.553 | Primary | 2040
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NPg Best View | 11.033 | 10.668 | 10.139 | 9.505 | 9.023 | 8.512 | 7.909 | 5.04 | 0.296 | -3.215 | -6.448 | Primary | 2041
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NPg Best View | 6.666 | 6.728 | 6.692 | 6.59 | 6.571 | 6.532 | 6.459 | 6.09 | 4.26 | 2.832 | 1.466 | Primary | 2042
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NPg Best View | 11.847 | 11.504 | 10.989 | 10.386 | 10.035 | 9.668 | 9.226 | 7.219 | 3.014 | -0.133 | -3.157 | Primary | 2043
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NPg Best View | 5.162 | 4.714 | 4.059 | 3.272 | 2.59 | 1.842 | 0.967 | -3.602 | -10.566 | -15.848 | -20.881 | Primary | 2044
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NPg Best View | 10.404 | 10.528 | 10.64 | 10.737 | 10.826 | 10.906 | 10.975 | 11.263 | 11.162 | 11.088 | 11.026 | Primary | 2045
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NPg Best View | 11.353 | 11.491 | 11.594 | 11.658 | 11.686 | 11.676 | 11.62 | 11.07 | 10.329 | 10.044 | 9.889 | Primary | 2046
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NPg Best View | 2.555 | 2.67 | 2.769 | 2.852 | 2.929 | 2.994 | 3.045 | 3.224 | 3.008 | 2.876 | 2.766 | Primary | 2047
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NPg Best View | 6.47 | 6.323 | 6.079 | 5.805 | 5.658 | 5.492 | 5.277 | 4.414 | 2.554 | 1.234 | 0.033 | Primary | 2048
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NPg Best View | 0.668 | 0.514 | 0.309 | 0.077 | -0.114 | -0.321 | -0.57 | -1.827 | -3.664 | -5.012 | -6.221 | Primary | 2049
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NPg Best View | 12.523 | 12.312 | 11.98 | 11.57 | 11.256 | 10.911 | 10.501 | 8.439 | 5.014 | 2.668 | 0.634 | Primary | 2050
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NPg Best View | 12.974 | 11.133 | 11.185 | 11.166 | 11.115 | 11.02 | 10.865 | 10.212 | 8.792 | 7.77 | 6.895 | Primary | 2051
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NPg Best View | 9.33 | 9.053 | 15.652 | 15.243 | 14.976 | 14.692 | 14.341 | 12.728 | 9.232 | 6.598 | 4.134 | Primary | 2052
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NPg Best View | 9.994 | 9.815 | 9.518 | 9.159 | 8.86 | 8.525 | 8.124 | 6.349 | 2.912 | 0.227 | -2.345 | Primary | 2053
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NPg Best View | 3.458 | 1.888 | 1.461 | 1.116 | 0.878 | 0.615 | 0.28 | -1.279 | -5.8 | -9.409 | -12.742 | Primary | 2054
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NPg Best View | 12.63 | 12.637 | 12.612 | 12.566 | 12.555 | 12.536 | 12.504 | 12.293 | 11.232 | 10.301 | 9.366 | Primary | 2055
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NPg Best View | 8.48 | 8.376 | 15.134 | 14.812 | 14.669 | 14.504 | 14.286 | 13.167 | 9.748 | 7.194 | 4.741 | Primary | 2056
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NPg Best View | 5.205 | 4.065 | 3.473 | 2.969 | 2.57 | 2.121 | 1.57 | -1.012 | -5.458 | -8.749 | -11.79 | Primary | 2057
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NPg Best View | 10.273 | 9.885 | 9.281 | 8.568 | 8.202 | 7.82 | 7.362 | 5.299 | 0.282 | -3.532 | -7.298 | Primary | 2058
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NPg Best View | 10.303 | 10.143 | 7.707 | 7.242 | 6.763 | 6.134 | 5.34 | 0.881 | -3.274 | -5.551 | -7.405 | Primary | 2059
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NPg Best View | 8.396 | 8.008 | 7.429 | 6.763 | 6.308 | 5.821 | 5.243 | 2.525 | -1.745 | -4.798 | -7.737 | Primary | 2060
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NPg Best View | 6.953 | 5.02 | 4.446 | 3.798 | 3.428 | 3.021 | 2.515 | 0.463 | -4.106 | -7.578 | -10.883 | Primary | 2061
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NPg Best View | 8.613 | 8.01 | 8.109 | 8.139 | 8.126 | 8.063 | 7.943 | 7.114 | 5.33 | 4.233 | 3.36 | Primary | 2062
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NPg Best View | 18.761 | 18.735 | 18.655 | 18.519 | 18.343 | 18.105 | 17.802 | 15.971 | 14.145 | 13.247 | 12.613 | Primary | 2063
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NPg Best View | 8.731 | 8.668 | 8.492 | 8.253 | 8.153 | 8.04 | 7.882 | 7.152 | 4.542 | 2.494 | 0.479 | Primary | 2064
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NPg Best View | 10.77 | 10.648 | 10.44 | 10.182 | 9.919 | 9.631 | 9.282 | 7.545 | 4.479 | 2.187 | 0.243 | Primary | 2065
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NPg Best View | 12.096 | 11.876 | 11.505 | 11.038 | 10.797 | 10.544 | 10.237 | 8.841 | 4.862 | 1.796 | -1.144 | Primary | 2066
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NPg Best View | 12.337 | 12.349 | 12.294 | 12.201 | 12.165 | 12.111 | 12.029 | 11.567 | 9.982 | 8.852 | 7.767 | Primary | 2067
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NPg Best View | 8.47 | 8.649 | 8.805 | 8.95 | 9.083 | 9.2 | 9.296 | 9.668 | 9.357 | 9.126 | 8.917 | Primary | 2068
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NPg Best View | 8.11 | 6.323 | 6.138 | 5.905 | 5.809 | 5.686 | 5.523 | 4.626 | 1.655 | -0.567 | -2.732 | Primary | 2069
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NPg Best View | 9.991 | 8.859 | 8.959 | 9.036 | 9.094 | 9.144 | 9.179 | 9.336 | 8.58 | 8.003 | 7.477 | Primary | 2070
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NPg Best View | 1.246 | 1.074 | 0.828 | 0.538 | 0.334 | 0.118 | -0.137 | -1.367 | -3.662 | -5.478 | -7.249 | Primary | 2071
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 2.886 | 2.862 | 2.806 | 2.741 | 2.731 | 2.719 | 2.698 | 2.591 | 1.703 | 0.984 | 0.228 | Primary | 2072
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NPg Best View | 12.887 | 12.805 | 12.63 | 12.408 | 12.174 | 11.894 | 11.56 | 9.667 | 7.283 | 5.821 | 4.548 | Primary | 2073
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NPg Best View | 24.544 | 24.636 | 24.712 | 24.764 | 24.803 | 24.832 | 24.848 | 24.867 | 24.25 | 23.68 | 23.127 | Primary | 2074
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NPg Best View | 13.857 | 13.926 | 13.952 | 13.953 | 13.981 | 14.001 | 14.006 | 14.016 | 13.103 | 12.356 | 11.64 | Primary | 2075
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NPg Best View | -1.639 | -1.676 | -1.78 | -1.938 | -2.073 | -2.236 | -2.445 | -3.597 | -5.86 | -7.69 | -9.422 | Primary | 2076
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NPg Best View | 3.308 | 3.084 | 2.715 | 2.204 | 1.718 | 1.115 | 0.375 | -3.921 | -10.074 | -14.337 | -18.221 | Primary | 2077
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NPg Best View | 11.046 | 10.916 | 10.659 | 10.331 | 10.154 | 9.965 | 9.725 | 8.651 | 5.671 | 3.405 | 1.242 | Primary | 2078
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NPg Best View | 11.415 | 11.562 | 11.683 | 11.778 | 11.849 | 11.891 | 11.901 | 11.764 | 11.565 | 11.585 | 11.657 | Primary | 2079
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NPg Best View | 8.208 | 7.879 | 7.35 | 6.696 | 6.262 | 5.776 | 5.183 | 2.229 | -3.515 | -7.772 | -11.736 | Primary | 2080
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NPg Best View | 11.782 | 11.074 | 10.866 | 10.617 | 10.441 | 10.265 | 10.077 | 9.421 | 6.875 | 4.643 | 2.46 | Primary | 2081
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NPg Best View | 4.193 | 3.945 | 3.611 | 3.277 | 3.039 | 2.789 | 2.484 | 1.157 | -1.941 | -4.38 | -6.581 | Primary | 2082
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NPg Best View | 11.04 | 10.908 | 10.641 | 10.29 | 10.056 | 9.809 | 9.505 | 8.076 | 4.183 | 1.068 | -1.848 | Primary | 2083
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NPg Best View | -1.19 | -1.348 | -1.593 | -1.883 | -0.058 | -0.242 | -0.464 | -1.504 | -4.402 | -6.699 | -8.886 | Primary | 2084
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NPg Best View | 15.308 | 15.271 | 15.182 | 15.043 | 14.886 | 14.693 | 14.457 | 13.09 | 10.661 | 8.915 | 7.363 | Primary | 2085
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NPg Best View | 14.67 | 14.155 | 13.595 | 13.218 | 12.918 | 12.588 | 12.187 | 10.235 | 6.58 | 3.891 | 1.499 | Primary | 2086
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NPg Best View | 10.143 | 9.828 | 9.316 | 8.702 | 8.374 | 8.021 | 7.591 | 5.605 | 1.674 | -1.156 | -3.995 | Primary | 2087
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NPg Best View | 23.807 | 23.877 | 23.937 | 23.992 | 24.044 | 24.09 | 24.127 | 24.268 | 24.075 | 23.921 | 23.78 | Primary | 2088
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NPg Best View | 8.596 | 8.686 | 8.758 | 8.811 | 8.853 | 8.888 | 8.91 | 8.969 | 8.06 | 7.33 | 6.681 | Primary | 2089
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NPg Best View | 11.317 | 11.066 | 10.649 | 10.144 | 9.877 | 9.598 | 9.26 | 7.774 | 4.296 | 1.666 | -0.957 | Primary | 2090
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NPg Best View | 4.365 | 4.349 | 4.308 | 4.251 | 4.207 | 4.157 | 4.091 | 3.892 | 3.498 | 3.143 | 2.784 | Primary | 2091
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NPg Best View | 8.868 | 8.793 | 8.653 | 8.483 | 8.348 | 8.202 | 8.036 | 7.197 | 5.087 | 3.337 | 1.613 | Primary | 2092
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NPg Best View | 13.917 | 13.697 | 13.34 | 12.915 | 12.682 | 12.435 | 12.131 | 10.714 | 7.117 | 4.281 | 1.509 | Primary | 2093
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NPg Best View | 10.822 | 10.566 | 10.182 | 9.716 | 9.398 | 9.057 | 8.657 | 6.906 | 3.559 | 1.024 | -1.348 | Primary | 2094
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NPg Best View | 7.861 | 7.54 | 7.07 | 6.507 | 6.012 | 5.486 | 4.868 | 2.031 | -2.183 | -5.28 | -8.046 | Primary | 2095
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NPg Best View | 13.124 | 12.926 | 12.645 | 12.306 | 11.967 | 11.583 | 11.142 | 8.819 | 5.13 | 2.199 | -0.551 | Primary | 2096
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NPg Best View | 7.762 | 7.77 | 7.665 | 7.495 | 7.336 | 7.137 | 6.879 | 5.358 | 1.471 | -1.401 | -3.957 | Primary | 2097
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NPg Best View | 13.814 | 13.601 | 13.254 | 12.839 | 12.624 | 12.397 | 12.12 | 10.867 | 7.869 | 5.6 | 3.336 | Primary | 2098
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NPg Best View | 7.352 | 7.018 | 6.54 | 6.045 | 5.725 | 5.383 | 4.963 | 20.101 | 15.402 | 11.713 | 8.276 | Primary | 2099
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NPg Best View | 7.521 | 7.403 | 7.2 | 6.934 | 6.726 | 6.49 | 6.213 | 4.69 | 0.999 | -2.013 | -4.971 | Primary | 2100
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2101
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Falling Short | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2102
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2103
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - System Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2104
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NPg Best View | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2105
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 33.647 | 31.045 | 29.529 | 27.748 | 26.504 | 25.427 | 24.121 | 18.015 | 2.695 | -8.977 | -20.499 | BSP | 2106
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Consumer Transformation | 43.555 | 43.516 | 42.138 | 42.054 | 42.171 | 42.343 | 42.412 | 42.329 | 35.987 | 31.108 | 26.224 | BSP | 2107
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Consumer Transformation | 53.972 | 52.03 | 50.669 | 49.167 | 48.14 | 47.264 | 46.204 | 41.471 | 25.47 | 12.281 | -0.56 | BSP | 2108
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Consumer Transformation | 32.971 | 30.953 | 28.444 | 25.703 | 23.521 | 21.503 | 19.093 | 7.57 | -18.684 | -39.682 | -59.925 | BSP | 2109
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Consumer Transformation | 22.994 | 20.869 | 18.903 | 16.82 | 15.236 | 13.814 | 12.07 | 4.258 | -13.377 | -27.302 | -40.976 | BSP | 2110
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Consumer Transformation | 14.598 | 13.746 | 12.52 | 11.379 | 10.443 | 9.564 | 8.429 | 3.34 | -5.297 | -11.198 | -16.62 | BSP | 2111
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 31.433 | 30.743 | 30.023 | 29.204 | 28.599 | 28.025 | 27.274 | 23.399 | 12.22 | 3.706 | -4.002 | BSP | 2112
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Consumer Transformation | 40.427 | 38.979 | 37.662 | 36.137 | 35.032 | 34.039 | 26.962 | -11.591 | -24.482 | -33.625 | -42.26 | BSP | 2113
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 98.985 | 97.128 | 96.259 | 95.134 | 94.465 | 93.885 | 93.037 | 88.222 | 67.363 | 50.633 | 34.901 | BSP | 2114
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Consumer Transformation | 28.109 | 27.369 | 26.688 | 25.898 | 25.218 | 24.547 | 23.721 | 19.701 | 8.825 | -0.136 | -8.395 | BSP | 2115
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Consumer Transformation | 40.937 | 39.354 | 38.025 | 36.556 | 35.571 | 34.753 | 33.697 | 28.777 | 15.281 | 4.91 | -5.464 | BSP | 2116
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Consumer Transformation | 68.844 | 66.968 | 65.495 | 62.312 | 61.18 | 60.171 | 58.914 | 53.627 | 43.54 | 35.972 | 28.476 | BSP | 2117
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 19.114 | 17.875 | 17.504 | 17.07 | 16.721 | 16.38 | 15.964 | 13.685 | 8.048 | 3.431 | -0.948 | BSP | 2118
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Consumer Transformation | 44.629 | 42.651 | 41.028 | 39.163 | 37.51 | 35.878 | 33.968 | 23.939 | 4.227 | -11.282 | -25.658 | BSP | 2119
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Consumer Transformation | 14.478 | 9.945 | 7.451 | 4.971 | 2.735 | 0.542 | -2.219 | -13.659 | -30.547 | -42.511 | -53.286 | BSP | 2120
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Consumer Transformation | 16.552 | 14.542 | 13.136 | 11.585 | 10.335 | 9.189 | 7.758 | 1.059 | -15.661 | -28.652 | -41.003 | BSP | 2121
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 60.837 | 55.415 | 52.704 | 49.835 | 47.674 | 45.783 | 43.376 | 32.654 | 6.43 | -13.469 | -32.812 | BSP | 2122
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 26.301 | 24.721 | 23.009 | 20.907 | 19.313 | 17.8 | 15.944 | 5.945 | -17.775 | -35.959 | -53.001 | BSP | 2123
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.046 | 19.574 | 17.96 | 16.179 | 14.929 | 13.872 | 12.583 | 6.824 | -9.141 | -21.758 | -34.468 | BSP | 2124
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Consumer Transformation | 34.881 | 34.117 | 33.917 | 33.484 | 33.122 | 32.681 | 31.488 | 25.2 | 16.53 | 11.437 | 7.7 | BSP | 2125
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 28.81 | 27.634 | 26.249 | 24.583 | 23.214 | 21.904 | 20.214 | 12.343 | -7.974 | -23.852 | -38.602 | BSP | 2126
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Consumer Transformation | 64.307 | 64.211 | 64.181 | 64.141 | 64.094 | 64.04 | 63.979 | 63.688 | 63.303 | 62.881 | 62.453 | BSP | 2127
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | 2.509 | 2.493 | 2.467 | 2.44 | 2.416 | 2.393 | 2.361 | 2.212 | 1.924 | 1.719 | 1.529 | BSP | 2128
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Consumer Transformation | 92.554 | 78.138 | 59.726 | 51.737 | 45.346 | 39.467 | 32.331 | 1.953 | -44.476 | -76.771 | -107.202 | BSP | 2129
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 56.419 | 55.658 | 54.755 | 53.618 | 52.977 | 52.476 | 51.855 | 47.974 | 31.684 | 18.339 | 5.196 | BSP | 2130
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 28.175 | 26.933 | 26.468 | 25.86 | 25.437 | 25.044 | 24.513 | 20.788 | 11.098 | 4.127 | -2.201 | BSP | 2131
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 33.604 | 31.447 | 30.79 | 29.975 | 28.964 | 27.825 | 26.69 | 21.58 | 17.396 | 14.162 | 11.899 | BSP | 2132
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Falling Short | 43.56 | 43.528 | 42.148 | 42.055 | 42.173 | 42.339 | 42.415 | 41.977 | 40.992 | 40.234 | 39.823 | BSP | 2133
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Falling Short | 53.996 | 52.087 | 50.736 | 49.23 | 48.221 | 47.348 | 46.309 | 42.295 | 40.09 | 38.536 | 37.537 | BSP | 2134
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Falling Short | 33.012 | 31.046 | 28.545 | 25.784 | 23.623 | 21.592 | 19.213 | 8.689 | 0.331 | -6.315 | -11.335 | BSP | 2135
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Falling Short | 23.046 | 20.982 | 19.048 | 16.983 | 15.469 | 14.104 | 12.475 | 6.006 | 1.847 | -1.053 | -3.078 | BSP | 2136
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Falling Short | 14.648 | 13.85 | 12.639 | 11.494 | 10.586 | 9.717 | 8.624 | 4.369 | 1.701 | 0.083 | -0.648 | BSP | 2137
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 31.448 | 30.778 | 30.053 | 29.212 | 28.596 | 27.993 | 27.225 | 23.894 | 21.358 | 19.651 | 18.828 | BSP | 2138
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Falling Short | 40.444 | 39.023 | 37.701 | 36.146 | 35.032 | 33.998 | 26.902 | -11.916 | -16.068 | -19.026 | -20.703 | BSP | 2139
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 99 | 97.165 | 96.285 | 95.125 | 94.433 | 93.802 | 92.918 | 88.672 | 85.243 | 82.832 | 81.653 | BSP | 2140
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Falling Short | 28.117 | 27.391 | 26.706 | 25.897 | 25.209 | 24.512 | 23.668 | 19.957 | 17.002 | 14.697 | 13.07 | BSP | 2141
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Falling Short | 40.968 | 39.423 | 38.107 | 36.637 | 35.681 | 34.877 | 33.868 | 29.654 | 26.878 | 24.956 | 23.781 | BSP | 2142
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Falling Short | 68.904 | 67.092 | 65.647 | 62.481 | 61.408 | 60.447 | 59.285 | 54.836 | 52.052 | 50.181 | 48.874 | BSP | 2143
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 19.115 | 17.877 | 17.498 | 17.048 | 16.685 | 16.323 | 15.89 | 13.381 | 10.727 | 8.342 | 6.341 | BSP | 2144
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Falling Short | 44.623 | 42.645 | 40.983 | 39.042 | 37.308 | 35.55 | 33.509 | 22.866 | 12.002 | 2.529 | -5.068 | BSP | 2145
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Falling Short | 14.562 | 10.132 | 7.687 | 5.232 | 3.113 | 1.018 | -1.537 | -10.754 | -15.698 | -18.412 | -19.595 | BSP | 2146
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Falling Short | 16.586 | 14.618 | 13.224 | 11.667 | 10.445 | 9.31 | 7.93 | 2.011 | -2.392 | -5.556 | -7.643 | BSP | 2147
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 60.915 | 55.585 | 52.906 | 50.042 | 47.957 | 46.119 | 43.85 | 34.799 | 28.987 | 25.105 | 22.865 | BSP | 2148
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 26.285 | 24.696 | 22.923 | 20.712 | 18.997 | 17.304 | 15.257 | 4.894 | -5.393 | -14.017 | -20.247 | BSP | 2149
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 21.085 | 19.66 | 18.067 | 16.293 | 15.082 | 14.05 | 12.819 | 7.411 | 3.157 | -0.248 | -2.987 | BSP | 2150
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Falling Short | 34.842 | 34.035 | 33.751 | 33.188 | 32.655 | 31.988 | 30.53 | 24.082 | 18.819 | 14.827 | 13.174 | BSP | 2151
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 28.846 | 27.72 | 26.361 | 24.71 | 23.415 | 22.171 | 20.62 | 14.437 | 10.516 | 8.121 | 6.897 | BSP | 2152
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Falling Short | 64.307 | 64.211 | 64.181 | 64.141 | 64.094 | 64.04 | 63.979 | 63.301 | 62.333 | 61.302 | 60.242 | BSP | 2153
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | 2.51 | 2.496 | 2.471 | 2.444 | 2.424 | 2.403 | 2.376 | 2.264 | 2.189 | 2.146 | 2.125 | BSP | 2154
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Falling Short | 92.677 | 78.432 | 60.062 | 52.021 | 45.719 | 39.81 | 32.778 | 6.473 | -10.171 | -21.072 | -26.867 | BSP | 2155
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 56.412 | 55.647 | 54.726 | 53.555 | 52.882 | 52.333 | 51.667 | 47.982 | 44.348 | 41.301 | 39.106 | BSP | 2156
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 28.153 | 26.891 | 26.375 | 25.688 | 25.165 | 24.637 | 23.952 | 20.107 | 15.858 | 12.493 | 10.6 | BSP | 2157
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 33.513 | 30.596 | 28.656 | 26.495 | 25.117 | 24.06 | 22.22 | 3.799 | -9.754 | -18.862 | -17.765 | BSP | 2158
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Leading the Way | 43.487 | 43.308 | 41.745 | 41.499 | 41.561 | 41.751 | 41.589 | 34.194 | 28.663 | 24.961 | 27.049 | BSP | 2159
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Leading the Way | 53.871 | 51.664 | 49.915 | 48.021 | 46.839 | 45.967 | 44.131 | 24.341 | 9.824 | -0.674 | 0.949 | BSP | 2160
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Leading the Way | 32.803 | 30.429 | 27.394 | 24.119 | 21.753 | 19.748 | 16.49 | -14.617 | -38.352 | -55.528 | -55.66 | BSP | 2161
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Leading the Way | 22.888 | 20.533 | 18.209 | 15.767 | 14.116 | 12.791 | 10.464 | -11.274 | -27.166 | -38.251 | -37.538 | BSP | 2162
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Leading the Way | 14.567 | 13.616 | 12.208 | 10.882 | 9.902 | 9.05 | 7.671 | -3.478 | -10.936 | -15.314 | -14.196 | BSP | 2163
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 31.391 | 30.582 | 29.668 | 28.646 | 27.966 | 27.374 | 26.174 | 12.944 | 3.293 | -3.096 | -1.533 | BSP | 2164
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Leading the Way | 40.321 | 38.641 | 36.983 | 35.121 | 33.892 | 32.896 | 25.377 | -23.586 | -34.68 | -41.485 | -39.929 | BSP | 2165
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 98.871 | 96.732 | 95.438 | 93.876 | 93.031 | 92.416 | 90.574 | 66.063 | 47.637 | 34.721 | 37.859 | BSP | 2166
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Leading the Way | 28.057 | 27.194 | 26.324 | 25.332 | 24.575 | 23.88 | 22.576 | 9.554 | -0.343 | -7.734 | -7.495 | BSP | 2167
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Leading the Way | 40.82 | 39.008 | 37.336 | 35.523 | 34.435 | 33.671 | 32.117 | 15.664 | 3.757 | -4.127 | -2.611 | BSP | 2168
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Leading the Way | 68.8 | 66.804 | 65.125 | 61.751 | 60.599 | 59.674 | 58.197 | 45.261 | 36.149 | 30.013 | 30.569 | BSP | 2169
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 19.093 | 17.794 | 17.331 | 16.801 | 16.41 | 16.053 | 15.448 | 8.934 | 3.826 | -0.049 | -0.367 | BSP | 2170
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Leading the Way | 44.532 | 42.323 | 40.378 | 38.206 | 36.381 | 34.639 | 32.196 | 9.772 | -7.959 | -21.136 | -23.186 | BSP | 2171
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Leading the Way | 14.485 | 9.843 | 7.103 | 4.379 | 2.164 | 0.092 | -2.984 | -26.466 | -41.591 | -51.233 | -49.89 | BSP | 2172
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Leading the Way | 16.454 | 14.2 | 12.452 | 10.595 | 9.244 | 8.126 | 6.245 | -14.079 | -29.102 | -39.731 | -38.418 | BSP | 2173
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 60.704 | 54.871 | 51.547 | 48.122 | 45.801 | 44.027 | 40.916 | 7.675 | -15.645 | -31.405 | -28.134 | BSP | 2174
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 26.135 | 24.145 | 21.869 | 19.21 | 17.317 | 15.654 | 12.916 | -15.404 | -36.434 | -51.177 | -51.036 | BSP | 2175
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 20.939 | 19.173 | 17.154 | 15.009 | 13.651 | 12.657 | 10.91 | -8.386 | -22.819 | -33.118 | -32.052 | BSP | 2176
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Leading the Way | 34.789 | 33.768 | 33.256 | 32.541 | 31.933 | 31.263 | 29.601 | 17.465 | 10.638 | 7.353 | 8.505 | BSP | 2177
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 28.73 | 27.325 | 25.61 | 23.643 | 22.232 | 21.008 | 18.72 | -6.296 | -24.437 | -37.07 | -34.765 | BSP | 2178
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Leading the Way | 64.307 | 64.21 | 64.178 | 64.138 | 64.091 | 64.037 | 63.976 | 63.579 | 63.195 | 62.774 | 62.427 | BSP | 2179
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | 2.508 | 2.49 | 2.46 | 2.43 | 2.408 | 2.388 | 2.356 | 1.973 | 1.718 | 1.553 | 1.6 | BSP | 2180
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Leading the Way | 92.192 | 77.05 | 57.462 | 48.256 | 41.499 | 35.724 | 27.059 | -34.869 | -75.376 | -99.641 | -97.405 | BSP | 2181
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 56.263 | 55.22 | 53.927 | 52.401 | 51.594 | 51.076 | 49.759 | 31.395 | 16.948 | 6.538 | 7.675 | BSP | 2182
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 28.074 | 26.661 | 25.95 | 25.09 | 24.503 | 24.003 | 23.048 | 11.851 | 3.49 | -1.902 | -1.502 | BSP | 2183
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 33.353 | 30.998 | 30.036 | 29.009 | 27.874 | 26.638 | 25.196 | 17.605 | 6.922 | -5.711 | -23.569 | BSP | 2184
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - System Transformation | 43.181 | 43.137 | 41.869 | 41.976 | 41.998 | 41.945 | 41.759 | 40.153 | 34.4 | 28.315 | 20.065 | BSP | 2185
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - System Transformation | 53.722 | 51.915 | 50.956 | 49.999 | 48.954 | 47.84 | 46.678 | 40.496 | 30.781 | 17.784 | -2.28 | BSP | 2186
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - System Transformation | 32.495 | 30.632 | 28.65 | 26.641 | 24.461 | 22.15 | 19.656 | 6.374 | -13.308 | -35.06 | -64.938 | BSP | 2187
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - System Transformation | 22.763 | 20.903 | 19.52 | 18.173 | 16.718 | 15.188 | 13.519 | 4.977 | -7.689 | -21.738 | -42.129 | BSP | 2188
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - System Transformation | 14.348 | 13.558 | 12.588 | 11.766 | 10.85 | 9.863 | 8.771 | 3.26 | -3.211 | -9.692 | -18.525 | BSP | 2189
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 31.204 | 30.546 | 30.008 | 29.462 | 28.828 | 28.125 | 27.34 | 22.676 | 14.295 | 5.723 | -6.145 | BSP | 2190
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - System Transformation | 40.1 | 38.851 | 37.992 | 37.059 | 35.987 | 34.799 | 27.667 | -11.772 | -21.691 | -31.974 | -45.729 | BSP | 2191
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 98.492 | 96.658 | 96.098 | 95.467 | 94.673 | 93.745 | 92.664 | 85.524 | 70.428 | 53.511 | 28.731 | BSP | 2192
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - System Transformation | 27.866 | 27.057 | 26.404 | 25.707 | 24.93 | 24.094 | 23.199 | 18.192 | 9.824 | 0.888 | -11.686 | BSP | 2193
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - System Transformation | 40.643 | 39.286 | 38.468 | 37.643 | 36.714 | 35.708 | 34.57 | 28.49 | 18.955 | 7.816 | -8.546 | BSP | 2194
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - System Transformation | 68.634 | 66.924 | 65.841 | 63.125 | 62.097 | 61.018 | 59.816 | 54.208 | 46.253 | 38.084 | 27.02 | BSP | 2195
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 18.885 | 17.582 | 17.204 | 16.801 | 16.347 | 15.852 | 15.304 | 12.109 | 6.846 | 1.492 | -5.219 | BSP | 2196
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - System Transformation | 43.942 | 41.819 | 40.224 | 38.513 | 36.625 | 34.584 | 32.31 | 19.769 | 1.302 | -16.744 | -38.002 | BSP | 2197
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - System Transformation | 14.21 | 9.747 | 7.639 | 5.681 | 3.55 | 1.312 | -1.08 | -12.073 | -25.469 | -37.265 | -52.402 | BSP | 2198
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - System Transformation | 16.173 | 14.251 | 13.153 | 12.038 | 10.793 | 9.453 | 7.963 | 0.126 | -12.657 | -26.161 | -44.218 | BSP | 2199
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 60.263 | 55.216 | 53.355 | 51.57 | 49.573 | 47.409 | 44.969 | 32.761 | 13.556 | -7.352 | -36.007 | BSP | 2200
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 25.662 | 24.136 | 22.771 | 21.223 | 19.44 | 17.432 | 15.122 | 2.091 | -18.049 | -38.661 | -64.738 | BSP | 2201
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 20.631 | 19.377 | 18.281 | 17.19 | 15.984 | 14.69 | 13.222 | 5.808 | -6.304 | -20.286 | -39.504 | BSP | 2202
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - System Transformation | 34.599 | 33.798 | 33.667 | 33.418 | 33.013 | 32.412 | 30.968 | 23.329 | 16.619 | 10.762 | 4.284 | BSP | 2203
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 28.496 | 27.393 | 26.332 | 25.17 | 23.855 | 22.43 | 20.837 | 12.185 | -3.351 | -18.799 | -40.104 | BSP | 2204
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - System Transformation | 64.135 | 63.918 | 63.759 | 63.584 | 63.394 | 63.189 | 62.968 | 62.006 | 60.996 | 59.936 | 58.869 | BSP | 2205
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | 2.502 | 2.487 | 2.468 | 2.45 | 2.428 | 2.405 | 2.376 | 2.226 | 1.959 | 1.743 | 1.495 | BSP | 2206
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - System Transformation | 92.133 | 78.754 | 62.676 | 57.351 | 51.629 | 45.584 | 38.977 | 8.367 | -23.253 | -56.687 | -102.977 | BSP | 2207
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 56.127 | 55.581 | 55.13 | 54.597 | 53.97 | 53.259 | 52.418 | 46.854 | 35.086 | 21.323 | 1.496 | BSP | 2208
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 27.927 | 26.764 | 26.507 | 26.183 | 25.747 | 25.201 | 24.485 | 19.758 | 11.502 | 3.808 | -5.766 | BSP | 2209
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 33.808 | 31.396 | 30.019 | 28.401 | 27.235 | 26.229 | 25.05 | 19.544 | 5.075 | -6.006 | -17.159 | BSP | 2210
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NPg Best View | 43.767 | 43.917 | 42.641 | 42.669 | 42.792 | 42.956 | 43.015 | 42.987 | 36.923 | 32.245 | 27.446 | BSP | 2211
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NPg Best View | 54.115 | 52.368 | 51.1 | 49.726 | 48.683 | 47.799 | 46.788 | 42.524 | 27.057 | 14.247 | 1.667 | BSP | 2212
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NPg Best View | 33.275 | 31.575 | 29.308 | 26.822 | 24.796 | 22.92 | 20.744 | 10.233 | -14.428 | -34.286 | -53.817 | BSP | 2213
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NPg Best View | 23.269 | 21.412 | 19.702 | 17.881 | 16.54 | 15.364 | 13.975 | 7.394 | -9.141 | -22.275 | -35.321 | BSP | 2214
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NPg Best View | 15.105 | 14.633 | 13.792 | 12.962 | 12.359 | 11.775 | 10.972 | 6.874 | -0.844 | -6.13 | -11.152 | BSP | 2215
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 31.605 | 31.079 | 30.472 | 29.764 | 29.207 | 28.666 | 27.977 | 24.41 | 14.016 | 6.052 | -1.37 | BSP | 2216
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NPg Best View | 40.635 | 39.418 | 38.266 | 36.913 | 35.894 | 34.963 | 27.986 | -9.521 | -21.386 | -29.833 | -38.131 | BSP | 2217
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 99.318 | 97.777 | 97.121 | 96.208 | 95.608 | 95.069 | 94.289 | 89.843 | 70.119 | 54.2 | 38.893 | BSP | 2218
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NPg Best View | 28.229 | 27.626 | 27.032 | 26.34 | 25.686 | 25.03 | 24.244 | 20.491 | 10.235 | 1.715 | -6.307 | BSP | 2219
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NPg Best View | 41.162 | 39.807 | 38.636 | 37.34 | 36.438 | 35.701 | 34.785 | 30.477 | 17.688 | 7.808 | -2.259 | BSP | 2220
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NPg Best View | 69.204 | 67.637 | 66.43 | 63.492 | 62.572 | 61.77 | 60.794 | 56.509 | 47.102 | 40.003 | 32.889 | BSP | 2221
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 19.236 | 18.102 | 17.809 | 17.442 | 17.128 | 16.805 | 16.402 | 14.159 | 8.859 | 4.49 | 0.216 | BSP | 2222
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NPg Best View | 44.861 | 43.173 | 41.684 | 40 | 38.281 | 36.561 | 34.598 | 24.678 | 6.427 | -8.052 | -22.028 | BSP | 2223
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NPg Best View | 15.047 | 11.024 | 9.095 | 7.136 | 5.472 | 3.842 | 1.834 | -7.292 | -22.351 | -33.057 | -42.921 | BSP | 2224
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NPg Best View | 16.82 | 15.075 | 13.87 | 12.529 | 11.404 | 10.378 | 9.14 | 3.202 | -12.526 | -24.816 | -36.735 | BSP | 2225
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 61.328 | 56.395 | 54.041 | 51.545 | 49.6 | 47.929 | 45.895 | 36.616 | 11.875 | -6.985 | -25.665 | BSP | 2226
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 26.607 | 25.37 | 23.877 | 21.976 | 20.41 | 18.859 | 16.951 | 6.916 | -14.992 | -31.89 | -48.441 | BSP | 2227
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 21.309 | 20.113 | 18.696 | 17.128 | 15.985 | 15.033 | 13.911 | 8.9 | -6.362 | -18.49 | -30.838 | BSP | 2228
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NPg Best View | 34.968 | 34.291 | 34.075 | 33.595 | 33.054 | 32.376 | 30.895 | 23.783 | 16.429 | 12.266 | 8.696 | BSP | 2229
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 29.061 | 28.161 | 26.998 | 25.594 | 24.419 | 23.316 | 21.959 | 15.223 | -3.995 | -19.08 | -33.314 | BSP | 2230
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NPg Best View | 64.468 | 64.515 | 64.603 | 64.664 | 64.697 | 64.697 | 64.649 | 64.384 | 64.005 | 63.588 | 63.167 | BSP | 2231
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | 2.517 | 2.51 | 2.491 | 2.471 | 2.455 | 2.44 | 2.42 | 2.301 | 2.032 | 1.841 | 1.66 | BSP | 2232
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NPg Best View | 93.668 | 80.276 | 63.158 | 56.378 | 51.415 | 46.848 | 41.334 | 16.118 | -24.356 | -52.617 | -80.174 | BSP | 2233
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 56.405 | 55.719 | 54.749 | 53.609 | 52.767 | 52.08 | 51.311 | 47.226 | 31.336 | 18.259 | 5.106 | BSP | 2234
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 28.241 | 27.081 | 26.601 | 25.973 | 25.405 | 24.839 | 24.119 | 19.896 | 11.109 | 4.779 | -1.423 | BSP | 2235
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Consumer Transformation | 5.471 | 5.1 | 4.494 | 3.787 | 3.339 | 3.001 | 2.587 | 0.798 | -4.782 | -9.102 | -13.631 | Primary | 2236
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Consumer Transformation | 10.897 | 9.841 | 7.554 | 6.297 | 5.327 | 4.489 | 3.48 | -0.468 | -9.822 | -16.849 | -23.739 | Primary | 2237
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 7.99 | 7.608 | 9.021 | 8.35 | 7.871 | 7.448 | 6.929 | 4.556 | -0.761 | -4.82 | -8.872 | Primary | 2238
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Consumer Transformation | 5.747 | 5.464 | 4.971 | 4.387 | 3.992 | 3.663 | 3.25 | 1.455 | -3.989 | -8.302 | -12.626 | Primary | 2239
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Consumer Transformation | 22.754 | 22.794 | 22.832 | 22.867 | 22.9 | 22.931 | 22.96 | 23.013 | 23.016 | 23.019 | 23.021 | Primary | 2240
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Consumer Transformation | 2.057 | 2.011 | 1.896 | 1.748 | 1.67 | 1.61 | 1.52 | 1.012 | -0.99 | -2.525 | -4.039 | Primary | 2241
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Consumer Transformation | 3.658 | 3.615 | 3.561 | 3.507 | 3.454 | 3.399 | 3.331 | 3.026 | 2.67 | 2.4 | 2.157 | Primary | 2242
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Consumer Transformation | 2.638 | 2.457 | 2.196 | 1.887 | 1.633 | 1.394 | 1.112 | -0.428 | -3.716 | -6.27 | -8.712 | Primary | 2243
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Consumer Transformation | 7.233 | 7.105 | 6.877 | 6.604 | 6.439 | 6.317 | 6.157 | 5.337 | 2.11 | -0.474 | -3.114 | Primary | 2244
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Consumer Transformation | 11.891 | 11.577 | 11.082 | 10.562 | 10.15 | 9.765 | 9.273 | 7.06 | 3.292 | 0.72 | -1.64 | Primary | 2245
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Consumer Transformation | 4.763 | 4.128 | 3.6 | 3.031 | 2.585 | 2.174 | 1.679 | -0.587 | -6.946 | -12.135 | -17.078 | Primary | 2246
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Consumer Transformation | 11.045 | 10.48 | 10.144 | 9.742 | 9.487 | 9.27 | 8.99 | 7.557 | 2.612 | -1.363 | -5.24 | Primary | 2247
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Consumer Transformation | 7.479 | 7.076 | 6.528 | 5.932 | 5.493 | 5.085 | 4.6 | 1.969 | -2.969 | -6.531 | -9.846 | Primary | 2248
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Consumer Transformation | 3.537 | 2.84 | 2.374 | 1.851 | 1.499 | 1.185 | 0.793 | -1.106 | -6.212 | -10.226 | -14.086 | Primary | 2249
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 13.303 | 13.131 | 12.845 | 12.511 | 12.224 | 11.92 | 10.929 | 6.975 | 3.569 | 1.487 | -0.101 | Primary | 2250
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 16.526 | 16.54 | 16.505 | 16.4 | 16.306 | 16.208 | 16.088 | 15.407 | 14.229 | 13.656 | 13.236 | Primary | 2251
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Consumer Transformation | 9.535 | 8.62 | 8.44 | 8.213 | 8.028 | 7.835 | 7.58 | 6.125 | 1.803 | -1.538 | -4.463 | Primary | 2252
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Consumer Transformation | 10.192 | 9.549 | 9.142 | 8.685 | 8.316 | 7.969 | 7.549 | 5.537 | 0.191 | -4.155 | -8.19 | Primary | 2253
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Consumer Transformation | 15.555 | 15.307 | 14.939 | 14.539 | 14.239 | 13.971 | 13.64 | 12.212 | 8.409 | 5.357 | 2.482 | Primary | 2254
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Consumer Transformation | 7.136 | 7.014 | 6.817 | 6.557 | 6.308 | 6.024 | 5.661 | 2.952 | -1.503 | -4.163 | -6.058 | Primary | 2255
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Consumer Transformation | 20.245 | 19.936 | 19.517 | 19.061 | 18.653 | 18.248 | 17.763 | 15.123 | 9.763 | 5.654 | 1.919 | Primary | 2256
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 17.765 | 17.609 | 17.393 | 17.152 | 16.943 | 16.738 | 16.496 | 15.287 | 12.39 | 9.93 | 7.596 | Primary | 2257
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Consumer Transformation | 11.79 | 11.006 | 10.241 | 9.368 | 8.742 | 8.192 | 7.53 | 4.563 | -2.304 | -7.632 | -12.905 | Primary | 2258
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Consumer Transformation | 7.86 | 7.329 | 7.199 | 7.045 | 6.954 | 6.891 | 6.801 | 6.386 | 4.343 | 2.739 | 1.132 | Primary | 2259
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Consumer Transformation | 8.8 | 8.411 | 7.76 | 6.994 | 6.461 | 6.019 | 5.458 | 2.575 | -4.111 | -8.837 | -13.524 | Primary | 2260
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Consumer Transformation | 6.911 | 6.236 | 5.596 | 4.962 | 4.446 | 3.988 | 3.426 | 1.073 | -3.179 | -6.28 | -9.313 | Primary | 2261
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Consumer Transformation | 8.077 | 7.791 | 7.347 | 6.836 | 6.459 | 6.135 | 5.73 | 3.818 | -1.028 | -4.68 | -8.214 | Primary | 2262
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Consumer Transformation | 8.044 | 7.815 | 7.445 | 7.011 | 6.637 | 6.281 | 5.838 | 3.855 | -0.841 | -4.629 | -8.18 | Primary | 2263
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Consumer Transformation | 4.028 | 3.75 | 3.268 | 2.685 | 2.269 | 1.892 | 1.418 | -0.824 | -7 | -11.832 | -16.42 | Primary | 2264
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Consumer Transformation | 7.798 | 7.424 | 6.906 | 6.324 | 5.832 | 5.371 | 4.828 | 2.308 | -2.873 | -7.134 | -11.325 | Primary | 2265
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Consumer Transformation | 8.429 | 8.256 | 8.352 | 8.411 | 8.493 | 8.573 | 8.621 | 8.714 | 6.97 | 5.62 | 4.349 | Primary | 2266
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Consumer Transformation | 5.552 | 4.578 | 4.255 | 3.928 | 3.651 | 3.385 | 3.044 | 1.598 | -1.417 | -3.758 | -5.943 | Primary | 2267
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Consumer Transformation | 14.635 | 13.283 | 12.486 | 11.546 | 10.855 | 10.237 | 9.485 | 5.924 | -1.764 | -7.356 | -12.782 | Primary | 2268
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Consumer Transformation | 12.841 | 12.817 | 12.738 | 12.633 | 12.577 | 12.535 | 12.465 | 12.14 | 10.745 | 9.677 | 8.579 | Primary | 2269
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Consumer Transformation | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | Primary | 2270
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 12.647 | 12.647 | 12.599 | 12.516 | 12.474 | 12.44 | 12.383 | 11.968 | 10.087 | 8.67 | 7.35 | Primary | 2271
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 14.683 | 14.628 | 14.513 | 14.351 | 14.251 | 14.162 | 14.039 | 13.109 | 10.488 | 8.651 | 6.988 | Primary | 2272
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Consumer Transformation | 4.492 | 4.442 | 4.366 | 4.283 | 4.243 | 4.222 | 4.194 | 4.04 | 2.994 | 2.114 | 1.171 | Primary | 2273
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Consumer Transformation | 8.957 | 8.793 | 8.553 | 8.298 | 8.128 | 7.983 | 7.807 | 6.995 | 4.759 | 3.028 | 1.334 | Primary | 2274
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Consumer Transformation | 8.337 | 8.113 | 7.745 | 7.329 | 7.02 | 6.734 | 6.37 | 4.677 | -0.335 | -4.301 | -8.02 | Primary | 2275
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 23.137 | 22.857 | 22.819 | 22.772 | 22.744 | 22.72 | 22.674 | 22.471 | 21.215 | 20.178 | 19.235 | Primary | 2276
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Consumer Transformation | 6.812 | 6.71 | 6.502 | 6.255 | 6.077 | 5.898 | 5.65 | 4.116 | 0.089 | -2.711 | -5.094 | Primary | 2277
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Consumer Transformation | 5.103 | 4.268 | 3.587 | 2.796 | 2.19 | 1.635 | 0.941 | -2.443 | -8.899 | -13.252 | -17.199 | Primary | 2278
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Consumer Transformation | 9.92 | 8.617 | 8.143 | 7.585 | 7.169 | 6.789 | 6.308 | 4.073 | -2.321 | -7.27 | -11.942 | Primary | 2279
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 8.63 | 8.48 | 8.226 | 7.957 | 7.707 | 7.448 | 7.102 | 5.548 | 2.384 | -0.03 | -2.147 | Primary | 2280
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 13.377 | 13.085 | 12.632 | 12.153 | 11.784 | 11.443 | 11.013 | 9.08 | 3.412 | -1.229 | -5.603 | Primary | 2281
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Consumer Transformation | 4.249 | 3.778 | 3.642 | 3.478 | 3.358 | 3.255 | 3.118 | 2.5 | 0.132 | -1.826 | -3.79 | Primary | 2282
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Consumer Transformation | 8.073 | 7.729 | 7.153 | 6.461 | 5.899 | 5.37 | 4.708 | 1.455 | -7.317 | -14.175 | -20.49 | Primary | 2283
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Consumer Transformation | 18.02 | 18.009 | 17.971 | 17.917 | 17.888 | 17.864 | 17.828 | 17.625 | 16.421 | 15.383 | 14.375 | Primary | 2284
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Consumer Transformation | 6.605 | 6.408 | 6.086 | 5.746 | 5.496 | 5.279 | 4.982 | 3.64 | 0.693 | -1.484 | -3.666 | Primary | 2285
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Consumer Transformation | 8.999 | 8.991 | 8.953 | 8.898 | 8.848 | 8.791 | 8.707 | 8.138 | 6.975 | 6.179 | 5.506 | Primary | 2286
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Consumer Transformation | 0.513 | 0.324 | -0.043 | -0.512 | -0.815 | -1.054 | -1.368 | 14.324 | 9.273 | 5.231 | 1.154 | Primary | 2287
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Consumer Transformation | 5.325 | 4.563 | 3.588 | 2.75 | 2.037 | 1.347 | 0.498 | -3.284 | -9.528 | -13.974 | -17.935 | Primary | 2288
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Consumer Transformation | 10.145 | 9.66 | 8.209 | 7.401 | 6.827 | 6.346 | 5.769 | 3.089 | -3.343 | -8.174 | -13.047 | Primary | 2289
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Consumer Transformation | 14.374 | 14.051 | 13.997 | 13.913 | 13.831 | 13.736 | 13.602 | 12.772 | 11.055 | 9.859 | 8.869 | Primary | 2290
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Consumer Transformation | 7.312 | 5.852 | 5.44 | 4.93 | 4.579 | 4.276 | 3.873 | 1.879 | -5.52 | -11.307 | -16.817 | Primary | 2291
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Consumer Transformation | 7.275 | 6.821 | 6.129 | 5.359 | 4.778 | 4.256 | 3.607 | 0.617 | -5.801 | -10.686 | -15.447 | Primary | 2292
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Consumer Transformation | 28.91 | 28.36 | 27.595 | 26.877 | 26.284 | 25.722 | 24.997 | 21.812 | 16.989 | 13.658 | 10.484 | Primary | 2293
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Consumer Transformation | 5.173 | 4.908 | 4.485 | 3.989 | 3.639 | 3.341 | 2.974 | 1.238 | -3.439 | -7.119 | -10.778 | Primary | 2294
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Consumer Transformation | 11.695 | 11.453 | 11.085 | 10.686 | 10.442 | 10.258 | 10.03 | 9.09 | 6.234 | 3.998 | 1.617 | Primary | 2295
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Consumer Transformation | 18.285 | 18.181 | 17.979 | 17.726 | 17.537 | 17.363 | 17.138 | 15.987 | 12.29 | 9.366 | 6.637 | Primary | 2296
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Consumer Transformation | 8.639 | 8.646 | 7.15 | 7.035 | 6.979 | 6.933 | 6.849 | 6.26 | 4.198 | 2.759 | 1.443 | Primary | 2297
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Consumer Transformation | 25.865 | 25.918 | 25.947 | 25.944 | 25.918 | 25.864 | 25.775 | 24.897 | 23.336 | 22.524 | 22.104 | Primary | 2298
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Consumer Transformation | 14.564 | 14.089 | 14.055 | 13.995 | 14.012 | 14.06 | 14.086 | 14.162 | 12.994 | 12.065 | 10.982 | Primary | 2299
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Consumer Transformation | 4.881 | 4.662 | 4.273 | 3.794 | 3.254 | 2.626 | 1.815 | -2.942 | -7.848 | -10.152 | -11.206 | Primary | 2300
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Consumer Transformation | 15.814 | 15.946 | 16.059 | 16.154 | 16.249 | 16.341 | 16.422 | 16.75 | 16.52 | 16.308 | 16.069 | Primary | 2301
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 7.483 | 6.947 | 6.436 | 5.86 | 5.39 | 4.949 | 4.411 | 18.049 | 13.445 | 9.978 | 6.687 | Primary | 2302
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary | 2303
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Consumer Transformation | 2.477 | 2.334 | 2.059 | 1.722 | 1.57 | 1.485 | 1.367 | 0.793 | -2.668 | -5.441 | -8.397 | Primary | 2304
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Consumer Transformation | 14.309 | 13.969 | 13.478 | 12.954 | 12.515 | 12.088 | 11.555 | 9.031 | 4.952 | 2.066 | -0.596 | Primary | 2305
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Consumer Transformation | 14.998 | 12.6 | 12.602 | 12.569 | 12.563 | 12.547 | 12.479 | 12.005 | 10.035 | 8.579 | 7.314 | Primary | 2306
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Consumer Transformation | 8.679 | 7.884 | 7.193 | 6.485 | 5.958 | 5.493 | 4.913 | 2.226 | -4.634 | -9.945 | -15.145 | Primary | 2307
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Consumer Transformation | 18.458 | 18.35 | 18.185 | 18.019 | 17.903 | 17.812 | 17.692 | 17.156 | 15.385 | 13.978 | 12.532 | Primary | 2308
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Consumer Transformation | 10.998 | 10.4 | 9.522 | 8.564 | 7.885 | 7.321 | 6.627 | 3.56 | -3.272 | -8.406 | -13.743 | Primary | 2309
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Consumer Transformation | 3.531 | 2.716 | 2.009 | 1.18 | 0.52 | -0.102 | -0.856 | -4.176 | -10.542 | -15.167 | -19.443 | Primary | 2310
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Consumer Transformation | 2.668 | 2.225 | 1.632 | 1.058 | 0.63 | 0.274 | -0.165 | -2.016 | -5.652 | -8.318 | -11.037 | Primary | 2311
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Consumer Transformation | 8.521 | 8.486 | 8.421 | 8.338 | 8.274 | 8.212 | 8.13 | 7.546 | 6.414 | 5.736 | 5.186 | Primary | 2312
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Consumer Transformation | 21.021 | 20.738 | 20.709 | 20.663 | 20.636 | 20.618 | 20.598 | 20.517 | 19.739 | 19.116 | 18.513 | Primary | 2313
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Consumer Transformation | 19.203 | 19.013 | 18.698 | 18.334 | 18.093 | 17.912 | 17.686 | 16.644 | 13.383 | 10.921 | 8.385 | Primary | 2314
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Consumer Transformation | 14.59 | 14.736 | 14.873 | 15.003 | 15.127 | 15.244 | 15.355 | 15.833 | 16.154 | 16.425 | 16.669 | Primary | 2315
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Consumer Transformation | 14.661 | 14.749 | 14.78 | 14.789 | 14.829 | 14.871 | 14.876 | 14.788 | 13.66 | 12.917 | 12.219 | Primary | 2316
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Consumer Transformation | 1.154 | 1.162 | 1.068 | 0.885 | 20.643 | 20.46 | 20.192 | 17.825 | 12.167 | 8.398 | 5.447 | Primary | 2317
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Consumer Transformation | 7.545 | 7.173 | 6.636 | 6.057 | 5.636 | 5.264 | 4.811 | 2.814 | -1.682 | -5.177 | -8.685 | Primary | 2318
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Consumer Transformation | 6.871 | 6.487 | 5.909 | 5.266 | 4.77 | 4.313 | 3.753 | 1.233 | -3.444 | -6.685 | -9.722 | Primary | 2319
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Consumer Transformation | 16.233 | 16.148 | 16.016 | 15.867 | 15.717 | 15.558 | 15.36 | 14.353 | 12.17 | 10.433 | 8.911 | Primary | 2320
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Consumer Transformation | 6.69 | 6.549 | 6.331 | 6.099 | 5.922 | 5.762 | 5.555 | 4.603 | 2.041 | 0.104 | -1.73 | Primary | 2321
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 1.699 | 1.171 | 0.467 | -0.238 | -0.856 | -1.456 | -2.19 | -5.586 | -11.233 | -15.489 | -19.5 | Primary | 2322
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Consumer Transformation | 18.432 | 18.419 | 18.376 | 18.318 | 18.278 | 18.242 | 18.189 | 17.885 | 16.954 | 16.255 | 15.605 | Primary | 2323
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Consumer Transformation | 6.562 | 6.275 | 5.842 | 5.392 | 5.078 | 4.809 | 4.472 | 3.094 | -0.18 | -2.692 | -5.224 | Primary | 2324
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Consumer Transformation | 2.77 | 2.75 | 2.72 | 2.688 | 2.661 | 2.633 | 2.597 | 2.43 | 2.122 | 1.902 | 1.697 | Primary | 2325
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Consumer Transformation | 9.159 | 8.821 | 8.679 | 8.504 | 8.386 | 8.281 | 8.143 | 7.334 | 4.732 | 2.699 | 0.791 | Primary | 2326
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Consumer Transformation | 14.281 | 14.088 | 13.796 | 13.478 | 13.223 | 12.987 | 12.69 | 11.375 | 8.749 | 6.758 | 4.826 | Primary | 2327
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Consumer Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 2328
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Consumer Transformation | 20.801 | 20.625 | 20.371 | 20.108 | 19.912 | 19.741 | 19.528 | 18.542 | 15.863 | 13.798 | 11.795 | Primary | 2329
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Consumer Transformation | 8.324 | 8.013 | 7.542 | 7.037 | 6.734 | 6.511 | 6.231 | 4.986 | 0.949 | -2.199 | -5.509 | Primary | 2330
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Consumer Transformation | 14.262 | 14.01 | 13.63 | 13.207 | 12.925 | 12.689 | 12.402 | 11.033 | 7.524 | 4.873 | 2.233 | Primary | 2331
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Consumer Transformation | 33.156 | 32.766 | 32.717 | 32.661 | 32.626 | 32.603 | 32.568 | 32.444 | 31.815 | 31.329 | 30.841 | Primary | 2332
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Consumer Transformation | 4.362 | 3.511 | 2.763 | 1.94 | 1.329 | 0.819 | 0.193 | -2.398 | -7.704 | -11.558 | -15.518 | Primary | 2333
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Consumer Transformation | 14.566 | 13.816 | 13.479 | 13.069 | 12.727 | 12.397 | 12.019 | 17.899 | 12.844 | 8.804 | 4.92 | Primary | 2334
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Consumer Transformation | 9.527 | 9.421 | 9.227 | 8.994 | 8.772 | 8.543 | 8.25 | 6.663 | 1.804 | -2.105 | -5.592 | Primary | 2335
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Consumer Transformation | 15.39 | 15.342 | 15.257 | 15.152 | 15.085 | 15.03 | 14.957 | 14.515 | 12.928 | 11.67 | 10.441 | Primary | 2336
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 24.317 | 22.474 | 22.034 | 21.567 | 21.198 | 20.853 | 20.428 | 18.737 | 15.668 | 13.345 | 11.136 | Primary | 2337
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Consumer Transformation | 5.261 | 4.737 | 4.34 | 3.893 | 3.531 | 3.186 | 2.784 | 0.876 | -4.044 | -8.169 | -12.113 | Primary | 2338
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Consumer Transformation | 1.467 | 0.641 | -0.014 | -0.695 | -1.201 | -1.634 | -2.163 | -4.507 | -10.654 | -15.663 | -20.716 | Primary | 2339
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Consumer Transformation | 3.134 | 3.089 | 1.702 | 1.613 | 1.532 | 1.45 | 1.344 | 0.874 | 0.348 | 0.019 | -0.252 | Primary | 2340
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Consumer Transformation | 7.505 | 7.011 | 8.618 | 8.21 | 7.889 | 7.581 | 7.177 | 5.269 | -0.008 | -4.144 | -7.994 | Primary | 2341
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Consumer Transformation | 5.647 | 5.497 | 5.193 | 4.795 | 4.629 | 4.54 | 4.409 | 3.652 | -1.45 | -5.65 | -10.048 | Primary | 2342
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Consumer Transformation | 32.128 | 30.756 | 30.683 | 30.589 | 30.504 | 30.411 | 30.293 | 29.65 | 27.639 | 25.957 | 24.455 | Primary | 2343
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Consumer Transformation | 12.227 | 12.097 | 11.869 | 11.599 | 11.386 | 11.183 | 10.928 | 9.759 | 5.825 | 2.553 | -0.483 | Primary | 2344
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Consumer Transformation | 8.787 | 8.017 | 7.644 | 7.313 | 7.057 | 6.822 | 6.53 | 5.452 | 3.089 | 1.259 | -0.47 | Primary | 2345
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Consumer Transformation | 6.53 | 6.602 | 6.629 | 6.627 | 6.676 | 6.736 | 6.779 | 6.87 | 5.823 | 5.011 | 4.161 | Primary | 2346
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Consumer Transformation | 13.507 | 13.466 | 13.363 | 13.216 | 13.089 | 12.961 | 12.793 | 11.96 | 8.933 | 6.482 | 4.267 | Primary | 2347
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 14.687 | 14.664 | 14.58 | 14.43 | 14.244 | 14.001 | 13.676 | 11.242 | 7.393 | 5.084 | 3.503 | Primary | 2348
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 13.001 | 12.855 | 12.631 | 12.353 | 12.183 | 12.041 | 11.874 | 10.965 | 7.531 | 4.543 | 1.467 | Primary | 2349
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Consumer Transformation | 4.613 | 3.544 | 3.161 | 2.708 | 2.357 | 2.033 | 1.663 | -0.126 | -4.339 | -7.791 | -11.184 | Primary | 2350
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Consumer Transformation | 4.811 | 3.088 | 1.704 | 0.158 | -1.059 | -2.124 | -3.366 | -8.523 | -17.237 | -23.692 | -30.197 | Primary | 2351
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Consumer Transformation | 11.531 | 10.579 | 9.982 | 9.448 | 9.027 | 8.66 | 8.21 | 6.35 | 2.812 | 0.198 | -2.432 | Primary | 2352
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Consumer Transformation | 15.797 | 14.947 | 14.462 | 13.912 | 13.517 | 13.163 | 12.722 | 10.797 | 5.805 | 1.916 | -1.801 | Primary | 2353
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Consumer Transformation | 8.13 | 7.953 | 7.625 | 7.227 | 6.923 | 6.643 | 6.279 | 4.639 | 0.287 | -3.138 | -6.352 | Primary | 2354
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Consumer Transformation | 12.772 | 12.811 | 12.845 | 12.874 | 12.899 | 12.921 | 12.936 | 12.984 | 12.909 | 12.834 | 12.756 | Primary | 2355
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Consumer Transformation | 21.706 | 21.634 | 21.494 | 21.312 | 21.192 | 21.09 | 20.964 | 20.399 | 18.824 | 17.606 | 16.372 | Primary | 2356
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Consumer Transformation | 15.073 | 15.223 | 15.351 | 15.459 | 15.57 | 15.676 | 15.767 | 16.139 | 15.542 | 15.063 | 14.606 | Primary | 2357
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 10.706 | 10.289 | 9.692 | 9.039 | 8.557 | 8.136 | 7.634 | 5.396 | 0.323 | -3.571 | -7.442 | Primary | 2358
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.908 | 21.877 | 21.819 | 21.756 | 21.717 | 21.687 | 21.643 | 21.443 | 20.817 | 20.32 | 19.798 | Primary | 2359
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Consumer Transformation | 2.596 | 2.345 | 1.922 | 1.428 | 1.096 | 0.823 | 0.481 | -0.998 | -5.821 | -9.624 | -13.371 | Primary | 2360
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Consumer Transformation | 6.601 | 6.587 | 6.562 | 6.533 | 6.514 | 6.497 | 6.474 | 6.369 | 6.013 | 5.735 | 5.466 | Primary | 2361
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Consumer Transformation | 6.073 | 5.264 | 4.934 | 4.601 | 4.378 | 4.215 | 4.001 | 3.108 | 0.626 | -1.199 | -3.14 | Primary | 2362
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Consumer Transformation | 12.03 | 11.422 | 10.523 | 9.5 | 8.648 | 7.843 | 6.861 | 1.993 | -8.697 | -16.899 | -24.441 | Primary | 2363
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Consumer Transformation | 10.511 | 9.011 | 8.082 | 7.506 | 7.079 | 6.689 | 6.199 | 3.842 | -2.185 | -6.726 | -10.962 | Primary | 2364
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 15.164 | 14.993 | 14.764 | 14.513 | 14.28 | 14.041 | 13.757 | 12.265 | 9.31 | 6.963 | 4.855 | Primary | 2365
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 15.946 | 15.886 | 15.815 | 15.741 | 15.667 | 15.592 | 15.508 | 15.106 | 14.571 | 14.1 | 13.659 | Primary | 2366
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Consumer Transformation | 2.096 | 1.693 | 22.725 | 22.396 | 22.157 | 21.941 | 21.658 | 19.83 | 15.685 | 12.809 | 10.163 | Primary | 2367
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Consumer Transformation | 13.667 | 13.1 | 12.645 | 12.174 | 11.769 | 11.385 | 10.906 | 8.931 | 6.522 | 4.998 | 3.624 | Primary | 2368
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Consumer Transformation | 3.266 | 3.061 | 2.773 | 2.467 | 2.229 | 2.009 | 1.749 | 0.643 | -1.26 | -2.701 | -4.09 | Primary | 2369
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Consumer Transformation | 2.822 | 2.674 | 2.476 | 2.268 | 2.077 | 1.885 | 1.651 | 0.509 | -1.25 | -2.553 | -3.712 | Primary | 2370
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 12.409 | 11.749 | 11.292 | 10.742 | 10.305 | 9.904 | 9.39 | 7.069 | 0.845 | -4.07 | -8.768 | Primary | 2371
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Consumer Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2372
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Consumer Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2373
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Consumer Transformation | 17.645 | 17.109 | 16.868 | 16.589 | 16.402 | 16.241 | 16.036 | 15.125 | 12.015 | 9.521 | 7.107 | Primary | 2374
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Consumer Transformation | 11.195 | 10.122 | 9.998 | 9.85 | 9.7 | 9.536 | 9.328 | 8.288 | 6.569 | 5.277 | 4.17 | Primary | 2375
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Consumer Transformation | 10.469 | 10.215 | 9.829 | 9.418 | 9.137 | 8.902 | 8.602 | 7.148 | 3.622 | 1.043 | -1.526 | Primary | 2376
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Consumer Transformation | 12.97 | 12.668 | 12.265 | 11.869 | 11.53 | 11.205 | 10.801 | 8.915 | 5.706 | 3.31 | 1.052 | Primary | 2377
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Consumer Transformation | 10.511 | 9.719 | 9.487 | 9.201 | 8.975 | 8.761 | 8.498 | 7.262 | 3.944 | 1.241 | -1.311 | Primary | 2378
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Consumer Transformation | 10.341 | 10.176 | 9.892 | 9.556 | 9.348 | 9.182 | 8.964 | 7.823 | 4.303 | 1.604 | -1.063 | Primary | 2379
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Consumer Transformation | 16.844 | 16.063 | 16.023 | 15.945 | 15.913 | 15.895 | 15.84 | 15.476 | 13.314 | 11.604 | 9.943 | Primary | 2380
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Consumer Transformation | 15.768 | 15.422 | 14.9 | 14.328 | 13.899 | 13.497 | 12.991 | 10.337 | 5.018 | 1.255 | -2.208 | Primary | 2381
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | 5.547 | 5.401 | 5.179 | 4.948 | 4.739 | 4.53 | 4.265 | 3.097 | 1.393 | 0.196 | -0.868 | Primary | 2382
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Consumer Transformation | 12.485 | 12.008 | 10.017 | 9.345 | 8.903 | 8.52 | 8.042 | 5.737 | -0.331 | -4.709 | -8.894 | Primary | 2383
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Consumer Transformation | 23.246 | 13.673 | 2.514 | 1.777 | 1.233 | 0.753 | 0.164 | -2.374 | -7.673 | -11.591 | -15.352 | Primary | 2384
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Consumer Transformation | 0.668 | -0.205 | -1.014 | -3.592 | -4.239 | -4.814 | -5.529 | -8.512 | -14.396 | -18.883 | -23.316 | Primary | 2385
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Consumer Transformation | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary | 2386
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Consumer Transformation | 3.276 | 3.121 | 2.906 | 2.653 | 2.463 | 2.285 | 2.074 | 0.858 | -2.278 | -4.788 | -7.173 | Primary | 2387
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Consumer Transformation | 12.067 | 11.223 | 10.818 | 10.3 | 9.924 | 9.592 | 9.201 | 7.395 | 3.19 | 0.116 | -2.874 | Primary | 2388
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 5.89 | 4.219 | 4.017 | 3.734 | 3.585 | 3.473 | 3.307 | 2.444 | -1.05 | -3.684 | -6.236 | Primary | 2389
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 27.96 | 27.983 | 28.006 | 28.028 | 28.048 | 28.068 | 28.087 | 28.168 | 28.233 | 28.287 | 28.335 | Primary | 2390
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Consumer Transformation | 19.994 | 18.92 | 18.48 | 17.981 | 17.621 | 17.307 | 16.926 | 15.299 | 11.499 | 8.511 | 5.533 | Primary | 2391
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Consumer Transformation | 8.44 | 7.869 | 8.045 | 8.147 | 8.209 | 8.207 | 8.117 | 6.835 | 4.227 | 2.97 | 2.371 | Primary | 2392
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Consumer Transformation | 3.183 | 3.098 | 3.079 | 3.053 | 3.023 | 2.988 | 2.949 | 2.723 | 2.369 | 1.981 | 1.588 | Primary | 2393
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Consumer Transformation | 13.824 | 13.446 | 12.892 | 12.306 | 11.913 | 11.594 | 11.206 | 9.458 | 3.941 | -0.584 | -5.156 | Primary | 2394
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Consumer Transformation | 2.336 | 2.007 | 1.549 | 1.051 | 0.592 | 0.132 | -0.428 | -3.161 | -7.774 | -11.275 | -14.451 | Primary | 2395
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Consumer Transformation | 7.792 | 6.82 | 6.424 | 6.005 | 5.634 | 5.29 | 4.862 | 3.1 | 0.769 | -0.827 | -2.382 | Primary | 2396
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 23.554 | 22.973 | 22.422 | 21.792 | 21.291 | 20.82 | 20.244 | 17.537 | 11.059 | 5.914 | 1.074 | Primary | 2397
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Consumer Transformation | 11.23 | 10.88 | 10.308 | 9.639 | 9.201 | 8.85 | 8.412 | 6.471 | 1.204 | -2.744 | -6.754 | Primary | 2398
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Consumer Transformation | 11.146 | 10.77 | 10.219 | 9.613 | 9.159 | 8.753 | 8.255 | 5.988 | 0.45 | -3.986 | -8.367 | Primary | 2399
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Consumer Transformation | 12.908 | 12.733 | 12.836 | 12.912 | 13.016 | 13.125 | 13.215 | 13.568 | 12.82 | 12.229 | 11.602 | Primary | 2400
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Consumer Transformation | 5.991 | 5.529 | 4.918 | 4.301 | 3.779 | 3.278 | 2.684 | -0.041 | -6.221 | -11.36 | -16.264 | Primary | 2401
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Consumer Transformation | 8.569 | 6.987 | 6.889 | 6.755 | 6.647 | 6.532 | 6.358 | 5.439 | 2.996 | 1.157 | -0.451 | Primary | 2402
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Consumer Transformation | 7.821 | 7.085 | 6.698 | 6.25 | 5.899 | 5.57 | 5.166 | 3.348 | -1.421 | -5.344 | -9.102 | Primary | 2403
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Consumer Transformation | 31.099 | 31.107 | 31.114 | 31.12 | 31.127 | 31.134 | 31.141 | 31.171 | 31.168 | 31.166 | 31.159 | Primary | 2404
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Consumer Transformation | 10.303 | 10.282 | 10.209 | 10.108 | 25.465 | 25.445 | 25.409 | 25.231 | 23.627 | 22.298 | 20.93 | Primary | 2405
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Consumer Transformation | 7.597 | 5.859 | 20.334 | 19.781 | 19.324 | 18.882 | 18.324 | 16.009 | 10.6 | 6.331 | 2.357 | Primary | 2406
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Consumer Transformation | 8.989 | 8.726 | 8.368 | 7.97 | 7.596 | 7.222 | 6.772 | 4.508 | 0.599 | -2.449 | -5.289 | Primary | 2407
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Consumer Transformation | 11.67 | 11.548 | 11.372 | 11.195 | 11.04 | 10.89 | 10.71 | 9.989 | 8.635 | 7.58 | 6.631 | Primary | 2408
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Consumer Transformation | 19.935 | 19.402 | 19.297 | 19.162 | 19.082 | 19.012 | 18.907 | 18.395 | 15.78 | 13.576 | 11.483 | Primary | 2409
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Consumer Transformation | 10.595 | 10.12 | 9.449 | 8.806 | 8.284 | 7.8 | 7.189 | 4.383 | -0.988 | -4.841 | -8.437 | Primary | 2410
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Consumer Transformation | 11.934 | 11.528 | 11.179 | 10.777 | 10.487 | 10.236 | 9.933 | 8.566 | 4.074 | 0.337 | -3.313 | Primary | 2411
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Consumer Transformation | 10.918 | 10.313 | 9.899 | 9.442 | 9.059 | 8.699 | 8.248 | 6.332 | 2.168 | -1.152 | -4.287 | Primary | 2412
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 13.921 | 13.909 | 13.866 | 13.803 | 13.779 | 13.762 | 13.733 | 13.55 | 12.473 | 11.64 | 10.832 | Primary | 2413
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 14.113 | 14.102 | 14.064 | 14.003 | 13.964 | 13.93 | 13.882 | 13.555 | 12.302 | 11.393 | 10.572 | Primary | 2414
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 18.662 | 18.543 | 18.359 | 18.152 | 17.987 | 17.838 | 17.649 | 16.811 | 15.302 | 14.226 | 13.177 | Primary | 2415
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 18.873 | 18.757 | 18.577 | 18.369 | 18.216 | 18.085 | 17.922 | 17.191 | 15.333 | 13.924 | 12.519 | Primary | 2416
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Consumer Transformation | 12.143 | 11.909 | 11.565 | 11.187 | 10.864 | 10.55 | 10.174 | 8.533 | 3.902 | -0.122 | -3.911 | Primary | 2417
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 22.115 | 21.693 | 21.126 | 20.589 | 20.182 | 19.824 | 19.378 | 17.383 | 13.548 | 10.737 | 7.938 | Primary | 2418
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Consumer Transformation | 26.993 | 26.086 | 26.02 | 25.946 | 25.871 | 25.787 | 25.689 | 25.262 | 24.787 | 24.417 | 24.1 | Primary | 2419
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Consumer Transformation | 5.591 | 5.171 | 5.131 | 5.087 | 5.052 | 5.02 | 4.98 | 4.808 | 4.297 | 3.893 | 3.501 | Primary | 2420
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Consumer Transformation | 11.175 | 11.206 | 11.195 | 11.16 | 11.157 | 11.163 | 11.152 | 11.06 | 9.29 | 7.811 | 6.424 | Primary | 2421
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Falling Short | 5.528 | 5.425 | 5.258 | 5.03 | 4.73 | 4.388 | 4.054 | 2.72 | 1.918 | 1.373 | 1.016 | Primary | 2422
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Falling Short | 11.029 | 10.412 | 8.805 | 8.288 | 7.619 | 6.867 | 6.143 | 3.384 | 1.683 | 0.705 | 0.181 | Primary | 2423
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 8.013 | 7.821 | 9.569 | 9.258 | 8.869 | 8.433 | 8.002 | 6.119 | 4.749 | 3.747 | 3.043 | Primary | 2424
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Falling Short | 5.748 | 5.635 | 5.461 | 5.225 | 4.916 | 4.563 | 4.221 | 2.855 | 2.122 | 1.691 | 1.437 | Primary | 2425
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Falling Short | 22.752 | 22.771 | 22.789 | 22.805 | 22.818 | 22.83 | 22.841 | 22.859 | 22.86 | 22.86 | 22.86 | Primary | 2426
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Falling Short | 1.92 | 1.871 | 1.8 | 1.707 | 1.587 | 1.448 | 1.304 | 0.583 | -0.124 | -0.739 | -1.224 | Primary | 2427
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Falling Short | 3.658 | 3.627 | 3.591 | 3.551 | 3.503 | 3.451 | 3.4 | 3.167 | 2.981 | 2.837 | 2.72 | Primary | 2428
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Falling Short | 2.42 | 2.207 | 1.967 | 1.694 | 1.382 | 1.043 | 0.691 | -1.152 | -3.097 | -4.828 | -6.235 | Primary | 2429
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Falling Short | 7.052 | 6.94 | 6.799 | 6.63 | 6.424 | 6.194 | 5.958 | 4.814 | 3.701 | 2.691 | 1.828 | Primary | 2430
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Falling Short | 11.959 | 11.841 | 11.662 | 11.43 | 11.114 | 10.742 | 10.374 | 8.755 | 7.639 | 6.977 | 6.688 | Primary | 2431
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Falling Short | 4.76 | 4.262 | 3.988 | 3.664 | 3.268 | 2.826 | 2.385 | 0.505 | -0.909 | -1.958 | -2.686 | Primary | 2432
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Falling Short | 11.019 | 10.546 | 10.408 | 10.226 | 9.993 | 9.724 | 9.448 | 8.256 | 7.448 | 6.883 | 6.59 | Primary | 2433
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Falling Short | 7.433 | 7.142 | 6.809 | 6.435 | 5.998 | 5.512 | 5.01 | 2.484 | 0.076 | -1.886 | -3.233 | Primary | 2434
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Falling Short | 3.482 | 2.889 | 2.655 | 2.378 | 2.039 | 1.657 | 1.275 | -0.429 | -1.734 | -2.751 | -3.489 | Primary | 2435
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 13.262 | 13.151 | 12.997 | 12.799 | 12.535 | 12.213 | 11.261 | 7.718 | 5.892 | 4.588 | 4.083 | Primary | 2436
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 16.431 | 16.419 | 16.392 | 16.351 | 16.292 | 16.219 | 16.136 | 15.529 | 14.463 | 13.515 | 12.904 | Primary | 2437
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Falling Short | 9.501 | 8.609 | 8.516 | 8.384 | 8.203 | 7.984 | 7.75 | 6.603 | 5.586 | 4.89 | 4.612 | Primary | 2438
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Falling Short | 10.23 | 9.671 | 9.438 | 9.156 | 8.816 | 8.436 | 8.05 | 6.434 | 5.454 | 4.802 | 4.453 | Primary | 2439
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Falling Short | 15.612 | 15.486 | 15.326 | 15.136 | 14.896 | 14.621 | 14.35 | 13.303 | 12.654 | 12.219 | 11.993 | Primary | 2440
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Falling Short | 7.119 | 7.047 | 6.947 | 6.809 | 6.619 | 6.375 | 6.079 | 4.036 | 1.338 | -0.632 | -1.373 | Primary | 2441
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Falling Short | 20.241 | 20.018 | 19.758 | 19.458 | 19.099 | 18.695 | 18.276 | 16.131 | 14.057 | 12.472 | 11.508 | Primary | 2442
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 17.615 | 17.424 | 17.212 | 16.977 | 16.712 | 16.426 | 16.139 | 14.746 | 13.46 | 12.3 | 11.266 | Primary | 2443
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Falling Short | 11.887 | 11.355 | 11.03 | 10.637 | 10.158 | 9.624 | 9.104 | 6.893 | 5.343 | 4.196 | 3.368 | Primary | 2444
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Falling Short | 7.826 | 7.351 | 7.327 | 7.283 | 7.216 | 7.136 | 7.057 | 6.709 | 6.452 | 6.29 | 6.198 | Primary | 2445
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Falling Short | 8.815 | 8.707 | 8.522 | 8.258 | 7.899 | 7.474 | 7.035 | 4.925 | 3.123 | 1.931 | 1.444 | Primary | 2446
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Falling Short | 7.074 | 6.662 | 6.398 | 6.089 | 5.703 | 5.27 | 4.85 | 3.156 | 2.117 | 1.444 | 1.019 | Primary | 2447
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Falling Short | 8.168 | 8.068 | 7.923 | 7.737 | 7.486 | 7.196 | 6.909 | 5.605 | 4.509 | 3.738 | 3.312 | Primary | 2448
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Falling Short | 8.032 | 7.879 | 7.676 | 7.417 | 7.092 | 6.728 | 6.373 | 4.878 | 3.913 | 3.264 | 2.822 | Primary | 2449
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Falling Short | 4.062 | 3.945 | 3.767 | 3.524 | 3.201 | 2.827 | 2.452 | 0.85 | -0.258 | -0.975 | -1.322 | Primary | 2450
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Falling Short | 7.703 | 7.396 | 7.044 | 6.64 | 6.172 | 5.667 | 5.167 | 2.845 | 0.858 | -0.825 | -2.274 | Primary | 2451
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Falling Short | 8.201 | 7.96 | 8.019 | 8.053 | 8.061 | 8.05 | 8.032 | 7.848 | 7.565 | 7.352 | 7.242 | Primary | 2452
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Falling Short | 5.516 | 4.613 | 4.436 | 4.227 | 3.963 | 3.662 | 3.365 | 2.131 | 1.231 | 0.565 | 0.095 | Primary | 2453
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Falling Short | 14.627 | 13.514 | 13.179 | 12.764 | 12.244 | 11.653 | 11.063 | 8.269 | 5.704 | 3.71 | 2.382 | Primary | 2454
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Falling Short | 12.786 | 12.793 | 12.782 | 12.753 | 12.703 | 12.639 | 12.575 | 12.288 | 12.074 | 11.935 | 11.852 | Primary | 2455
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Falling Short | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | Primary | 2456
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 12.576 | 12.582 | 12.572 | 12.543 | 12.492 | 12.427 | 12.353 | 11.939 | 11.484 | 11.149 | 10.995 | Primary | 2457
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 14.651 | 14.641 | 14.613 | 14.563 | 14.487 | 14.388 | 14.272 | 13.529 | 12.614 | 11.944 | 11.688 | Primary | 2458
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Falling Short | 4.48 | 4.464 | 4.444 | 4.421 | 4.392 | 4.36 | 4.327 | 4.166 | 4.018 | 3.888 | 3.772 | Primary | 2459
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Falling Short | 9.016 | 8.953 | 8.873 | 8.778 | 8.658 | 8.523 | 8.392 | 7.846 | 7.516 | 7.32 | 7.222 | Primary | 2460
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Falling Short | 8.359 | 8.258 | 8.112 | 7.922 | 7.67 | 7.38 | 7.095 | 5.89 | 5.118 | 4.649 | 4.397 | Primary | 2461
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 23.088 | 22.804 | 22.786 | 22.755 | 22.706 | 22.645 | 22.585 | 22.352 | 22.243 | 22.176 | 22.134 | Primary | 2462
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Falling Short | 6.757 | 6.717 | 6.643 | 6.532 | 6.368 | 6.161 | 5.936 | 4.693 | 3.39 | 2.493 | 2.163 | Primary | 2463
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Falling Short | 5.174 | 4.612 | 4.387 | 4.071 | 3.642 | 3.135 | 2.618 | 0.198 | -1.852 | -3.174 | -3.684 | Primary | 2464
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Falling Short | 9.931 | 8.785 | 8.608 | 8.368 | 8.05 | 7.684 | 7.323 | 5.746 | 4.58 | 3.851 | 3.479 | Primary | 2465
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 8.633 | 8.547 | 8.423 | 8.262 | 8.042 | 7.782 | 7.523 | 6.436 | 5.722 | 5.288 | 5.093 | Primary | 2466
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 13.441 | 13.293 | 13.097 | 12.857 | 12.546 | 12.191 | 11.843 | 10.456 | 9.708 | 9.257 | 9.003 | Primary | 2467
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Falling Short | 4.098 | 3.615 | 3.509 | 3.376 | 3.213 | 3.034 | 2.856 | 2.019 | 1.248 | 0.571 | -0.049 | Primary | 2468
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Falling Short | 8.09 | 7.924 | 7.682 | 7.352 | 6.918 | 6.417 | 5.916 | 3.641 | 1.886 | 0.76 | 0.237 | Primary | 2469
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Falling Short | 17.943 | 17.913 | 17.875 | 17.827 | 17.769 | 17.705 | 17.639 | 17.324 | 17.046 | 16.784 | 16.537 | Primary | 2470
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Falling Short | 6.611 | 6.548 | 6.449 | 6.317 | 6.135 | 5.919 | 5.706 | 4.782 | 4.177 | 3.818 | 3.637 | Primary | 2471
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Falling Short | 8.89 | 8.848 | 8.793 | 8.724 | 8.636 | 8.531 | 8.415 | 7.753 | 7.008 | 6.389 | 5.987 | Primary | 2472
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Falling Short | 0.468 | 0.395 | 0.266 | 0.078 | -0.173 | -0.464 | -0.752 | 15.191 | 14.471 | 13.958 | 13.595 | Primary | 2473
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Falling Short | 5.643 | 5.245 | 4.788 | 4.308 | 3.713 | 3.037 | 2.376 | -0.422 | -2.202 | -3.295 | -3.826 | Primary | 2474
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Falling Short | 10.217 | 10.018 | 9.013 | 8.684 | 8.274 | 7.811 | 7.348 | 5.267 | 3.502 | 2.19 | 1.336 | Primary | 2475
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Falling Short | 14.205 | 13.825 | 13.739 | 13.627 | 13.485 | 13.318 | 13.135 | 12.14 | 11.044 | 10.131 | 9.516 | Primary | 2476
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Falling Short | 7.235 | 5.918 | 5.789 | 5.588 | 5.308 | 4.976 | 4.643 | 3.108 | 1.848 | 1.017 | 0.586 | Primary | 2477
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Falling Short | 7.394 | 7.189 | 6.912 | 6.565 | 6.127 | 5.631 | 5.138 | 3.065 | 1.79 | 1.014 | 0.655 | Primary | 2478
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Falling Short | 29.129 | 28.92 | 28.649 | 28.337 | 27.922 | 27.439 | 26.974 | 24.979 | 23.665 | 22.929 | 22.584 | Primary | 2479
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Falling Short | 5.099 | 4.944 | 4.739 | 4.482 | 4.165 | 3.809 | 3.453 | 1.859 | 0.62 | -0.349 | -1.061 | Primary | 2480
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Falling Short | 11.748 | 11.662 | 11.544 | 11.398 | 11.213 | 11.004 | 10.799 | 10.031 | 9.675 | 9.438 | 9.278 | Primary | 2481
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Falling Short | 18.25 | 18.197 | 18.114 | 17.996 | 17.837 | 17.651 | 17.462 | 16.583 | 15.883 | 15.41 | 15.164 | Primary | 2482
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Falling Short | 8.553 | 8.579 | 7.146 | 7.125 | 7.074 | 6.998 | 6.909 | 6.375 | 5.733 | 5.269 | 5.083 | Primary | 2483
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Falling Short | 25.776 | 25.796 | 25.8 | 25.784 | 25.744 | 25.678 | 25.587 | 24.843 | 23.757 | 22.981 | 22.754 | Primary | 2484
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Falling Short | 14.421 | 13.945 | 13.957 | 13.952 | 13.93 | 13.894 | 13.853 | 13.661 | 13.525 | 13.386 | 13.261 | Primary | 2485
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Falling Short | 4.818 | 4.656 | 4.412 | 4.075 | 3.613 | 3.042 | 2.409 | -1.194 | -5.175 | -7.958 | -8.965 | Primary | 2486
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Falling Short | 15.574 | 15.595 | 15.606 | 15.604 | 15.591 | 15.569 | 15.542 | 15.33 | 15.011 | 14.648 | 14.268 | Primary | 2487
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 7.513 | 7.116 | 6.864 | 6.558 | 6.179 | 5.755 | 5.342 | 19.558 | 18.24 | 17.284 | 16.622 | Primary | 2488
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary | 2489
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Falling Short | 2.455 | 2.446 | 2.407 | 2.339 | 2.237 | 2.114 | 1.991 | 1.484 | 1.156 | 0.912 | 0.736 | Primary | 2490
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Falling Short | 14.359 | 14.178 | 13.95 | 13.675 | 13.33 | 12.938 | 12.548 | 10.736 | 9.282 | 8.286 | 7.697 | Primary | 2491
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Falling Short | 14.865 | 12.428 | 12.433 | 12.408 | 12.341 | 12.242 | 12.129 | 11.572 | 11.057 | 10.697 | 10.573 | Primary | 2492
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Falling Short | 8.705 | 8.156 | 7.865 | 7.524 | 7.089 | 6.595 | 6.109 | 3.883 | 2.056 | 0.7 | -0.263 | Primary | 2493
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Falling Short | 18.401 | 18.34 | 18.264 | 18.175 | 18.06 | 17.931 | 17.804 | 17.21 | 16.7 | 16.278 | 15.909 | Primary | 2494
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Falling Short | 11.162 | 10.95 | 10.659 | 10.294 | 9.827 | 9.299 | 8.784 | 6.632 | 5.263 | 4.405 | 3.897 | Primary | 2495
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Falling Short | 3.547 | 2.917 | 2.573 | 2.145 | 1.609 | 1.003 | 0.398 | -2.181 | -4.21 | -5.697 | -6.591 | Primary | 2496
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Falling Short | 2.821 | 2.645 | 2.427 | 2.179 | 1.867 | 1.512 | 1.166 | -0.207 | -0.985 | -1.462 | -1.716 | Primary | 2497
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Falling Short | 8.509 | 8.503 | 8.487 | 8.46 | 8.418 | 8.363 | 8.297 | 7.856 | 7.277 | 6.86 | 6.714 | Primary | 2498
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Falling Short | 21.002 | 20.73 | 20.725 | 20.711 | 20.691 | 20.668 | 20.646 | 20.554 | 20.47 | 20.413 | 20.371 | Primary | 2499
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Falling Short | 19.21 | 19.163 | 19.082 | 18.968 | 18.814 | 18.633 | 18.453 | 17.653 | 16.98 | 16.488 | 16.189 | Primary | 2500
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Falling Short | 14.436 | 14.508 | 14.573 | 14.632 | 14.686 | 14.734 | 14.777 | 14.932 | 15.006 | 15.033 | 15.044 | Primary | 2501
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Falling Short | 14.498 | 14.555 | 14.592 | 14.61 | 14.601 | 14.572 | 14.535 | 14.273 | 13.95 | 13.711 | 13.603 | Primary | 2502
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Falling Short | 1.022 | 1.016 | 0.974 | 0.884 | 20.635 | 20.426 | 20.158 | 18.27 | 15.789 | 14.009 | 13.456 | Primary | 2503
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Falling Short | 7.59 | 7.394 | 7.15 | 6.863 | 6.511 | 6.119 | 5.737 | 4.139 | 3.126 | 2.419 | 1.907 | Primary | 2504
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Falling Short | 6.962 | 6.8 | 6.58 | 6.302 | 5.941 | 5.529 | 5.123 | 3.324 | 1.91 | 0.959 | 0.442 | Primary | 2505
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Falling Short | 16.197 | 16.118 | 16.018 | 15.895 | 15.743 | 15.57 | 15.394 | 14.555 | 13.837 | 13.309 | 12.98 | Primary | 2506
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Falling Short | 6.637 | 6.547 | 6.429 | 6.284 | 6.1 | 5.889 | 5.678 | 4.745 | 4.047 | 3.54 | 3.209 | Primary | 2507
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 1.829 | 1.529 | 1.177 | 0.776 | 0.285 | -0.262 | -0.8 | -3.25 | -5.165 | -6.503 | -7.384 | Primary | 2508
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Falling Short | 18.402 | 18.397 | 18.382 | 18.356 | 18.316 | 18.267 | 18.215 | 17.955 | 17.715 | 17.547 | 17.469 | Primary | 2509
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Falling Short | 6.616 | 6.491 | 6.323 | 6.123 | 5.869 | 5.581 | 5.298 | 4.227 | 3.641 | 3.24 | 2.976 | Primary | 2510
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Falling Short | 2.774 | 2.768 | 2.758 | 2.745 | 2.727 | 2.706 | 2.685 | 2.59 | 2.513 | 2.47 | 2.448 | Primary | 2511
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Falling Short | 9.042 | 8.702 | 8.605 | 8.486 | 8.338 | 8.169 | 7.991 | 7.08 | 6.17 | 5.406 | 4.857 | Primary | 2512
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Falling Short | 14.296 | 14.195 | 14.064 | 13.902 | 13.699 | 13.471 | 13.249 | 12.299 | 11.658 | 11.236 | 10.947 | Primary | 2513
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Falling Short | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 2514
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Falling Short | 20.847 | 20.777 | 20.686 | 20.575 | 20.432 | 20.269 | 20.108 | 19.41 | 18.93 | 18.639 | 18.496 | Primary | 2515
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Falling Short | 8.363 | 8.251 | 8.102 | 7.924 | 7.698 | 7.442 | 7.19 | 6.164 | 5.552 | 5.115 | 4.793 | Primary | 2516
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Falling Short | 14.284 | 14.174 | 14.032 | 13.858 | 13.642 | 13.399 | 13.157 | 12.074 | 11.25 | 10.652 | 10.267 | Primary | 2517
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Falling Short | 33.138 | 32.766 | 32.755 | 32.736 | 32.705 | 32.668 | 32.633 | 32.498 | 32.417 | 32.368 | 32.337 | Primary | 2518
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Falling Short | 4.469 | 3.938 | 3.7 | 3.387 | 2.976 | 2.506 | 2.055 | 0.233 | -0.845 | -1.471 | -1.812 | Primary | 2519
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Falling Short | 14.426 | 13.691 | 13.425 | 13.12 | 12.774 | 12.398 | 12.004 | 17.89 | 15.404 | 13.215 | 11.528 | Primary | 2520
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Falling Short | 9.381 | 9.243 | 9.067 | 8.847 | 8.573 | 8.264 | 7.944 | 6.396 | 5.041 | 4.014 | 3.362 | Primary | 2521
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Falling Short | 15.324 | 15.279 | 15.224 | 15.156 | 15.073 | 14.979 | 14.879 | 14.357 | 13.822 | 13.368 | 13.034 | Primary | 2522
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 24.411 | 22.706 | 22.527 | 22.307 | 22.03 | 21.717 | 21.413 | 20.293 | 19.705 | 19.363 | 19.192 | Primary | 2523
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Falling Short | 5.147 | 4.631 | 4.324 | 3.976 | 3.576 | 3.141 | 2.706 | 0.747 | -0.864 | -2.245 | -3.403 | Primary | 2524
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Falling Short | 1.532 | 0.94 | 0.659 | 0.332 | -0.072 | -0.521 | -0.959 | -2.8 | -4.043 | -4.949 | -5.643 | Primary | 2525
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Falling Short | 3.101 | 3.06 | 1.69 | 1.614 | 1.522 | 1.416 | 1.308 | 0.836 | 0.446 | 0.134 | -0.084 | Primary | 2526
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Falling Short | 7.524 | 7.144 | 8.968 | 8.751 | 8.465 | 8.133 | 7.806 | 6.382 | 5.427 | 4.846 | 4.561 | Primary | 2527
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Falling Short | 5.612 | 5.611 | 5.579 | 5.515 | 5.415 | 5.294 | 5.17 | 4.612 | 4.177 | 3.851 | 3.628 | Primary | 2528
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Falling Short | 32.102 | 30.714 | 30.64 | 30.549 | 30.44 | 30.315 | 30.18 | 29.605 | 29.195 | 28.891 | 28.748 | Primary | 2529
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Falling Short | 12.217 | 12.132 | 12.015 | 11.863 | 11.666 | 11.443 | 11.226 | 10.349 | 9.873 | 9.587 | 9.421 | Primary | 2530
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Falling Short | 8.839 | 8.181 | 7.993 | 7.793 | 7.548 | 7.275 | 7.008 | 6.093 | 5.711 | 5.482 | 5.339 | Primary | 2531
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Falling Short | 6.402 | 6.44 | 6.464 | 6.474 | 6.468 | 6.451 | 6.427 | 6.252 | 6 | 5.757 | 5.576 | Primary | 2532
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Falling Short | 13.458 | 13.43 | 13.379 | 13.296 | 13.183 | 13.05 | 12.918 | 12.316 | 11.855 | 11.57 | 11.425 | Primary | 2533
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 14.455 | 14.35 | 14.213 | 14.03 | 13.795 | 13.505 | 13.165 | 10.909 | 7.989 | 5.709 | 4.523 | Primary | 2534
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 12.811 | 12.636 | 12.443 | 12.227 | 11.988 | 11.737 | 11.482 | 10.215 | 9 | 7.829 | 6.693 | Primary | 2535
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Falling Short | 4.439 | 3.363 | 3.046 | 2.693 | 2.298 | 1.877 | 1.449 | -0.588 | -2.572 | -4.377 | -5.947 | Primary | 2536
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Falling Short | 4.866 | 3.534 | 2.829 | 2.001 | 1.019 | -0.059 | -1.107 | -5.535 | -9.042 | -11.967 | -14.361 | Primary | 2537
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Falling Short | 11.694 | 11.004 | 10.784 | 10.549 | 10.251 | 9.914 | 9.592 | 8.256 | 7.357 | 6.763 | 6.354 | Primary | 2538
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Falling Short | 15.859 | 15.18 | 15 | 14.766 | 14.458 | 14.104 | 13.758 | 12.382 | 11.569 | 11.07 | 10.807 | Primary | 2539
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Falling Short | 8.125 | 8.045 | 7.916 | 7.734 | 7.489 | 7.204 | 6.927 | 5.786 | 5.12 | 4.726 | 4.525 | Primary | 2540
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Falling Short | 12.674 | 12.665 | 12.653 | 12.637 | 12.617 | 12.593 | 12.567 | 12.405 | 12.2 | 11.979 | 11.754 | Primary | 2541
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Falling Short | 21.638 | 21.578 | 21.499 | 21.4 | 21.28 | 21.146 | 21.013 | 20.399 | 19.834 | 19.326 | 18.894 | Primary | 2542
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Falling Short | 14.886 | 14.961 | 15.025 | 15.076 | 15.114 | 15.144 | 15.169 | 15.225 | 15.195 | 15.157 | 15.125 | Primary | 2543
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 10.801 | 10.599 | 10.346 | 10.045 | 9.675 | 9.262 | 8.859 | 7.131 | 5.908 | 5.017 | 4.386 | Primary | 2544
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 21.849 | 21.816 | 21.774 | 21.725 | 21.665 | 21.597 | 21.529 | 21.214 | 20.941 | 20.687 | 20.45 | Primary | 2545
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Falling Short | 2.618 | 2.517 | 2.364 | 2.158 | 1.886 | 1.575 | 1.27 | 0.068 | -0.577 | -0.994 | -1.262 | Primary | 2546
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Falling Short | 6.6 | 6.595 | 6.587 | 6.576 | 6.561 | 6.544 | 6.527 | 6.453 | 6.405 | 6.377 | 6.361 | Primary | 2547
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Falling Short | 6.06 | 5.388 | 5.281 | 5.149 | 4.976 | 4.775 | 4.575 | 3.767 | 3.284 | 2.951 | 2.755 | Primary | 2548
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Falling Short | 12.149 | 11.813 | 11.377 | 10.833 | 10.15 | 9.373 | 8.591 | 4.989 | 2.089 | 0.075 | -0.992 | Primary | 2549
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Falling Short | 10.504 | 9.141 | 8.492 | 8.229 | 7.879 | 7.472 | 7.06 | 5.246 | 3.881 | 2.99 | 2.604 | Primary | 2550
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Falling Short | 15.095 | 14.923 | 14.731 | 14.515 | 14.266 | 13.992 | 13.712 | 12.301 | 10.942 | 9.815 | 8.966 | Primary | 2551
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Falling Short | 15.827 | 15.709 | 15.586 | 15.457 | 15.321 | 15.18 | 15.036 | 14.352 | 13.683 | 13.019 | 12.379 | Primary | 2552
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Falling Short | 1.99 | 1.663 | 22.851 | 22.7 | 22.501 | 22.261 | 21.994 | 20.409 | 18.547 | 17.105 | 16.316 | Primary | 2553
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Falling Short | 13.769 | 13.375 | 13.195 | 12.969 | 12.672 | 12.332 | 12.007 | 10.684 | 9.909 | 9.485 | 9.289 | Primary | 2554
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Falling Short | 3.292 | 3.163 | 3.009 | 2.833 | 2.623 | 2.393 | 2.172 | 1.243 | 0.63 | 0.164 | -0.217 | Primary | 2555
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Falling Short | 2.817 | 2.704 | 2.573 | 2.425 | 2.248 | 2.051 | 1.853 | 0.903 | 0.073 | -0.57 | -1.018 | Primary | 2556
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 12.416 | 11.915 | 11.751 | 11.518 | 11.206 | 10.845 | 10.495 | 8.989 | 7.936 | 7.29 | 6.924 | Primary | 2557
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Falling Short | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2558
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Falling Short | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2559
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Falling Short | 17.614 | 17.138 | 17.03 | 16.892 | 16.714 | 16.512 | 16.313 | 15.492 | 14.954 | 14.564 | 14.283 | Primary | 2560
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Falling Short | 11.071 | 9.956 | 9.813 | 9.647 | 9.451 | 9.232 | 9.002 | 7.91 | 6.864 | 5.978 | 5.318 | Primary | 2561
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Falling Short | 10.513 | 10.423 | 10.297 | 10.141 | 9.936 | 9.697 | 9.455 | 8.366 | 7.548 | 7.002 | 6.74 | Primary | 2562
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Falling Short | 13.027 | 12.85 | 12.641 | 12.405 | 12.116 | 11.791 | 11.47 | 10.005 | 8.875 | 8.068 | 7.528 | Primary | 2563
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Falling Short | 10.431 | 9.647 | 9.487 | 9.291 | 9.053 | 8.788 | 8.523 | 7.361 | 6.479 | 5.775 | 5.243 | Primary | 2564
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Falling Short | 10.338 | 10.288 | 10.205 | 10.09 | 9.933 | 9.744 | 9.548 | 8.649 | 7.913 | 7.401 | 7.165 | Primary | 2565
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Falling Short | 16.741 | 15.964 | 15.969 | 15.95 | 15.907 | 15.846 | 15.781 | 15.425 | 15.063 | 14.799 | 14.654 | Primary | 2566
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Falling Short | 15.78 | 15.605 | 15.378 | 15.102 | 14.75 | 14.341 | 13.918 | 11.827 | 9.903 | 8.505 | 7.747 | Primary | 2567
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | 5.587 | 5.515 | 5.416 | 5.293 | 5.13 | 4.943 | 4.761 | 3.988 | 3.496 | 3.222 | 3.109 | Primary | 2568
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Falling Short | 12.457 | 12.141 | 10.474 | 10.225 | 9.893 | 9.505 | 9.109 | 7.265 | 5.535 | 4.213 | 3.437 | Primary | 2569
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Falling Short | 23.178 | 13.728 | 2.976 | 2.603 | 2.136 | 1.604 | 1.058 | -1.196 | -3.041 | -4.477 | -5.405 | Primary | 2570
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Falling Short | 0.84 | 0.29 | -0.034 | -2.199 | -2.703 | -3.275 | -3.827 | -6.059 | -7.461 | -8.392 | -9.029 | Primary | 2571
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Falling Short | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary | 2572
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Falling Short | 3.204 | 3.065 | 2.908 | 2.731 | 2.528 | 2.307 | 2.077 | 0.87 | -0.366 | -1.428 | -2.246 | Primary | 2573
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Falling Short | 12.004 | 11.242 | 11.036 | 10.785 | 10.478 | 10.137 | 9.796 | 8.16 | 6.478 | 5.038 | 3.96 | Primary | 2574
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 5.8 | 4.206 | 4.183 | 4.115 | 4.001 | 3.854 | 3.7 | 2.971 | 2.297 | 1.843 | 1.639 | Primary | 2575
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 27.934 | 27.946 | 27.956 | 27.966 | 27.975 | 27.983 | 27.99 | 28.017 | 28.03 | 28.035 | 28.037 | Primary | 2576
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Falling Short | 20.024 | 19.083 | 18.889 | 18.651 | 18.359 | 18.034 | 17.717 | 16.438 | 15.647 | 15.082 | 14.662 | Primary | 2577
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Falling Short | 8.139 | 7.439 | 7.513 | 7.535 | 7.497 | 7.397 | 7.24 | 5.924 | 4.001 | 2.608 | 2.192 | Primary | 2578
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Falling Short | 2.952 | 2.727 | 2.567 | 2.401 | 2.229 | 2.052 | 1.871 | 0.993 | 0.09 | -0.872 | -1.861 | Primary | 2579
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Falling Short | 13.94 | 13.786 | 13.59 | 13.36 | 13.072 | 12.749 | 12.435 | 11.202 | 10.594 | 10.227 | 9.993 | Primary | 2580
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Falling Short | 2.324 | 2.079 | 1.789 | 1.449 | 1.04 | 0.586 | 0.129 | -2.051 | -3.929 | -5.353 | -6.33 | Primary | 2581
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Falling Short | 7.826 | 6.981 | 6.791 | 6.559 | 6.267 | 5.942 | 5.627 | 4.325 | 3.451 | 2.868 | 2.484 | Primary | 2582
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 23.572 | 23.13 | 22.848 | 22.502 | 22.079 | 21.606 | 21.138 | 19.094 | 17.619 | 16.567 | 15.865 | Primary | 2583
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Falling Short | 11.311 | 11.223 | 11.074 | 10.866 | 10.582 | 10.25 | 9.922 | 8.554 | 7.567 | 6.909 | 6.559 | Primary | 2584
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Falling Short | 11.224 | 11.048 | 10.825 | 10.557 | 10.224 | 9.852 | 9.491 | 7.936 | 6.84 | 6.074 | 5.529 | Primary | 2585
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Falling Short | 12.712 | 12.475 | 12.54 | 12.59 | 12.623 | 12.646 | 12.663 | 12.687 | 12.639 | 12.581 | 12.532 | Primary | 2586
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Falling Short | 6.008 | 5.655 | 5.257 | 4.819 | 4.308 | 3.75 | 3.202 | 0.805 | -0.943 | -2.332 | -3.467 | Primary | 2587
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Falling Short | 8.487 | 6.903 | 6.854 | 6.773 | 6.648 | 6.491 | 6.325 | 5.557 | 4.945 | 4.546 | 4.403 | Primary | 2588
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Falling Short | 7.81 | 7.143 | 6.923 | 6.654 | 6.327 | 5.963 | 5.603 | 4.135 | 3.28 | 2.686 | 2.273 | Primary | 2589
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Falling Short | 31.089 | 31.093 | 31.097 | 31.101 | 31.104 | 31.106 | 31.108 | 31.116 | 31.12 | 31.12 | 31.12 | Primary | 2590
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Falling Short | 10.249 | 10.252 | 10.241 | 10.216 | 25.574 | 25.523 | 25.471 | 25.256 | 25.102 | 24.977 | 24.882 | Primary | 2591
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Falling Short | 7.652 | 6.067 | 20.831 | 20.545 | 20.174 | 19.753 | 19.341 | 17.755 | 16.811 | 16.253 | 15.97 | Primary | 2592
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Falling Short | 8.95 | 8.746 | 8.509 | 8.231 | 7.904 | 7.541 | 7.174 | 5.333 | 3.56 | 2.146 | 1.119 | Primary | 2593
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Falling Short | 11.706 | 11.633 | 11.539 | 11.427 | 11.288 | 11.132 | 10.983 | 10.421 | 10.183 | 10.062 | 9.995 | Primary | 2594
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Falling Short | 19.882 | 19.357 | 19.309 | 19.24 | 19.142 | 19.026 | 18.909 | 18.447 | 18.216 | 18.069 | 17.986 | Primary | 2595
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Falling Short | 10.745 | 10.54 | 10.278 | 9.977 | 9.581 | 9.123 | 8.671 | 6.683 | 5.266 | 4.391 | 3.995 | Primary | 2596
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Falling Short | 11.953 | 11.635 | 11.464 | 11.25 | 10.991 | 10.703 | 10.419 | 9.305 | 8.749 | 8.378 | 8.136 | Primary | 2597
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Falling Short | 10.97 | 10.49 | 10.305 | 10.07 | 9.766 | 9.42 | 9.086 | 7.775 | 7.102 | 6.732 | 6.529 | Primary | 2598
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 13.894 | 13.897 | 13.893 | 13.88 | 13.857 | 13.827 | 13.796 | 13.635 | 13.478 | 13.37 | 13.316 | Primary | 2599
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 14.081 | 14.084 | 14.078 | 14.06 | 14.029 | 13.99 | 13.946 | 13.674 | 13.338 | 13.103 | 13.006 | Primary | 2600
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 18.696 | 18.657 | 18.598 | 18.519 | 18.412 | 18.287 | 18.167 | 17.644 | 17.26 | 17.023 | 16.898 | Primary | 2601
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 18.901 | 18.868 | 18.817 | 18.746 | 18.652 | 18.544 | 18.44 | 17.984 | 17.632 | 17.408 | 17.272 | Primary | 2602
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Falling Short | 12.151 | 11.972 | 11.754 | 11.497 | 11.188 | 10.847 | 10.515 | 9.209 | 8.477 | 7.956 | 7.544 | Primary | 2603
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 22.245 | 22.069 | 21.856 | 21.62 | 21.319 | 20.976 | 20.642 | 19.167 | 18.077 | 17.329 | 16.84 | Primary | 2604
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Falling Short | 26.878 | 25.87 | 25.704 | 25.53 | 25.345 | 25.149 | 24.943 | 24.137 | 23.463 | 22.812 | 22.23 | Primary | 2605
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Falling Short | 5.584 | 5.174 | 5.158 | 5.135 | 5.106 | 5.072 | 5.039 | 4.901 | 4.797 | 4.723 | 4.669 | Primary | 2606
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Falling Short | 11.079 | 11.087 | 11.081 | 11.059 | 11.019 | 10.969 | 10.916 | 10.688 | 10.531 | 10.403 | 10.313 | Primary | 2607
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Leading the Way | 5.382 | 4.87 | 4.081 | 3.204 | 2.701 | 2.397 | 1.777 | -4.906 | -9.838 | -13.068 | -12.374 | Primary | 2608
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Leading the Way | 10.834 | 9.594 | 7.069 | 5.616 | 4.605 | 3.833 | 2.686 | -9.89 | -18.476 | -24.439 | -23.358 | Primary | 2609
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 7.951 | 7.48 | 8.764 | 7.967 | 7.455 | 7.055 | 6.368 | -0.156 | -4.883 | -8.065 | -7.757 | Primary | 2610
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Leading the Way | 5.704 | 5.339 | 4.723 | 4.011 | 3.586 | 3.284 | 2.667 | -3.908 | -8.829 | -12.245 | -11.666 | Primary | 2611
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Leading the Way | 22.754 | 22.794 | 22.832 | 22.867 | 22.901 | 22.932 | 22.962 | 23.01 | 23.012 | 23.014 | 23.017 | Primary | 2612
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Leading the Way | 2.038 | 1.954 | 1.784 | 1.583 | 1.485 | 1.423 | 1.258 | -1.029 | -2.758 | -3.915 | -3.616 | Primary | 2613
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Leading the Way | 3.659 | 3.618 | 3.562 | 3.507 | 3.457 | 3.406 | 3.336 | 2.855 | 2.527 | 2.299 | 2.253 | Primary | 2614
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Leading the Way | 2.608 | 2.373 | 2.041 | 1.668 | 1.377 | 1.122 | 0.753 | -2.93 | -5.88 | -8.039 | -8.344 | Primary | 2615
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Leading the Way | 7.196 | 6.987 | 6.657 | 6.297 | 6.097 | 5.98 | 5.713 | 1.984 | -0.911 | -2.994 | -2.727 | Primary | 2616
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Leading the Way | 11.86 | 11.491 | 10.911 | 10.303 | 9.87 | 9.497 | 8.877 | 4.044 | 0.827 | -0.987 | -0.46 | Primary | 2617
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Leading the Way | 4.734 | 4.022 | 3.374 | 2.683 | 2.197 | 1.789 | 1.049 | -6.74 | -12.589 | -16.929 | -16.689 | Primary | 2618
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Leading the Way | 11.006 | 10.36 | 9.905 | 9.379 | 9.074 | 8.854 | 8.345 | 2.443 | -1.972 | -5.084 | -4.572 | Primary | 2619
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Leading the Way | 7.44 | 6.956 | 6.287 | 5.558 | 5.049 | 4.603 | 3.912 | -1.859 | -6.07 | -8.751 | -8.901 | Primary | 2620
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Leading the Way | 3.513 | 2.751 | 2.174 | 1.527 | 1.141 | 0.834 | 0.215 | -5.852 | -10.313 | -13.327 | -12.955 | Primary | 2621
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 13.287 | 13.065 | 12.692 | 12.249 | 11.879 | 11.493 | 10.302 | 4.197 | 1.431 | 0.016 | 0.206 | Primary | 2622
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 16.5 | 16.401 | 16.265 | 16.115 | 15.983 | 15.86 | 15.713 | 14.423 | 13.566 | 13.285 | 13.605 | Primary | 2623
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Leading the Way | 9.523 | 8.57 | 8.323 | 8.019 | 7.791 | 7.567 | 7.102 | 1.99 | -1.798 | -4.395 | -3.947 | Primary | 2624
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Leading the Way | 10.16 | 9.45 | 8.946 | 8.387 | 7.972 | 7.611 | 6.948 | 0.457 | -4.364 | -7.83 | -7.462 | Primary | 2625
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Leading the Way | 15.534 | 15.217 | 14.749 | 14.248 | 13.911 | 13.64 | 13.096 | 8.087 | 4.618 | 2.191 | 2.538 | Primary | 2626
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Leading the Way | 7.094 | 6.909 | 6.62 | 6.25 | 5.895 | 5.496 | 4.92 | -0.109 | -3.678 | -5.542 | -5.552 | Primary | 2627
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Leading the Way | 20.204 | 19.822 | 19.299 | 18.738 | 18.27 | 17.83 | 17.168 | 10.971 | 6.201 | 2.821 | 2.599 | Primary | 2628
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 17.758 | 17.582 | 17.329 | 17.048 | 16.828 | 16.622 | 16.289 | 13.003 | 10.332 | 8.232 | 7.984 | Primary | 2629
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Leading the Way | 11.736 | 10.82 | 9.876 | 8.839 | 8.167 | 7.646 | 6.745 | -1.676 | -7.759 | -11.865 | -11.404 | Primary | 2630
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Leading the Way | 7.842 | 7.274 | 7.094 | 6.897 | 6.796 | 6.746 | 6.602 | 4.141 | 2.302 | 1.012 | 1.393 | Primary | 2631
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Leading the Way | 8.698 | 8.161 | 7.31 | 6.346 | 5.726 | 5.28 | 4.497 | -3.536 | -9.364 | -12.938 | -12.36 | Primary | 2632
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Leading the Way | 6.892 | 6.147 | 5.404 | 4.68 | 4.145 | 3.722 | 3.091 | -2.477 | -6.203 | -8.599 | -8.094 | Primary | 2633
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Leading the Way | 8.036 | 7.632 | 7.045 | 6.417 | 5.999 | 5.688 | 5.112 | -0.792 | -5.006 | -7.75 | -7.152 | Primary | 2634
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Leading the Way | 8.036 | 7.761 | 7.322 | 6.82 | 6.436 | 6.098 | 5.511 | -0.266 | -4.526 | -7.628 | -7.323 | Primary | 2635
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Leading the Way | 3.996 | 3.632 | 3.02 | 2.299 | 1.84 | 1.466 | 0.721 | -6.757 | -12.247 | -15.992 | -15.419 | Primary | 2636
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Leading the Way | 7.772 | 7.335 | 6.732 | 6.074 | 5.566 | 5.124 | 4.47 | -1.644 | -6.44 | -10.111 | -10.49 | Primary | 2637
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Leading the Way | 8.421 | 8.222 | 8.281 | 8.311 | 8.386 | 8.469 | 8.465 | 6.454 | 4.928 | 3.867 | 4.565 | Primary | 2638
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Leading the Way | 5.553 | 4.558 | 4.186 | 3.809 | 3.523 | 3.266 | 2.826 | -1.169 | -3.922 | -5.872 | -5.702 | Primary | 2639
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Leading the Way | 14.555 | 13.007 | 11.967 | 10.832 | 10.064 | 9.45 | 8.461 | -0.88 | -7.605 | -11.9 | -11.337 | Primary | 2640
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Leading the Way | 12.828 | 12.777 | 12.661 | 12.525 | 12.464 | 12.435 | 12.332 | 10.607 | 9.361 | 8.518 | 8.833 | Primary | 2641
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Leading the Way | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | 7.498 | Primary | 2642
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 12.63 | 12.592 | 12.493 | 12.364 | 12.298 | 12.255 | 12.119 | 9.926 | 8.3 | 7.218 | 7.567 | Primary | 2643
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 14.65 | 14.537 | 14.345 | 14.108 | 13.96 | 13.842 | 13.598 | 10.595 | 8.394 | 7.056 | 7.332 | Primary | 2644
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Leading the Way | 4.478 | 4.406 | 4.3 | 4.19 | 4.142 | 4.128 | 4.066 | 2.896 | 1.932 | 1.209 | 1.286 | Primary | 2645
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Leading the Way | 8.944 | 8.749 | 8.461 | 8.155 | 7.974 | 7.838 | 7.575 | 4.895 | 2.934 | 1.628 | 1.865 | Primary | 2646
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Leading the Way | 8.32 | 8.041 | 7.586 | 7.084 | 6.757 | 6.488 | 5.952 | -0.08 | -4.518 | -7.603 | -6.95 | Primary | 2647
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 23.137 | 22.85 | 22.797 | 22.732 | 22.701 | 22.679 | 22.567 | 21.085 | 20.003 | 19.254 | 19.587 | Primary | 2648
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Leading the Way | 6.789 | 6.638 | 6.352 | 6.021 | 5.792 | 5.575 | 5.151 | 0.488 | -2.861 | -4.857 | -4.243 | Primary | 2649
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Leading the Way | 5.042 | 4.099 | 3.258 | 2.302 | 1.623 | 1.044 | 0.123 | -7.874 | -13.361 | -16.548 | -15.894 | Primary | 2650
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Leading the Way | 9.902 | 8.519 | 7.924 | 7.258 | 6.818 | 6.458 | 5.789 | -2.104 | -7.841 | -11.839 | -11.054 | Primary | 2651
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 8.631 | 8.463 | 8.171 | 7.862 | 7.607 | 7.355 | 6.892 | 2.731 | -0.059 | -1.923 | -1.539 | Primary | 2652
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 13.363 | 13.018 | 12.477 | 11.903 | 11.515 | 11.191 | 10.513 | 3.625 | -1.468 | -5.121 | -4.562 | Primary | 2653
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Leading the Way | 4.237 | 3.728 | 3.542 | 3.344 | 3.218 | 3.129 | 2.967 | 0.114 | -2.097 | -3.836 | -3.658 | Primary | 2654
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Leading the Way | 8.025 | 7.572 | 6.842 | 6.001 | 5.388 | 4.859 | 3.875 | -6.591 | -14.39 | -19.827 | -19.057 | Primary | 2655
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Leading the Way | 18.017 | 17.993 | 17.936 | 17.864 | 17.831 | 17.811 | 17.728 | 16.369 | 15.288 | 14.462 | 14.602 | Primary | 2656
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Leading the Way | 6.577 | 6.333 | 5.94 | 5.533 | 5.275 | 5.088 | 4.721 | 0.908 | -1.708 | -3.364 | -2.939 | Primary | 2657
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Leading the Way | 8.988 | 8.962 | 8.897 | 8.816 | 8.744 | 8.67 | 8.541 | 7.177 | 6.196 | 5.586 | 5.624 | Primary | 2658
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Leading the Way | 0.464 | 0.171 | -0.334 | -0.933 | -1.277 | -1.495 | -1.992 | 9.047 | 4.524 | 1.361 | 2.065 | Primary | 2659
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Leading the Way | 5.341 | 4.543 | 3.468 | 2.515 | 1.772 | 1.085 | 0.032 | -7.888 | -13.294 | -16.644 | -16.132 | Primary | 2660
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Leading the Way | 10.06 | 9.437 | 7.803 | 6.823 | 6.182 | 5.714 | 4.951 | -2.81 | -8.549 | -12.38 | -12.039 | Primary | 2661
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Leading the Way | 14.363 | 14.018 | 13.93 | 13.809 | 13.699 | 13.578 | 13.374 | 11.353 | 9.898 | 8.971 | 9.031 | Primary | 2662
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Leading the Way | 7.269 | 5.702 | 5.14 | 4.503 | 4.112 | 3.825 | 3.205 | -5.756 | -12.391 | -17.084 | -15.962 | Primary | 2663
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Leading the Way | 7.235 | 6.694 | 5.865 | 4.951 | 4.329 | 3.827 | 2.954 | -5.078 | -10.803 | -14.622 | -14.2 | Primary | 2664
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Leading the Way | 28.899 | 28.302 | 27.447 | 26.643 | 26.055 | 25.546 | 24.746 | 18.208 | 13.96 | 11.406 | 11.897 | Primary | 2665
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Leading the Way | 5.122 | 4.773 | 4.233 | 3.623 | 3.232 | 2.943 | 2.41 | -3.125 | -7.299 | -10.203 | -9.945 | Primary | 2666
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Leading the Way | 11.665 | 11.359 | 10.898 | 10.406 | 10.133 | 9.968 | 9.627 | 6.095 | 3.544 | 1.83 | 2.164 | Primary | 2667
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Leading the Way | 18.263 | 18.11 | 17.839 | 17.52 | 17.308 | 17.133 | 16.764 | 12.414 | 9.122 | 6.815 | 7.225 | Primary | 2668
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Leading the Way | 8.616 | 8.577 | 7.019 | 6.843 | 6.752 | 6.688 | 6.509 | 3.955 | 2.199 | 1.133 | 1.527 | Primary | 2669
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Leading the Way | 25.852 | 25.887 | 25.887 | 25.848 | 25.779 | 25.668 | 25.5 | 23.778 | 22.593 | 22.081 | 22.266 | Primary | 2670
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Leading the Way | 14.539 | 14.022 | 13.932 | 13.821 | 13.82 | 13.88 | 13.856 | 12.482 | 11.459 | 10.797 | 11.208 | Primary | 2671
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Leading the Way | 4.849 | 4.588 | 4.117 | 3.521 | 2.859 | 2.075 | 1.035 | -5.145 | -8.858 | -10.212 | -10.237 | Primary | 2672
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Leading the Way | 15.811 | 15.933 | 16.036 | 16.126 | 16.219 | 16.314 | 16.394 | 16.218 | 16.022 | 15.854 | 16.111 | Primary | 2673
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 7.47 | 6.853 | 6.237 | 5.579 | 5.091 | 4.67 | 4.013 | 14.259 | 10.192 | 7.473 | 7.821 | Primary | 2674
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary | 2675
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Leading the Way | 2.429 | 2.2 | 1.809 | 1.361 | 1.175 | 1.11 | 0.839 | -3.152 | -6.204 | -8.263 | -7.687 | Primary | 2676
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Leading the Way | 14.297 | 13.919 | 13.361 | 12.771 | 12.322 | 11.911 | 11.309 | 6.126 | 2.573 | 0.324 | 0.487 | Primary | 2677
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Leading the Way | 14.991 | 12.57 | 12.524 | 12.435 | 12.4 | 12.362 | 12.159 | 9.587 | 7.895 | 6.818 | 7.295 | Primary | 2678
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Leading the Way | 8.646 | 7.759 | 6.926 | 6.088 | 5.53 | 5.09 | 4.324 | -3.899 | -10.073 | -14.412 | -13.978 | Primary | 2679
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Leading the Way | 18.444 | 18.307 | 18.101 | 17.901 | 17.78 | 17.701 | 17.548 | 15.473 | 13.85 | 12.667 | 12.816 | Primary | 2680
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Leading the Way | 10.919 | 10.179 | 9.106 | 7.966 | 7.241 | 6.73 | 5.867 | -2.675 | -8.79 | -12.828 | -12.324 | Primary | 2681
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Leading the Way | 3.501 | 2.549 | 1.662 | 0.682 | -0.04 | -0.669 | -1.644 | -9.925 | -15.491 | -19.063 | -18.477 | Primary | 2682
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Leading the Way | 2.628 | 2.102 | 1.391 | 0.707 | 0.243 | -0.092 | -0.632 | -5.422 | -8.663 | -10.754 | -10.398 | Primary | 2683
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Leading the Way | 8.501 | 8.441 | 8.342 | 8.224 | 8.132 | 8.048 | 7.916 | 6.633 | 5.721 | 5.266 | 5.348 | Primary | 2684
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Leading the Way | 21.015 | 20.717 | 20.668 | 20.609 | 20.578 | 20.563 | 20.529 | 19.57 | 18.845 | 18.297 | 18.453 | Primary | 2685
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Leading the Way | 19.146 | 18.863 | 18.436 | 17.972 | 17.693 | 17.523 | 17.185 | 13.333 | 10.449 | 8.572 | 8.969 | Primary | 2686
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Leading the Way | 14.59 | 14.735 | 14.872 | 15.001 | 15.125 | 15.243 | 15.354 | 15.76 | 16.088 | 16.365 | 16.676 | Primary | 2687
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Leading the Way | 14.652 | 14.714 | 14.708 | 14.685 | 14.712 | 14.753 | 14.717 | 13.367 | 12.463 | 11.995 | 12.556 | Primary | 2688
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Leading the Way | 1.111 | 1.046 | 0.838 | 0.512 | 20.151 | 19.85 | 19.264 | 12.943 | 8.306 | 5.638 | 6.1 | Primary | 2689
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Leading the Way | 7.535 | 7.107 | 6.477 | 5.803 | 5.365 | 5.019 | 4.437 | -1.107 | -5.146 | -7.95 | -7.699 | Primary | 2690
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Leading the Way | 6.849 | 6.374 | 5.674 | 4.927 | 4.402 | 3.957 | 3.277 | -2.556 | -6.532 | -8.893 | -8.338 | Primary | 2691
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Leading the Way | 16.224 | 16.122 | 15.962 | 15.784 | 15.62 | 15.452 | 15.172 | 12.582 | 10.623 | 9.19 | 9.191 | Primary | 2692
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Leading the Way | 6.698 | 6.53 | 6.263 | 5.985 | 5.793 | 5.636 | 5.366 | 2.237 | -0.018 | -1.579 | -1.213 | Primary | 2693
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 1.698 | 1.13 | 0.35 | -0.43 | -1.055 | -1.633 | -2.465 | -9.54 | -14.646 | -18.21 | -18.305 | Primary | 2694
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Leading the Way | 18.423 | 18.394 | 18.327 | 18.245 | 18.196 | 18.157 | 18.063 | 16.965 | 16.158 | 15.634 | 15.768 | Primary | 2695
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Leading the Way | 6.537 | 6.184 | 5.655 | 5.11 | 4.768 | 4.518 | 4.054 | -0.189 | -3.092 | -4.989 | -4.564 | Primary | 2696
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Leading the Way | 2.77 | 2.747 | 2.712 | 2.678 | 2.652 | 2.628 | 2.591 | 2.183 | 1.907 | 1.728 | 1.769 | Primary | 2697
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Leading the Way | 9.14 | 8.766 | 8.57 | 8.339 | 8.193 | 8.076 | 7.826 | 4.883 | 2.612 | 1.044 | 1.216 | Primary | 2698
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Leading the Way | 14.269 | 14.045 | 13.705 | 13.344 | 13.087 | 12.871 | 12.524 | 9.18 | 6.817 | 5.212 | 5.416 | Primary | 2699
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Leading the Way | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 2700
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Leading the Way | 20.785 | 20.574 | 20.264 | 19.949 | 19.738 | 19.575 | 19.284 | 16.049 | 13.63 | 11.947 | 12.188 | Primary | 2701
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Leading the Way | 8.274 | 7.875 | 7.278 | 6.651 | 6.315 | 6.121 | 5.688 | 0.854 | -2.686 | -5.005 | -4.493 | Primary | 2702
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Leading the Way | 14.225 | 13.91 | 13.439 | 12.925 | 12.615 | 12.389 | 11.981 | 7.819 | 4.765 | 2.782 | 3.073 | Primary | 2703
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Leading the Way | 33.151 | 32.746 | 32.678 | 32.606 | 32.568 | 32.55 | 32.5 | 31.665 | 31.087 | 30.68 | 30.822 | Primary | 2704
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Leading the Way | 4.286 | 3.316 | 2.409 | 1.441 | 0.795 | 0.331 | -0.427 | -7.178 | -11.902 | -14.869 | -14.329 | Primary | 2705
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Leading the Way | 14.514 | 13.668 | 13.216 | 12.708 | 12.305 | 11.944 | 11.447 | 13.788 | 9.194 | 5.72 | 5.353 | Primary | 2706
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Leading the Way | 9.505 | 9.34 | 9.067 | 8.762 | 8.499 | 8.244 | 7.778 | 2.173 | -2.175 | -5.404 | -5.051 | Primary | 2707
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Leading the Way | 15.376 | 15.3 | 15.178 | 15.036 | 14.952 | 14.891 | 14.762 | 12.972 | 11.555 | 10.533 | 10.621 | Primary | 2708
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 24.31 | 22.441 | 21.943 | 21.414 | 21.038 | 20.713 | 20.176 | 15.964 | 13.203 | 11.369 | 11.618 | Primary | 2709
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Leading the Way | 5.245 | 4.672 | 4.194 | 3.659 | 3.264 | 2.912 | 2.327 | -3.405 | -7.944 | -11.441 | -11.612 | Primary | 2710
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Leading the Way | 1.414 | 0.494 | -0.297 | -1.104 | -1.642 | -2.04 | -2.77 | -10.248 | -15.896 | -20.021 | -19.839 | Primary | 2711
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Leading the Way | 3.133 | 3.085 | 1.689 | 1.587 | 1.5 | 1.414 | 1.29 | 0.545 | 0.106 | -0.134 | -0.138 | Primary | 2712
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Leading the Way | 7.501 | 6.962 | 8.487 | 7.994 | 7.654 | 7.356 | 6.782 | 0.317 | -4.434 | -7.788 | -7.165 | Primary | 2713
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Leading the Way | 5.589 | 5.326 | 4.873 | 4.336 | 4.13 | 4.072 | 3.728 | -2.165 | -6.728 | -9.958 | -9.213 | Primary | 2714
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Leading the Way | 32.12 | 30.728 | 30.619 | 30.488 | 30.375 | 30.261 | 30.008 | 27.43 | 25.584 | 24.193 | 24.302 | Primary | 2715
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Leading the Way | 12.221 | 12.06 | 11.778 | 11.449 | 11.224 | 11.029 | 10.605 | 5.941 | 2.401 | -0.195 | 0.234 | Primary | 2716
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Leading the Way | 8.802 | 8.011 | 7.587 | 7.202 | 6.938 | 6.717 | 6.332 | 3.031 | 0.931 | -0.489 | -0.126 | Primary | 2717
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Leading the Way | 6.515 | 6.556 | 6.542 | 6.501 | 6.533 | 6.592 | 6.579 | 5.405 | 4.52 | 3.954 | 4.341 | Primary | 2718
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Leading the Way | 13.497 | 13.427 | 13.283 | 13.101 | 12.967 | 12.845 | 12.586 | 9.017 | 6.315 | 4.339 | 4.759 | Primary | 2719
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 14.658 | 14.591 | 14.442 | 14.216 | 13.945 | 13.599 | 13.127 | 8.779 | 5.665 | 3.944 | 3.857 | Primary | 2720
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 12.98 | 12.783 | 12.489 | 12.147 | 11.961 | 11.834 | 11.577 | 7.754 | 4.585 | 2.056 | 1.961 | Primary | 2721
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Leading the Way | 4.588 | 3.437 | 2.952 | 2.418 | 2.032 | 1.704 | 1.234 | -3.708 | -7.541 | -10.474 | -10.73 | Primary | 2722
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Leading the Way | 4.695 | 2.712 | 1.016 | -0.785 | -2.092 | -3.114 | -4.585 | -15.624 | -23.306 | -28.276 | -28.159 | Primary | 2723
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Leading the Way | 11.51 | 10.508 | 9.827 | 9.219 | 8.788 | 8.453 | 7.937 | 3.429 | 0.231 | -1.895 | -1.695 | Primary | 2724
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Leading the Way | 15.775 | 14.864 | 14.281 | 13.625 | 13.205 | 12.869 | 12.212 | 6.006 | 1.606 | -1.339 | -0.748 | Primary | 2725
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Leading the Way | 8.113 | 7.887 | 7.485 | 7.013 | 6.697 | 6.436 | 5.9 | 0.547 | -3.27 | -5.832 | -5.217 | Primary | 2726
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Leading the Way | 12.772 | 12.811 | 12.844 | 12.873 | 12.899 | 12.921 | 12.939 | 12.874 | 12.808 | 12.74 | 12.771 | Primary | 2727
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Leading the Way | 21.689 | 21.568 | 21.373 | 21.147 | 21.012 | 20.914 | 20.728 | 18.877 | 17.493 | 16.565 | 16.708 | Primary | 2728
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Leading the Way | 15.073 | 15.214 | 15.33 | 15.432 | 15.543 | 15.654 | 15.732 | 15.079 | 14.563 | 14.191 | 14.689 | Primary | 2729
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 10.67 | 10.162 | 9.438 | 8.668 | 8.15 | 7.747 | 7.094 | 0.927 | -3.597 | -6.685 | -6.399 | Primary | 2730
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 21.902 | 21.857 | 21.78 | 21.7 | 21.656 | 21.631 | 21.571 | 20.81 | 20.247 | 19.846 | 19.904 | Primary | 2731
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Leading the Way | 2.561 | 2.218 | 1.668 | 1.056 | 0.689 | 0.435 | -0.097 | -5.885 | -10.098 | -12.932 | -12.153 | Primary | 2732
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Leading the Way | 6.6 | 6.582 | 6.551 | 6.516 | 6.497 | 6.482 | 6.45 | 6.019 | 5.704 | 5.487 | 5.545 | Primary | 2733
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Leading the Way | 6.04 | 5.167 | 4.744 | 4.327 | 4.073 | 3.927 | 3.65 | 0.53 | -1.667 | -3.067 | -2.662 | Primary | 2734
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Leading the Way | 11.962 | 11.2 | 10.092 | 8.862 | 7.919 | 7.089 | 5.699 | -7.193 | -16.619 | -23.077 | -22.597 | Primary | 2735
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Leading the Way | 10.472 | 8.891 | 7.835 | 7.122 | 6.636 | 6.231 | 5.488 | -1.954 | -7.297 | -10.861 | -10.259 | Primary | 2736
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Leading the Way | 15.158 | 14.969 | 14.708 | 14.419 | 14.166 | 13.91 | 13.532 | 10.149 | 7.496 | 5.533 | 5.299 | Primary | 2737
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Leading the Way | 15.945 | 15.883 | 15.808 | 15.728 | 15.652 | 15.575 | 15.48 | 14.867 | 14.366 | 13.936 | 13.692 | Primary | 2738
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Leading the Way | 2.041 | 1.555 | 22.476 | 22.039 | 21.733 | 21.48 | 21.048 | 16.277 | 12.737 | 10.549 | 10.693 | Primary | 2739
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Leading the Way | 13.662 | 13.069 | 12.568 | 12.051 | 11.647 | 11.286 | 10.775 | 7.419 | 5.375 | 4.29 | 4.568 | Primary | 2740
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Leading the Way | 3.261 | 3.035 | 2.712 | 2.368 | 2.126 | 1.916 | 1.597 | -0.781 | -2.46 | -3.576 | -3.545 | Primary | 2741
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Leading the Way | 2.819 | 2.661 | 2.44 | 2.208 | 2.009 | 1.813 | 1.537 | -0.623 | -2.18 | -3.242 | -3.339 | Primary | 2742
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 12.373 | 11.626 | 11.051 | 10.404 | 9.956 | 9.594 | 8.914 | 1.188 | -4.448 | -8.43 | -7.766 | Primary | 2743
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Leading the Way | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2744
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Leading the Way | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2745
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Leading the Way | 17.632 | 17.056 | 16.751 | 16.408 | 16.204 | 16.051 | 15.719 | 11.951 | 9.172 | 7.21 | 7.609 | Primary | 2746
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Leading the Way | 11.191 | 10.107 | 9.959 | 9.783 | 9.615 | 9.433 | 9.158 | 6.949 | 5.432 | 4.371 | 4.264 | Primary | 2747
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Leading the Way | 10.433 | 10.114 | 9.632 | 9.126 | 8.81 | 8.581 | 8.165 | 3.87 | 0.782 | -1.184 | -0.818 | Primary | 2748
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Leading the Way | 12.964 | 12.634 | 12.18 | 11.732 | 11.382 | 11.066 | 10.592 | 6.528 | 3.642 | 1.663 | 1.68 | Primary | 2749
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Leading the Way | 10.497 | 9.664 | 9.37 | 9.019 | 8.772 | 8.556 | 8.158 | 4.166 | 1.164 | -1.029 | -0.869 | Primary | 2750
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Leading the Way | 10.302 | 10.064 | 9.676 | 9.232 | 8.979 | 8.807 | 8.419 | 4.14 | 1.009 | -1.079 | -0.745 | Primary | 2751
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Leading the Way | 16.826 | 16.006 | 15.914 | 15.794 | 15.747 | 15.737 | 15.614 | 12.979 | 11.06 | 9.708 | 10.186 | Primary | 2752
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Leading the Way | 15.728 | 15.303 | 14.661 | 13.96 | 13.474 | 13.051 | 12.353 | 5.916 | 1.361 | -1.448 | -1.143 | Primary | 2753
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | 5.547 | 5.391 | 5.147 | 4.891 | 4.683 | 4.484 | 4.178 | 1.894 | 0.392 | -0.541 | -0.412 | Primary | 2754
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Leading the Way | 12.428 | 11.779 | 9.581 | 8.732 | 8.212 | 7.82 | 7.111 | -0.374 | -5.554 | -8.752 | -7.826 | Primary | 2755
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Leading the Way | 23.191 | 13.52 | 2.201 | 1.289 | 0.662 | 0.165 | -0.647 | -7.869 | -12.57 | -15.671 | -15.367 | Primary | 2756
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Leading the Way | 0.644 | -0.296 | -1.224 | -3.921 | -4.585 | -5.116 | -6.014 | -13.661 | -18.973 | -22.56 | -22.222 | Primary | 2757
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Leading the Way | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary | 2758
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Leading the Way | 3.257 | 3.058 | 2.783 | 2.471 | 2.253 | 2.064 | 1.752 | -1.789 | -4.563 | -6.587 | -6.643 | Primary | 2759
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Leading the Way | 12.022 | 11.023 | 10.447 | 9.813 | 9.384 | 9.048 | 8.527 | 3.48 | -0.141 | -2.464 | -2.063 | Primary | 2760
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 5.855 | 4.11 | 3.801 | 3.42 | 3.234 | 3.125 | 2.814 | -1.721 | -4.842 | -6.924 | -6.291 | Primary | 2761
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 27.96 | 27.983 | 28.006 | 28.028 | 28.048 | 28.068 | 28.087 | 28.168 | 28.232 | 28.286 | 28.335 | Primary | 2762
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Leading the Way | 19.969 | 18.838 | 18.31 | 17.723 | 17.344 | 17.049 | 16.534 | 11.773 | 8.361 | 6.007 | 6.24 | Primary | 2763
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Leading the Way | 8.415 | 7.8 | 7.908 | 7.93 | 7.903 | 7.793 | 7.54 | 4.454 | 2.554 | 1.885 | 2.572 | Primary | 2764
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Leading the Way | 3.183 | 3.097 | 3.077 | 3.051 | 3.021 | 2.986 | 2.947 | 2.633 | 2.279 | 1.893 | 1.582 | Primary | 2765
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Leading the Way | 13.776 | 13.312 | 12.627 | 11.901 | 11.469 | 11.175 | 10.548 | 3.969 | -1.047 | -4.62 | -4.235 | Primary | 2766
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Leading the Way | 2.326 | 1.963 | 1.446 | 0.889 | 0.412 | -0.051 | -0.722 | -6.359 | -10.493 | -13.396 | -13.581 | Primary | 2767
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Leading the Way | 7.781 | 6.77 | 6.316 | 5.851 | 5.475 | 5.156 | 4.727 | 1.468 | -0.61 | -1.905 | -1.754 | Primary | 2768
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 23.523 | 22.868 | 22.207 | 21.467 | 20.936 | 20.479 | 19.682 | 11.828 | 6.067 | 2.019 | 2.406 | Primary | 2769
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Leading the Way | 11.164 | 10.682 | 9.939 | 9.114 | 8.626 | 8.298 | 7.658 | 1.164 | -3.459 | -6.42 | -5.768 | Primary | 2770
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Leading the Way | 11.112 | 10.661 | 9.999 | 9.289 | 8.819 | 8.448 | 7.78 | 1.034 | -3.988 | -7.553 | -7.313 | Primary | 2771
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Leading the Way | 12.9 | 12.704 | 12.781 | 12.836 | 12.936 | 13.053 | 13.113 | 12.263 | 11.626 | 11.21 | 11.745 | Primary | 2772
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Leading the Way | 5.98 | 5.463 | 4.753 | 4.027 | 3.479 | 2.986 | 2.196 | -5.125 | -10.817 | -15.15 | -15.303 | Primary | 2773
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Leading the Way | 8.559 | 6.955 | 6.81 | 6.619 | 6.489 | 6.361 | 6.057 | 2.988 | 0.867 | -0.503 | -0.11 | Primary | 2774
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Leading the Way | 7.802 | 7.013 | 6.54 | 6.004 | 5.628 | 5.308 | 4.717 | -1.14 | -5.502 | -8.71 | -8.459 | Primary | 2775
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Leading the Way | 31.099 | 31.106 | 31.111 | 31.116 | 31.123 | 31.131 | 31.136 | 31.136 | 31.137 | 31.142 | 31.166 | Primary | 2776
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Leading the Way | 10.282 | 10.228 | 10.108 | 9.964 | 25.305 | 25.29 | 25.182 | 23.365 | 21.916 | 20.883 | 21.164 | Primary | 2777
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Leading the Way | 7.591 | 5.802 | 20.179 | 19.527 | 19.055 | 18.635 | 17.885 | 10.573 | 5.572 | 2.007 | 2.503 | Primary | 2778
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Leading the Way | 8.969 | 8.662 | 8.248 | 7.801 | 7.409 | 7.033 | 6.507 | 1.829 | -1.735 | -4.36 | -4.725 | Primary | 2779
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Leading the Way | 11.67 | 11.54 | 11.345 | 11.146 | 10.986 | 10.84 | 10.6 | 8.891 | 7.693 | 6.883 | 7.01 | Primary | 2780
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Leading the Way | 19.93 | 19.373 | 19.222 | 19.036 | 18.943 | 18.876 | 18.636 | 15.533 | 13.179 | 11.456 | 11.876 | Primary | 2781
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Leading the Way | 10.568 | 10.027 | 9.244 | 8.487 | 7.931 | 7.456 | 6.68 | -0.049 | -4.769 | -7.747 | -7.258 | Primary | 2782
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Leading the Way | 11.904 | 11.429 | 10.985 | 10.485 | 10.161 | 9.916 | 9.421 | 4.025 | -0.061 | -3.073 | -2.7 | Primary | 2783
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Leading the Way | 10.903 | 10.262 | 9.784 | 9.256 | 8.867 | 8.529 | 7.926 | 2.668 | -1.107 | -3.755 | -3.477 | Primary | 2784
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 13.915 | 13.886 | 13.819 | 13.734 | 13.703 | 13.689 | 13.62 | 12.383 | 11.457 | 10.835 | 11.061 | Primary | 2785
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 14.103 | 14.071 | 14.005 | 13.92 | 13.867 | 13.826 | 13.741 | 12.321 | 11.239 | 10.527 | 10.727 | Primary | 2786
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 18.65 | 18.504 | 18.284 | 18.046 | 17.878 | 17.743 | 17.527 | 15.562 | 14.232 | 13.404 | 13.558 | Primary | 2787
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 18.855 | 18.703 | 18.477 | 18.232 | 18.072 | 17.955 | 17.756 | 15.459 | 13.792 | 12.664 | 12.865 | Primary | 2788
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Leading the Way | 12.127 | 11.851 | 11.436 | 10.976 | 10.635 | 10.332 | 9.74 | 4.114 | -0.2 | -3.564 | -3.507 | Primary | 2789
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 22.091 | 21.611 | 20.952 | 20.33 | 19.906 | 19.573 | 19.034 | 14.23 | 10.838 | 8.649 | 8.874 | Primary | 2790
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Leading the Way | 26.991 | 26.076 | 25.998 | 25.91 | 25.821 | 25.721 | 25.597 | 24.925 | 24.509 | 24.192 | 24.017 | Primary | 2791
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Leading the Way | 5.587 | 5.157 | 5.104 | 5.049 | 5.012 | 4.984 | 4.931 | 4.27 | 3.804 | 3.463 | 3.528 | Primary | 2792
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Leading the Way | 11.169 | 11.176 | 11.132 | 11.069 | 11.055 | 11.061 | 10.966 | 8.934 | 7.381 | 6.253 | 6.727 | Primary | 2793
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - System Transformation | 5.409 | 5.224 | 4.937 | 4.617 | 4.264 | 3.884 | 3.432 | 1.211 | -2.045 | -6.628 | -13.743 | Primary | 2794
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - System Transformation | 10.829 | 10.016 | 8.137 | 7.415 | 6.619 | 5.78 | 4.826 | 0.874 | -6.286 | -13.527 | -22.8 | Primary | 2795
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 7.892 | 7.607 | 9.221 | 8.812 | 8.365 | 7.889 | 7.362 | 4.609 | 0.777 | -3.595 | -9.838 | Primary | 2796
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - System Transformation | 5.665 | 5.468 | 5.166 | 4.833 | 4.467 | 4.082 | 3.664 | 1.515 | -2.157 | -6.548 | -13.189 | Primary | 2797
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - System Transformation | 22.753 | 22.781 | 22.806 | 22.828 | 22.847 | 22.864 | 22.878 | 22.9 | 22.9 | 22.9 | 22.9 | Primary | 2798
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - System Transformation | 1.952 | 1.909 | 1.833 | 1.744 | 1.635 | 1.506 | 1.349 | 0.396 | -1.323 | -3.267 | -5.881 | Primary | 2799
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - System Transformation | 3.647 | 3.601 | 3.546 | 3.494 | 3.439 | 3.381 | 3.321 | 3.016 | 2.661 | 2.371 | 2.037 | Primary | 2800
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - System Transformation | 2.497 | 2.305 | 2.068 | 1.806 | 1.513 | 1.19 | 0.813 | -1.284 | -4.433 | -7.605 | -11.357 | Primary | 2801
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - System Transformation | 7.087 | 6.981 | 6.832 | 6.677 | 6.492 | 6.279 | 6.007 | 4.505 | 1.858 | -1.316 | -5.61 | Primary | 2802
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - System Transformation | 11.802 | 11.54 | 11.179 | 10.827 | 10.435 | 10.012 | 9.539 | 7.128 | 4.345 | 1.526 | -2.42 | Primary | 2803
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - System Transformation | 4.668 | 4.067 | 3.66 | 3.26 | 2.82 | 2.351 | 1.842 | -0.778 | -5.579 | -10.699 | -17.82 | Primary | 2804
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - System Transformation | 10.954 | 10.435 | 10.225 | 9.996 | 9.734 | 9.444 | 9.126 | 7.217 | 3.968 | -0.027 | -6.101 | Primary | 2805
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - System Transformation | 7.354 | 7.013 | 6.605 | 6.187 | 5.727 | 5.227 | 4.68 | 1.504 | -2.447 | -6.56 | -11.952 | Primary | 2806
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - System Transformation | 3.415 | 2.758 | 2.428 | 2.093 | 1.724 | 1.328 | 0.901 | -1.532 | -5.335 | -9.611 | -15.847 | Primary | 2807
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 13.228 | 13.071 | 12.849 | 12.598 | 12.29 | 11.927 | 10.914 | 6.768 | 4.097 | 1.884 | -0.719 | Primary | 2808
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 16.456 | 16.451 | 16.426 | 16.389 | 16.334 | 16.231 | 16.011 | 14.725 | 14.409 | 13.487 | 12.429 | Primary | 2809
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - System Transformation | 9.468 | 8.534 | 8.376 | 8.201 | 7.988 | 7.743 | 7.474 | 5.736 | 2.532 | -0.65 | -5.06 | Primary | 2810
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - System Transformation | 10.123 | 9.486 | 9.147 | 8.791 | 8.403 | 7.991 | 7.57 | 5.214 | 1.887 | -2.202 | -8.369 | Primary | 2811
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - System Transformation | 15.508 | 15.292 | 15.02 | 14.76 | 14.475 | 14.168 | 13.833 | 12.127 | 9.703 | 6.782 | 2.318 | Primary | 2812
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - System Transformation | 7.088 | 6.997 | 6.862 | 6.687 | 6.451 | 6.147 | 5.761 | 2.971 | -0.784 | -3.437 | -6.093 | Primary | 2813
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - System Transformation | 20.175 | 19.881 | 19.529 | 19.168 | 18.764 | 18.322 | 17.831 | 15.007 | 10.827 | 6.741 | 1.523 | Primary | 2814
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 17.658 | 17.463 | 17.233 | 16.994 | 16.737 | 16.465 | 16.178 | 14.569 | 11.889 | 9.137 | 5.589 | Primary | 2815
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - System Transformation | 11.699 | 11.04 | 10.536 | 10.012 | 9.45 | 8.854 | 8.191 | 4.751 | 0.31 | -5.168 | -13.245 | Primary | 2816
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - System Transformation | 7.812 | 7.314 | 7.259 | 7.2 | 7.126 | 7.041 | 6.927 | 6.343 | 4.71 | 2.996 | 0.67 | Primary | 2817
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - System Transformation | 8.721 | 8.519 | 8.194 | 7.818 | 7.382 | 6.894 | 6.306 | 3.151 | -1.442 | -6.518 | -13.65 | Primary | 2818
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - System Transformation | 6.828 | 6.249 | 5.785 | 5.359 | 4.9 | 4.416 | 3.885 | 1.415 | -1.522 | -4.864 | -9.413 | Primary | 2819
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - System Transformation | 8.005 | 7.808 | 7.537 | 7.266 | 6.962 | 6.62 | 6.19 | 3.832 | 0.643 | -3.151 | -8.671 | Primary | 2820
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - System Transformation | 7.959 | 7.725 | 7.401 | 7.052 | 6.672 | 6.272 | 5.853 | 3.634 | 0.159 | -3.541 | -8.766 | Primary | 2821
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - System Transformation | 3.958 | 3.746 | 3.43 | 3.082 | 2.691 | 2.268 | 1.802 | -0.787 | -4.974 | -9.683 | -16.689 | Primary | 2822
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - System Transformation | 7.678 | 7.315 | 6.871 | 6.406 | 5.909 | 5.387 | 4.82 | 1.908 | -2.417 | -7.022 | -12.969 | Primary | 2823
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - System Transformation | 8.296 | 8.079 | 8.153 | 8.207 | 8.235 | 8.24 | 8.211 | 7.828 | 6.006 | 4.295 | 2.146 | Primary | 2824
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - System Transformation | 5.463 | 4.477 | 4.191 | 3.925 | 3.628 | 3.311 | 2.966 | 1.315 | -1.239 | -3.716 | -6.953 | Primary | 2825
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - System Transformation | 14.486 | 13.251 | 12.734 | 12.194 | 11.595 | 10.924 | 10.093 | 5.737 | 0.52 | -5.619 | -14.04 | Primary | 2826
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - System Transformation | 12.787 | 12.782 | 12.749 | 12.706 | 12.649 | 12.581 | 12.49 | 11.979 | 10.801 | 9.554 | 7.832 | Primary | 2827
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - System Transformation | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | Primary | 2828
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 12.589 | 12.598 | 12.582 | 12.551 | 12.5 | 12.431 | 12.335 | 11.656 | 10.165 | 8.622 | 6.553 | Primary | 2829
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 14.637 | 14.625 | 14.585 | 14.524 | 14.436 | 14.319 | 14.158 | 12.984 | 11.013 | 9.072 | 6.507 | Primary | 2830
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - System Transformation | 4.473 | 4.452 | 4.426 | 4.404 | 4.377 | 4.346 | 4.302 | 4.048 | 3.262 | 2.321 | 0.955 | Primary | 2831
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - System Transformation | 8.938 | 8.822 | 8.678 | 8.542 | 8.396 | 8.243 | 8.077 | 7.193 | 5.719 | 4.024 | 1.488 | Primary | 2832
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - System Transformation | 8.256 | 8.061 | 7.793 | 7.521 | 7.217 | 6.892 | 6.541 | 4.597 | 0.964 | -2.92 | -8.466 | Primary | 2833
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 23.088 | 22.789 | 22.747 | 22.705 | 22.652 | 22.593 | 22.53 | 22.124 | 21.185 | 20.107 | 18.484 | Primary | 2834
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - System Transformation | 6.715 | 6.625 | 6.481 | 6.329 | 6.134 | 5.9 | 5.617 | 3.764 | 0.572 | -2.36 | -6.119 | Primary | 2835
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - System Transformation | 5.021 | 4.323 | 3.9 | 3.428 | 2.892 | 2.302 | 1.626 | -1.901 | -6.633 | -11.192 | -17.173 | Primary | 2836
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - System Transformation | 9.822 | 8.575 | 8.253 | 7.917 | 7.537 | 7.123 | 6.653 | 4.142 | -0.788 | -5.705 | -12.352 | Primary | 2837
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 8.561 | 8.382 | 8.136 | 7.896 | 7.622 | 7.324 | 7.006 | 5.324 | 2.889 | 0.562 | -2.636 | Primary | 2838
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 13.297 | 13.021 | 12.666 | 12.327 | 11.954 | 11.561 | 11.15 | 8.904 | 5.105 | 0.706 | -5.982 | Primary | 2839
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - System Transformation | 4.14 | 3.657 | 3.539 | 3.414 | 3.267 | 3.103 | 2.904 | 1.917 | -0.409 | -2.745 | -5.538 | Primary | 2840
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - System Transformation | 7.974 | 7.681 | 7.257 | 6.787 | 6.26 | 5.686 | 5.047 | 1.447 | -4.899 | -11.452 | -20.696 | Primary | 2841
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - System Transformation | 17.969 | 17.947 | 17.911 | 17.869 | 17.819 | 17.763 | 17.699 | 17.277 | 16.238 | 15.082 | 13.479 | Primary | 2842
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - System Transformation | 6.529 | 6.381 | 6.173 | 5.975 | 5.749 | 5.5 | 5.208 | 3.697 | 1.425 | -0.94 | -4.287 | Primary | 2843
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - System Transformation | 8.932 | 8.901 | 8.85 | 8.787 | 8.704 | 8.601 | 8.474 | 7.666 | 6.512 | 5.48 | 4.321 | Primary | 2844
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - System Transformation | 0.397 | 0.28 | 0.07 | -0.182 | -0.471 | -0.788 | -1.142 | 14.006 | 10.739 | 6.479 | 0.043 | Primary | 2845
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - System Transformation | 5.191 | 4.438 | 3.603 | 2.937 | 2.22 | 1.467 | 0.685 | -3.251 | -7.618 | -12.164 | -18.5 | Primary | 2846
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - System Transformation | 10.074 | 9.767 | 8.62 | 8.195 | 7.725 | 7.213 | 6.601 | 3.589 | -0.92 | -6.087 | -13.208 | Primary | 2847
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - System Transformation | 14.276 | 13.913 | 13.831 | 13.728 | 13.595 | 13.435 | 13.242 | 12.089 | 10.441 | 9.099 | 7.733 | Primary | 2848
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - System Transformation | 7.171 | 5.777 | 5.533 | 5.265 | 4.941 | 4.575 | 4.13 | 1.656 | -4.197 | -10.081 | -17.897 | Primary | 2849
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - System Transformation | 7.21 | 6.858 | 6.386 | 5.896 | 5.362 | 4.798 | 4.195 | 1.032 | -3.3 | -8.115 | -15.205 | Primary | 2850
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - System Transformation | 28.816 | 28.342 | 27.765 | 27.275 | 26.736 | 26.162 | 25.525 | 22.387 | 18.562 | 15.051 | 10.379 | Primary | 2851
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - System Transformation | 5.069 | 4.872 | 4.593 | 4.283 | 3.939 | 3.57 | 3.157 | 0.966 | -2.459 | -6.46 | -12.159 | Primary | 2852
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - System Transformation | 11.65 | 11.501 | 11.303 | 11.108 | 10.897 | 10.675 | 10.428 | 9.237 | 7.495 | 5.037 | 1.174 | Primary | 2853
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - System Transformation | 18.223 | 18.133 | 17.992 | 17.833 | 17.648 | 17.441 | 17.203 | 15.789 | 13.114 | 10.238 | 6.131 | Primary | 2854
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - System Transformation | 8.575 | 8.604 | 7.162 | 7.134 | 7.077 | 6.991 | 6.856 | 5.99 | 4.277 | 2.645 | 0.563 | Primary | 2855
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - System Transformation | 25.817 | 25.847 | 25.855 | 25.836 | 25.786 | 25.703 | 25.585 | 24.588 | 23.065 | 22.172 | 21.51 | Primary | 2856
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - System Transformation | 14.47 | 14.012 | 14.034 | 14.046 | 14.04 | 14.02 | 13.974 | 13.63 | 12.704 | 11.356 | 9.277 | Primary | 2857
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - System Transformation | 4.788 | 4.53 | 4.13 | 3.651 | 3.069 | 2.387 | 1.601 | -3.1 | -7.487 | -9.755 | -11.119 | Primary | 2858
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - System Transformation | 15.695 | 15.768 | 15.824 | 15.863 | 15.888 | 15.9 | 15.896 | 15.75 | 15.074 | 14.383 | 13.653 | Primary | 2859
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 7.391 | 6.885 | 6.482 | 6.073 | 5.632 | 5.159 | 4.624 | 17.921 | 14.755 | 11.119 | 6.07 | Primary | 2860
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary | 2861
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - System Transformation | 2.41 | 2.379 | 2.301 | 2.21 | 2.098 | 1.969 | 1.796 | 0.787 | -1.417 | -4.457 | -9.249 | Primary | 2862
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - System Transformation | 14.24 | 13.944 | 13.567 | 13.19 | 12.775 | 12.331 | 11.843 | 9.321 | 5.897 | 2.847 | -0.89 | Primary | 2863
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - System Transformation | 14.901 | 12.46 | 12.443 | 12.41 | 12.341 | 12.241 | 12.114 | 11.244 | 9.553 | 7.913 | 5.658 | Primary | 2864
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - System Transformation | 8.524 | 7.812 | 7.326 | 6.887 | 6.397 | 5.869 | 5.259 | 2.101 | -3.468 | -9.193 | -16.84 | Primary | 2865
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - System Transformation | 18.387 | 18.295 | 18.181 | 18.08 | 17.964 | 17.838 | 17.685 | 16.921 | 15.33 | 13.65 | 11.474 | Primary | 2866
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - System Transformation | 10.933 | 10.556 | 10.051 | 9.537 | 8.975 | 8.381 | 7.71 | 4.448 | -0.226 | -5.705 | -13.637 | Primary | 2867
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - System Transformation | 3.403 | 2.648 | 2.119 | 1.559 | 0.942 | 0.264 | -0.51 | -4.332 | -8.547 | -13.361 | -19.887 | Primary | 2868
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - System Transformation | 2.594 | 2.263 | 1.868 | 1.522 | 1.149 | 0.755 | 0.33 | -1.668 | -3.954 | -6.81 | -10.95 | Primary | 2869
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - System Transformation | 8.507 | 8.495 | 8.469 | 8.432 | 8.38 | 8.311 | 8.215 | 7.582 | 6.716 | 5.985 | 5.146 | Primary | 2870
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - System Transformation | 21.008 | 20.735 | 20.727 | 20.713 | 20.695 | 20.673 | 20.64 | 20.508 | 19.874 | 19.237 | 18.463 | Primary | 2871
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - System Transformation | 19.154 | 19.06 | 18.914 | 18.756 | 18.576 | 18.372 | 18.103 | 16.747 | 14.702 | 12.019 | 8.04 | Primary | 2872
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - System Transformation | 14.515 | 14.619 | 14.713 | 14.797 | 14.872 | 14.939 | 14.996 | 15.178 | 15.17 | 15.141 | 15.111 | Primary | 2873
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - System Transformation | 14.558 | 14.623 | 14.657 | 14.683 | 14.683 | 14.661 | 14.611 | 14.176 | 13.189 | 12.308 | 11.277 | Primary | 2874
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - System Transformation | 1.053 | 1.053 | 0.998 | 0.888 | 20.607 | 20.352 | 20.022 | 17.246 | 12.701 | 8.957 | 4.346 | Primary | 2875
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - System Transformation | 7.46 | 7.163 | 6.789 | 6.418 | 6.017 | 5.6 | 5.157 | 2.93 | -0.302 | -3.973 | -9.206 | Primary | 2876
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - System Transformation | 6.799 | 6.506 | 6.114 | 5.719 | 5.283 | 4.811 | 4.26 | 1.512 | -1.749 | -5.226 | -9.879 | Primary | 2877
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - System Transformation | 16.187 | 16.079 | 15.935 | 15.78 | 15.608 | 15.422 | 15.224 | 14.085 | 12.336 | 10.647 | 8.39 | Primary | 2878
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - System Transformation | 6.592 | 6.456 | 6.28 | 6.11 | 5.916 | 5.704 | 5.472 | 4.255 | 2.152 | -0.023 | -2.824 | Primary | 2879
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 1.615 | 1.127 | 0.549 | 0.01 | -0.574 | -1.188 | -1.85 | -5.198 | -9.833 | -14.122 | -19.484 | Primary | 2880
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - System Transformation | 18.405 | 18.393 | 18.365 | 18.329 | 18.284 | 18.23 | 18.164 | 17.748 | 17.044 | 16.294 | 15.23 | Primary | 2881
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - System Transformation | 6.495 | 6.272 | 5.984 | 5.716 | 5.422 | 5.106 | 4.756 | 3.087 | 1.063 | -1.644 | -5.792 | Primary | 2882
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - System Transformation | 2.764 | 2.747 | 2.724 | 2.703 | 2.679 | 2.653 | 2.621 | 2.46 | 2.183 | 1.96 | 1.701 | Primary | 2883
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - System Transformation | 9.072 | 8.734 | 8.627 | 8.508 | 8.365 | 8.202 | 8.009 | 6.821 | 4.668 | 2.391 | -0.68 | Primary | 2884
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - System Transformation | 14.227 | 14.058 | 13.835 | 13.613 | 13.37 | 13.113 | 12.833 | 11.428 | 9.401 | 7.328 | 4.543 | Primary | 2885
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - System Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 2886
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - System Transformation | 20.768 | 20.631 | 20.461 | 20.306 | 20.133 | 19.949 | 19.743 | 18.684 | 16.724 | 14.676 | 11.834 | Primary | 2887
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - System Transformation | 8.245 | 8.057 | 7.813 | 7.582 | 7.327 | 7.055 | 6.739 | 5.111 | 2.482 | -0.962 | -6.226 | Primary | 2888
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - System Transformation | 14.21 | 14.043 | 13.825 | 13.601 | 13.353 | 13.089 | 12.789 | 11.218 | 8.76 | 5.957 | 1.977 | Primary | 2889
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - System Transformation | 33.135 | 32.752 | 32.726 | 32.701 | 32.668 | 32.631 | 32.583 | 32.388 | 31.861 | 31.31 | 30.596 | Primary | 2890
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - System Transformation | 4.299 | 3.616 | 3.17 | 2.707 | 2.202 | 1.671 | 1.061 | -1.69 | -5.223 | -9.378 | -15.386 | Primary | 2891
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - System Transformation | 14.467 | 13.754 | 13.495 | 13.2 | 12.867 | 12.484 | 12.015 | 17.37 | 13.096 | 8.589 | 3.147 | Primary | 2892
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - System Transformation | 9.389 | 9.219 | 8.989 | 8.741 | 8.452 | 8.135 | 7.789 | 5.704 | 1.87 | -2.071 | -7.267 | Primary | 2893
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - System Transformation | 15.338 | 15.297 | 15.24 | 15.175 | 15.097 | 15.008 | 14.899 | 14.226 | 12.898 | 11.469 | 9.581 | Primary | 2894
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 24.288 | 22.484 | 22.157 | 21.836 | 21.494 | 21.137 | 20.758 | 19.05 | 16.936 | 14.673 | 11.387 | Primary | 2895
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - System Transformation | 5.141 | 4.589 | 4.221 | 3.841 | 3.431 | 3 | 2.552 | 0.142 | -3.762 | -8.084 | -13.98 | Primary | 2896
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - System Transformation | 1.38 | 0.662 | 0.221 | -0.203 | -0.662 | -1.145 | -1.68 | -4.368 | -8.744 | -13.867 | -21.371 | Primary | 2897
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - System Transformation | 3.099 | 3.046 | 1.658 | 1.57 | 1.471 | 1.363 | 1.245 | 0.68 | 0.138 | -0.33 | -0.851 | Primary | 2898
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - System Transformation | 7.396 | 6.892 | 8.564 | 8.264 | 7.923 | 7.556 | 7.161 | 4.962 | 0.908 | -3.178 | -8.832 | Primary | 2899
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - System Transformation | 5.57 | 5.558 | 5.498 | 5.415 | 5.306 | 5.174 | 4.981 | 3.686 | 0.218 | -4.146 | -10.885 | Primary | 2900
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - System Transformation | 32.093 | 30.698 | 30.607 | 30.505 | 30.386 | 30.253 | 30.116 | 29.266 | 27.999 | 26.458 | 24.118 | Primary | 2901
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - System Transformation | 12.169 | 12.028 | 11.831 | 11.622 | 11.391 | 11.149 | 10.902 | 9.491 | 6.739 | 3.669 | -0.925 | Primary | 2902
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - System Transformation | 8.724 | 7.951 | 7.635 | 7.384 | 7.111 | 6.827 | 6.539 | 5.278 | 3.645 | 1.687 | -1.176 | Primary | 2903
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - System Transformation | 6.45 | 6.517 | 6.563 | 6.594 | 6.608 | 6.605 | 6.578 | 6.252 | 5.319 | 4.155 | 2.483 | Primary | 2904
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - System Transformation | 13.458 | 13.405 | 13.313 | 13.199 | 13.065 | 12.917 | 12.752 | 11.78 | 9.358 | 7.04 | 3.954 | Primary | 2905
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 14.554 | 14.476 | 14.348 | 14.166 | 13.919 | 13.602 | 13.203 | 10.417 | 6.466 | 3.778 | 1.501 | Primary | 2906
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 12.874 | 12.733 | 12.564 | 12.376 | 12.167 | 11.942 | 11.692 | 10.211 | 7.166 | 3.702 | -0.874 | Primary | 2907
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - System Transformation | 4.471 | 3.409 | 3.088 | 2.743 | 2.366 | 1.959 | 1.49 | -0.942 | -4.634 | -8.679 | -13.666 | Primary | 2908
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - System Transformation | 4.628 | 3.117 | 2.135 | 1.107 | 0.02 | -1.142 | -2.472 | -8.674 | -14.181 | -21.88 | -32.813 | Primary | 2909
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - System Transformation | 11.47 | 10.599 | 10.177 | 9.846 | 9.487 | 9.112 | 8.682 | 6.763 | 4.081 | 1.265 | -2.527 | Primary | 2910
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - System Transformation | 15.733 | 14.949 | 14.623 | 14.285 | 13.913 | 13.519 | 13.095 | 10.898 | 7.482 | 3.614 | -2.173 | Primary | 2911
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - System Transformation | 8.059 | 7.903 | 7.659 | 7.389 | 7.088 | 6.766 | 6.417 | 4.5 | 1.477 | -1.892 | -6.923 | Primary | 2912
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - System Transformation | 12.723 | 12.735 | 12.74 | 12.74 | 12.734 | 12.724 | 12.707 | 12.566 | 12.265 | 11.977 | 11.694 | Primary | 2913
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - System Transformation | 21.642 | 21.577 | 21.479 | 21.369 | 21.247 | 21.109 | 20.935 | 19.991 | 18.919 | 17.425 | 15.256 | Primary | 2914
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - System Transformation | 14.974 | 15.079 | 15.168 | 15.244 | 15.305 | 15.354 | 15.384 | 15.402 | 14.541 | 13.758 | 12.827 | Primary | 2915
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 10.632 | 10.317 | 9.918 | 9.521 | 9.091 | 8.637 | 8.135 | 5.61 | 2.165 | -1.927 | -7.755 | Primary | 2916
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 21.862 | 21.827 | 21.78 | 21.733 | 21.679 | 21.618 | 21.546 | 21.167 | 20.569 | 19.87 | 18.946 | Primary | 2917
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - System Transformation | 2.505 | 2.325 | 2.06 | 1.78 | 1.468 | 1.132 | 0.76 | -1.198 | -4.235 | -8.208 | -14.245 | Primary | 2918
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - System Transformation | 6.594 | 6.583 | 6.568 | 6.553 | 6.534 | 6.515 | 6.493 | 6.367 | 6.086 | 5.804 | 5.414 | Primary | 2919
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - System Transformation | 5.994 | 5.258 | 5.073 | 4.905 | 4.713 | 4.503 | 4.253 | 3.116 | 1.53 | -0.616 | -3.735 | Primary | 2920
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - System Transformation | 11.904 | 11.389 | 10.702 | 9.969 | 9.158 | 8.283 | 7.324 | 1.974 | -5.51 | -13.512 | -24.782 | Primary | 2921
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - System Transformation | 10.424 | 8.98 | 8.203 | 7.839 | 7.424 | 6.971 | 6.471 | 3.78 | -0.564 | -5.119 | -11.508 | Primary | 2922
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - System Transformation | 15.093 | 14.896 | 14.663 | 14.424 | 14.161 | 13.881 | 13.582 | 11.876 | 9.264 | 6.797 | 3.769 | Primary | 2923
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - System Transformation | 15.882 | 15.787 | 15.682 | 15.574 | 15.459 | 15.338 | 15.21 | 14.566 | 13.833 | 13.115 | 12.37 | Primary | 2924
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - System Transformation | 2.003 | 1.663 | 22.821 | 22.65 | 22.432 | 22.168 | 21.821 | 19.656 | 16.143 | 12.91 | 8.973 | Primary | 2925
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - System Transformation | 13.621 | 13.095 | 12.739 | 12.389 | 12.011 | 11.618 | 11.199 | 9.293 | 7.531 | 5.848 | 3.645 | Primary | 2926
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - System Transformation | 3.222 | 3.036 | 2.806 | 2.578 | 2.34 | 2.095 | 1.843 | 0.608 | -0.77 | -2.342 | -4.549 | Primary | 2927
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - System Transformation | 2.781 | 2.628 | 2.443 | 2.26 | 2.06 | 1.848 | 1.622 | 0.416 | -1.122 | -2.507 | -4.165 | Primary | 2928
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 12.326 | 11.721 | 11.406 | 11.061 | 10.673 | 10.253 | 9.766 | 7.215 | 2.539 | -2.255 | -8.928 | Primary | 2929
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - System Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2930
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - System Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2931
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - System Transformation | 17.574 | 17.057 | 16.887 | 16.713 | 16.518 | 16.308 | 16.077 | 14.845 | 12.559 | 9.953 | 6.183 | Primary | 2932
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - System Transformation | 11.117 | 10.005 | 9.851 | 9.682 | 9.487 | 9.269 | 9.027 | 7.769 | 6.193 | 4.873 | 3.483 | Primary | 2933
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - System Transformation | 10.407 | 10.235 | 10.01 | 9.794 | 9.55 | 9.282 | 8.972 | 7.325 | 4.856 | 2.074 | -1.894 | Primary | 2934
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - System Transformation | 12.895 | 12.611 | 12.273 | 11.964 | 11.626 | 11.269 | 10.888 | 8.905 | 6.236 | 3.701 | 0.46 | Primary | 2935
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - System Transformation | 10.428 | 9.621 | 9.413 | 9.182 | 8.927 | 8.653 | 8.361 | 6.757 | 4.284 | 1.483 | -2.489 | Primary | 2936
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - System Transformation | 10.284 | 10.193 | 10.051 | 9.895 | 9.71 | 9.5 | 9.251 | 7.804 | 5.391 | 2.589 | -1.591 | Primary | 2937
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - System Transformation | 16.763 | 15.988 | 15.984 | 15.964 | 15.921 | 15.858 | 15.762 | 15.094 | 13.273 | 11.398 | 8.866 | Primary | 2938
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - System Transformation | 15.671 | 15.399 | 15.045 | 14.686 | 14.275 | 13.819 | 13.298 | 10.359 | 6.227 | 2.203 | -3.056 | Primary | 2939
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | 5.515 | 5.369 | 5.176 | 4.986 | 4.778 | 4.56 | 4.328 | 3.171 | 1.839 | 0.647 | -0.946 | Primary | 2940
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - System Transformation | 12.362 | 11.991 | 10.229 | 9.905 | 9.528 | 9.085 | 8.511 | 5.422 | 1.409 | -3.444 | -10.194 | Primary | 2941
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - System Transformation | 23.15 | 13.658 | 2.812 | 2.367 | 1.857 | 1.291 | 0.622 | -2.389 | -6.464 | -10.817 | -16.535 | Primary | 2942
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - System Transformation | 0.555 | -0.221 | -0.81 | -3.12 | -3.719 | -4.346 | -5.028 | -8.256 | -12.714 | -17.467 | -24.204 | Primary | 2943
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - System Transformation | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary | 2944
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - System Transformation | 3.203 | 3.064 | 2.898 | 2.718 | 2.515 | 2.293 | 2.043 | 0.52 | -2.095 | -4.802 | -8.255 | Primary | 2945
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - System Transformation | 11.949 | 11.155 | 10.886 | 10.595 | 10.273 | 9.897 | 9.393 | 6.76 | 4.067 | 0.455 | -4.435 | Primary | 2946
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 5.804 | 4.195 | 4.133 | 4.04 | 3.91 | 3.75 | 3.528 | 2.327 | -0.479 | -3.311 | -7.114 | Primary | 2947
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 27.947 | 27.964 | 27.98 | 27.994 | 28.006 | 28.018 | 28.027 | 28.06 | 28.07 | 28.073 | 28.077 | Primary | 2948
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - System Transformation | 19.937 | 18.929 | 18.632 | 18.32 | 17.983 | 17.631 | 17.254 | 15.395 | 12.785 | 9.688 | 5.148 | Primary | 2949
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - System Transformation | 8.273 | 7.619 | 7.719 | 7.756 | 7.716 | 7.596 | 7.387 | 5.554 | 2.708 | 0.963 | -0.417 | Primary | 2950
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - System Transformation | 3.069 | 2.909 | 2.809 | 2.699 | 2.58 | 2.451 | 2.312 | 1.579 | 0.667 | -0.288 | -1.251 | Primary | 2951
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - System Transformation | 13.774 | 13.504 | 13.165 | 12.844 | 12.499 | 12.142 | 11.764 | 9.744 | 6.355 | 1.978 | -4.971 | Primary | 2952
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - System Transformation | 2.25 | 1.912 | 1.494 | 1.065 | 0.596 | 0.099 | -0.436 | -3.295 | -7.183 | -10.771 | -15.187 | Primary | 2953
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - System Transformation | 7.735 | 6.803 | 6.489 | 6.171 | 5.826 | 5.462 | 5.062 | 3.274 | 1.541 | -0.258 | -2.489 | Primary | 2954
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 23.467 | 22.927 | 22.502 | 22.051 | 21.56 | 21.04 | 20.484 | 17.491 | 12.794 | 7.754 | 0.676 | Primary | 2955
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - System Transformation | 11.164 | 10.98 | 10.696 | 10.388 | 10.043 | 9.662 | 9.199 | 6.864 | 3.454 | -0.75 | -7.039 | Primary | 2956
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - System Transformation | 11.091 | 10.801 | 10.432 | 10.064 | 9.667 | 9.246 | 8.777 | 6.324 | 2.346 | -2.027 | -8.349 | Primary | 2957
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - System Transformation | 12.799 | 12.594 | 12.683 | 12.758 | 12.815 | 12.857 | 12.875 | 12.798 | 11.901 | 10.929 | 9.605 | Primary | 2958
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - System Transformation | 5.864 | 5.376 | 4.816 | 4.291 | 3.731 | 3.152 | 2.56 | -0.56 | -5.244 | -10.422 | -17.599 | Primary | 2959
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - System Transformation | 8.49 | 6.878 | 6.776 | 6.658 | 6.509 | 6.336 | 6.143 | 4.944 | 3.021 | 1.126 | -1.568 | Primary | 2960
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - System Transformation | 7.743 | 7.006 | 6.683 | 6.339 | 5.967 | 5.577 | 5.179 | 3.045 | -0.222 | -4.034 | -9.688 | Primary | 2961
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - System Transformation | 31.094 | 31.1 | 31.106 | 31.111 | 31.116 | 31.12 | 31.123 | 31.129 | 31.116 | 31.092 | 31.052 | Primary | 2962
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - System Transformation | 10.261 | 10.262 | 10.241 | 10.21 | 25.57 | 25.519 | 25.45 | 25.029 | 23.971 | 22.54 | 20.314 | Primary | 2963
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - System Transformation | 7.518 | 5.782 | 20.348 | 19.942 | 19.491 | 19.013 | 18.502 | 16.053 | 11.972 | 7.91 | 2.283 | Primary | 2964
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - System Transformation | 8.919 | 8.661 | 8.344 | 8.009 | 7.642 | 7.247 | 6.802 | 4.409 | 0.981 | -2.198 | -6.004 | Primary | 2965
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - System Transformation | 11.646 | 11.516 | 11.351 | 11.192 | 11.026 | 10.856 | 10.689 | 9.898 | 9.064 | 8.04 | 6.455 | Primary | 2966
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - System Transformation | 19.87 | 19.32 | 19.232 | 19.141 | 19.032 | 18.912 | 18.787 | 17.969 | 16.128 | 13.957 | 10.601 | Primary | 2967
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - System Transformation | 10.494 | 10.075 | 9.568 | 9.128 | 8.64 | 8.116 | 7.533 | 4.561 | 0.703 | -3.258 | -8.742 | Primary | 2968
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - System Transformation | 11.874 | 11.5 | 11.248 | 10.977 | 10.684 | 10.377 | 10.061 | 8.355 | 5.621 | 2.018 | -3.539 | Primary | 2969
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - System Transformation | 10.868 | 10.28 | 9.946 | 9.6 | 9.225 | 8.836 | 8.432 | 6.418 | 3.548 | 0.403 | -4.323 | Primary | 2970
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 13.893 | 13.895 | 13.885 | 13.869 | 13.845 | 13.814 | 13.772 | 13.472 | 12.611 | 11.722 | 10.494 | Primary | 2971
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 14.088 | 14.089 | 14.078 | 14.056 | 14.022 | 13.978 | 13.915 | 13.501 | 12.454 | 11.502 | 10.354 | Primary | 2972
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 18.643 | 18.56 | 18.441 | 18.317 | 18.18 | 18.031 | 17.858 | 17.002 | 15.875 | 14.744 | 13.208 | Primary | 2973
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 18.855 | 18.786 | 18.687 | 18.581 | 18.464 | 18.336 | 18.179 | 17.403 | 16.047 | 14.609 | 12.642 | Primary | 2974
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - System Transformation | 12.082 | 11.827 | 11.503 | 11.172 | 10.821 | 10.459 | 10.1 | 8.183 | 5.007 | 1.283 | -4.436 | Primary | 2975
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 22.041 | 21.705 | 21.314 | 20.986 | 20.627 | 20.245 | 19.812 | 17.666 | 14.706 | 11.62 | 7.404 | Primary | 2976
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - System Transformation | 26.933 | 25.969 | 25.845 | 25.713 | 25.566 | 25.404 | 25.225 | 24.475 | 23.777 | 23.138 | 22.519 | Primary | 2977
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - System Transformation | 5.578 | 5.16 | 5.13 | 5.102 | 5.068 | 5.031 | 4.986 | 4.771 | 4.365 | 3.94 | 3.381 | Primary | 2978
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - System Transformation | 11.105 | 11.115 | 11.105 | 11.087 | 11.056 | 11.013 | 10.958 | 10.539 | 9.188 | 7.614 | 5.344 | Primary | 2979
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NPg Best View | 5.51 | 5.197 | 4.632 | 3.984 | 3.564 | 3.259 | 2.906 | 1.4 | -3.973 | -8.153 | -12.558 | Primary | 2980
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NPg Best View | 11.026 | 10.115 | 7.989 | 6.903 | 6.114 | 5.453 | 4.683 | 1.443 | -7.304 | -13.903 | -20.449 | Primary | 2981
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 8.045 | 7.734 | 9.197 | 8.59 | 8.145 | 7.758 | 7.306 | 5.22 | 0.19 | -3.669 | -7.587 | Primary | 2982
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NPg Best View | 5.805 | 5.594 | 5.161 | 4.65 | 4.306 | 4.029 | 3.694 | 2.216 | -2.97 | -7.101 | -11.272 | Primary | 2983
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NPg Best View | 22.754 | 22.804 | 22.85 | 22.893 | 22.932 | 22.967 | 22.997 | 23.055 | 23.057 | 23.06 | 23.062 | Primary | 2984
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NPg Best View | 2.119 | 2.125 | 2.047 | 1.935 | 1.873 | 1.823 | 1.741 | 1.282 | -0.598 | -2.049 | -3.518 | Primary | 2985
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NPg Best View | 3.674 | 3.644 | 3.604 | 3.565 | 3.528 | 3.49 | 3.444 | 3.2 | 2.883 | 2.641 | 2.417 | Primary | 2986
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NPg Best View | 2.697 | 2.572 | 2.348 | 2.076 | 1.831 | 1.593 | 1.31 | -0.219 | -3.248 | -5.621 | -7.988 | Primary | 2987
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NPg Best View | 7.3 | 7.245 | 7.051 | 6.821 | 6.646 | 6.514 | 6.352 | 5.601 | 2.493 | -0.007 | -2.6 | Primary | 2988
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NPg Best View | 12.044 | 11.846 | 11.492 | 11.088 | 10.823 | 10.57 | 10.228 | 8.467 | 5.125 | 2.851 | 0.705 | Primary | 2989
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NPg Best View | 4.834 | 4.277 | 3.802 | 3.288 | 2.865 | 2.474 | 2.017 | -0.055 | -6.084 | -11.036 | -15.833 | Primary | 2990
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NPg Best View | 11.088 | 10.575 | 10.265 | 9.897 | 9.638 | 9.417 | 9.146 | 7.806 | 3.096 | -0.714 | -4.506 | Primary | 2991
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NPg Best View | 7.54 | 7.196 | 6.683 | 6.115 | 5.67 | 5.24 | 4.732 | 2.104 | -2.337 | -5.557 | -8.731 | Primary | 2992
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NPg Best View | 3.6 | 2.969 | 2.548 | 2.075 | 1.74 | 1.439 | 1.077 | -0.649 | -5.48 | -9.304 | -13.05 | Primary | 2993
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 13.317 | 13.171 | 12.875 | 12.523 | 12.169 | 11.777 | 10.692 | 6.513 | 3.624 | 1.905 | 0.4 | Primary | 2994
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 16.539 | 16.574 | 16.537 | 16.437 | 16.318 | 16.193 | 16.049 | 15.329 | 14.256 | 13.757 | 13.353 | Primary | 2995
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NPg Best View | 9.565 | 8.691 | 8.526 | 8.318 | 8.112 | 7.893 | 7.62 | 6.156 | 2.149 | -0.97 | -3.813 | Primary | 2996
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NPg Best View | 10.219 | 9.617 | 9.232 | 8.805 | 8.437 | 8.09 | 7.691 | 5.824 | 0.739 | -3.408 | -7.326 | Primary | 2997
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NPg Best View | 15.6 | 15.406 | 15.081 | 14.723 | 14.454 | 14.211 | 13.92 | 12.657 | 9.095 | 6.216 | 3.462 | Primary | 2998
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NPg Best View | 7.142 | 7.02 | 6.798 | 6.488 | 6.157 | 5.761 | 5.262 | 2.11 | -1.561 | -3.67 | -5.459 | Primary | 2999
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NPg Best View | 20.281 | 20.013 | 19.612 | 19.172 | 18.75 | 18.324 | 17.827 | 15.193 | 10.314 | 6.548 | 2.95 | Primary | 3000
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 17.817 | 17.71 | 17.53 | 17.325 | 17.138 | 16.951 | 16.729 | 15.611 | 12.86 | 10.506 | 8.238 | Primary | 3001
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NPg Best View | 11.858 | 11.154 | 10.46 | 9.671 | 9.112 | 8.63 | 8.076 | 5.52 | -0.976 | -6.044 | -11.108 | Primary | 3002
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NPg Best View | 7.9 | 7.404 | 7.301 | 7.174 | 7.098 | 7.05 | 6.981 | 6.645 | 4.675 | 3.124 | 1.555 | Primary | 3003
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NPg Best View | 8.847 | 8.521 | 7.904 | 7.181 | 6.65 | 6.204 | 5.661 | 2.902 | -3.239 | -7.589 | -12.112 | Primary | 3004
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NPg Best View | 7.044 | 6.482 | 5.957 | 5.427 | 5.022 | 4.675 | 4.257 | 2.372 | -1.558 | -4.439 | -7.287 | Primary | 3005
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NPg Best View | 8.134 | 7.911 | 7.511 | 7.052 | 6.7 | 6.405 | 6.054 | 4.373 | -0.209 | -3.678 | -7.094 | Primary | 3006
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NPg Best View | 8.079 | 7.909 | 7.575 | 7.198 | 6.843 | 6.515 | 6.135 | 4.432 | -0.056 | -3.697 | -7.145 | Primary | 3007
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NPg Best View | 4.063 | 3.841 | 3.392 | 2.858 | 2.454 | 2.09 | 1.657 | -0.372 | -6.212 | -10.81 | -15.262 | Primary | 3008
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NPg Best View | 7.87 | 7.567 | 7.113 | 6.601 | 6.168 | 5.766 | 5.304 | 3.073 | -1.83 | -5.888 | -9.925 | Primary | 3009
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NPg Best View | 8.516 | 8.41 | 8.552 | 8.653 | 8.754 | 8.846 | 8.9 | 9.015 | 7.357 | 6.071 | 4.826 | Primary | 3010
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NPg Best View | 5.625 | 4.728 | 4.468 | 4.2 | 3.967 | 3.74 | 3.455 | 2.21 | -0.599 | -2.795 | -4.887 | Primary | 3011
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NPg Best View | 14.741 | 13.495 | 12.788 | 11.939 | 11.313 | 10.753 | 10.087 | 6.864 | -0.301 | -5.529 | -10.738 | Primary | 3012
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NPg Best View | 12.882 | 12.895 | 12.843 | 12.767 | 12.731 | 12.71 | 12.666 | 12.427 | 11.089 | 10.061 | 8.991 | Primary | 3013
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NPg Best View | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.499 | 7.498 | 7.498 | 7.498 | Primary | 3014
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 12.679 | 12.709 | 12.678 | 12.61 | 12.567 | 12.528 | 12.463 | 12.03 | 10.278 | 8.954 | 7.667 | Primary | 3015
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 14.7 | 14.662 | 14.546 | 14.38 | 14.255 | 14.132 | 13.969 | 12.919 | 10.561 | 8.909 | 7.291 | Primary | 3016
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NPg Best View | 4.505 | 4.467 | 4.395 | 4.317 | 4.273 | 4.25 | 4.224 | 4.082 | 3.049 | 2.178 | 1.242 | Primary | 3017
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NPg Best View | 8.985 | 8.848 | 8.634 | 8.402 | 8.255 | 8.131 | 7.986 | 7.3 | 5.229 | 3.616 | 2.019 | Primary | 3018
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NPg Best View | 8.401 | 8.247 | 7.93 | 7.574 | 7.3 | 7.052 | 6.752 | 5.312 | 0.551 | -3.234 | -6.826 | Primary | 3019
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 23.172 | 22.924 | 22.911 | 22.89 | 22.876 | 22.863 | 22.834 | 22.704 | 21.498 | 20.497 | 19.585 | Primary | 3020
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NPg Best View | 6.878 | 6.833 | 6.657 | 6.432 | 6.244 | 6.042 | 5.767 | 4.187 | 0.585 | -1.919 | -4.199 | Primary | 3021
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NPg Best View | 5.159 | 4.4 | 3.771 | 3.037 | 2.446 | 1.894 | 1.226 | -1.971 | -7.751 | -11.647 | -15.388 | Primary | 3022
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NPg Best View | 9.993 | 8.771 | 8.355 | 7.867 | 7.487 | 7.145 | 6.736 | 4.776 | -1.289 | -6.002 | -10.526 | Primary | 3023
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 8.711 | 8.639 | 8.459 | 8.26 | 8.079 | 7.886 | 7.629 | 6.332 | 3.427 | 1.196 | -0.807 | Primary | 3024
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 13.465 | 13.259 | 12.882 | 12.479 | 12.175 | 11.899 | 11.56 | 9.963 | 4.602 | 0.185 | -4.008 | Primary | 3025
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NPg Best View | 4.323 | 3.915 | 3.831 | 3.715 | 3.632 | 3.563 | 3.462 | 2.952 | 0.661 | -1.237 | -3.155 | Primary | 3026
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NPg Best View | 8.144 | 7.885 | 7.37 | 6.75 | 6.227 | 5.732 | 5.139 | 2.177 | -6.037 | -12.5 | -18.59 | Primary | 3027
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NPg Best View | 18.041 | 18.051 | 18.025 | 17.985 | 17.959 | 17.939 | 17.909 | 17.736 | 16.556 | 15.538 | 14.544 | Primary | 3028
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NPg Best View | 6.704 | 6.588 | 6.346 | 6.08 | 5.91 | 5.772 | 5.579 | 4.527 | 1.776 | -0.258 | -2.33 | Primary | 3029
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NPg Best View | 9.03 | 9.048 | 9.024 | 8.978 | 8.925 | 8.858 | 8.758 | 8.136 | 7.121 | 6.429 | 5.782 | Primary | 3030
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NPg Best View | 0.566 | 0.447 | 0.125 | -0.28 | -0.553 | -0.759 | -1.015 | 14.919 | 10.039 | 6.119 | 2.139 | Primary | 3031
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NPg Best View | 5.645 | 5.108 | 4.377 | 3.716 | 3.216 | 2.717 | 2.09 | -0.968 | -6.395 | -10.281 | -13.842 | Primary | 3032
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NPg Best View | 10.209 | 9.796 | 8.394 | 7.642 | 7.093 | 6.634 | 6.104 | 3.649 | -2.391 | -6.949 | -11.659 | Primary | 3033
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NPg Best View | 14.428 | 14.155 | 14.131 | 14.072 | 13.988 | 13.88 | 13.724 | 12.843 | 11.34 | 10.295 | 9.348 | Primary | 3034
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NPg Best View | 7.425 | 6.068 | 5.732 | 5.3 | 4.991 | 4.726 | 4.382 | 2.605 | -4.434 | -9.96 | -15.318 | Primary | 3035
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NPg Best View | 7.371 | 7.009 | 6.415 | 5.741 | 5.261 | 4.836 | 4.321 | 1.759 | -4.144 | -8.663 | -13.163 | Primary | 3036
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NPg Best View | 29.132 | 28.763 | 28.194 | 27.644 | 27.249 | 26.883 | 26.409 | 23.958 | 19.659 | 16.686 | 13.789 | Primary | 3037
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NPg Best View | 5.222 | 5.018 | 4.635 | 4.189 | 3.858 | 3.577 | 3.243 | 1.676 | -2.755 | -6.265 | -9.818 | Primary | 3038
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NPg Best View | 11.724 | 11.526 | 11.183 | 10.819 | 10.581 | 10.406 | 10.205 | 9.423 | 6.672 | 4.504 | 2.185 | Primary | 3039
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NPg Best View | 18.307 | 18.241 | 18.055 | 17.83 | 17.636 | 17.459 | 17.249 | 16.189 | 12.666 | 9.867 | 7.204 | Primary | 3040
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NPg Best View | 8.667 | 8.705 | 7.219 | 7.116 | 7.042 | 6.972 | 6.862 | 6.216 | 4.333 | 3.02 | 1.737 | Primary | 3041
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NPg Best View | 25.882 | 25.946 | 25.97 | 25.95 | 25.89 | 25.784 | 25.628 | 24.531 | 23.318 | 22.751 | 22.373 | Primary | 3042
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NPg Best View | 14.614 | 14.181 | 14.174 | 14.142 | 14.167 | 14.221 | 14.254 | 14.368 | 13.228 | 12.32 | 11.252 | Primary | 3043
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NPg Best View | 4.944 | 4.788 | 4.432 | 3.96 | 3.381 | 2.669 | 1.757 | -3.276 | -6.959 | -8.438 | -9.303 | Primary | 3044
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NPg Best View | 15.891 | 16.079 | 16.236 | 16.37 | 16.493 | 16.604 | 16.691 | 17.034 | 16.811 | 16.608 | 16.373 | Primary | 3045
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 7.544 | 7.08 | 6.627 | 6.121 | 5.699 | 5.31 | 4.861 | 18.842 | 14.5 | 11.212 | 8.054 | Primary | 3046
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Primary | 3047
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NPg Best View | 2.498 | 2.398 | 2.14 | 1.838 | 1.677 | 1.589 | 1.487 | 1.035 | -2.348 | -5.069 | -7.979 | Primary | 3048
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NPg Best View | 14.392 | 14.129 | 13.715 | 13.264 | 12.9 | 12.547 | 12.119 | 9.912 | 6.228 | 3.618 | 1.116 | Primary | 3049
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NPg Best View | 15.046 | 12.707 | 12.736 | 12.736 | 12.71 | 12.669 | 12.578 | 12.092 | 10.299 | 8.966 | 7.739 | Primary | 3050
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NPg Best View | 8.828 | 8.166 | 7.579 | 6.968 | 6.505 | 6.1 | 5.608 | 3.282 | -3.158 | -8.174 | -13.173 | Primary | 3051
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NPg Best View | 18.52 | 18.462 | 18.336 | 18.206 | 18.119 | 18.052 | 17.962 | 17.535 | 15.843 | 14.491 | 13.094 | Primary | 3052
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NPg Best View | 11.098 | 10.603 | 9.823 | 8.971 | 8.388 | 7.924 | 7.376 | 4.812 | -1.587 | -6.42 | -11.514 | Primary | 3053
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NPg Best View | 3.595 | 2.869 | 2.224 | 1.468 | 0.838 | 0.244 | -0.45 | -3.486 | -9.399 | -13.712 | -17.823 | Primary | 3054
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NPg Best View | 2.775 | 2.428 | 1.925 | 1.427 | 1.076 | 0.791 | 0.445 | -1.077 | -4.403 | -6.855 | -9.405 | Primary | 3055
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NPg Best View | 8.522 | 8.491 | 8.42 | 8.329 | 8.242 | 8.153 | 8.042 | 7.369 | 6.406 | 5.846 | 5.319 | Primary | 3056
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NPg Best View | 21.03 | 20.757 | 20.734 | 20.695 | 20.671 | 20.656 | 20.638 | 20.57 | 19.808 | 19.194 | 18.601 | Primary | 3057
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NPg Best View | 19.24 | 19.092 | 18.804 | 18.472 | 18.244 | 18.074 | 17.87 | 16.951 | 13.844 | 11.486 | 9.021 | Primary | 3058
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NPg Best View | 14.645 | 14.829 | 14.997 | 15.151 | 15.294 | 15.424 | 15.537 | 16.015 | 16.332 | 16.6 | 16.839 | Primary | 3059
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NPg Best View | 14.754 | 14.911 | 14.996 | 15.051 | 15.121 | 15.183 | 15.202 | 15.148 | 14.129 | 13.46 | 12.79 | Primary | 3060
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NPg Best View | 1.172 | 1.197 | 1.076 | 0.848 | 20.502 | 20.187 | 19.76 | 16.912 | 12.026 | 8.804 | 5.955 | Primary | 3061
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NPg Best View | 7.597 | 7.29 | 6.797 | 6.273 | 5.879 | 5.539 | 5.147 | 3.425 | -0.852 | -4.198 | -7.594 | Primary | 3062
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NPg Best View | 6.959 | 6.659 | 6.164 | 5.602 | 5.181 | 4.795 | 4.334 | 2.163 | -2.113 | -5.084 | -7.946 | Primary | 3063
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NPg Best View | 16.258 | 16.201 | 16.087 | 15.959 | 15.815 | 15.659 | 15.472 | 14.526 | 12.516 | 10.901 | 9.439 | Primary | 3064
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NPg Best View | 6.745 | 6.661 | 6.475 | 6.278 | 6.104 | 5.946 | 5.751 | 4.896 | 2.492 | 0.662 | -1.115 | Primary | 3065
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 1.815 | 1.392 | 0.79 | 0.178 | -0.344 | -0.85 | -1.446 | -4.379 | -9.496 | -13.374 | -17.13 | Primary | 3066
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NPg Best View | 18.447 | 18.448 | 18.414 | 18.365 | 18.327 | 18.291 | 18.24 | 17.952 | 17.091 | 16.44 | 15.81 | Primary | 3067
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NPg Best View | 6.616 | 6.395 | 6.004 | 5.605 | 5.309 | 5.063 | 4.776 | 3.629 | 0.498 | -1.918 | -4.371 | Primary | 3068
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NPg Best View | 2.779 | 2.767 | 2.743 | 2.719 | 2.699 | 2.68 | 2.655 | 2.521 | 2.234 | 2.029 | 1.834 | Primary | 3069
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NPg Best View | 9.184 | 8.883 | 8.747 | 8.589 | 8.44 | 8.304 | 8.141 | 7.315 | 4.869 | 2.945 | 1.072 | Primary | 3070
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NPg Best View | 14.333 | 14.19 | 13.945 | 13.677 | 13.467 | 13.279 | 13.052 | 11.965 | 9.496 | 7.618 | 5.773 | Primary | 3071
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NPg Best View | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 3072
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NPg Best View | 20.844 | 20.707 | 20.483 | 20.249 | 20.074 | 19.922 | 19.741 | 18.88 | 16.37 | 14.423 | 12.5 | Primary | 3073
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NPg Best View | 8.382 | 8.132 | 7.701 | 7.243 | 6.963 | 6.763 | 6.527 | 5.484 | 1.596 | -1.451 | -4.672 | Primary | 3074
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NPg Best View | 14.295 | 14.082 | 13.729 | 13.336 | 13.068 | 12.845 | 12.584 | 11.342 | 8.039 | 5.531 | 2.979 | Primary | 3075
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NPg Best View | 33.177 | 32.805 | 32.773 | 32.732 | 32.709 | 32.696 | 32.673 | 32.587 | 31.984 | 31.517 | 31.045 | Primary | 3076
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NPg Best View | 4.452 | 3.696 | 3.043 | 2.324 | 1.807 | 1.393 | 0.901 | -1.2 | -6.143 | -9.752 | -13.501 | Primary | 3077
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NPg Best View | 14.598 | 13.882 | 13.553 | 13.154 | 12.786 | 12.422 | 12.01 | 17.804 | 13.037 | 9.205 | 5.379 | Primary | 3078
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NPg Best View | 9.592 | 9.558 | 9.4 | 9.211 | 8.976 | 8.731 | 8.434 | 6.901 | 2.345 | -1.346 | -4.741 | Primary | 3079
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NPg Best View | 15.414 | 15.39 | 15.316 | 15.222 | 15.149 | 15.085 | 15.004 | 14.554 | 13.059 | 11.866 | 10.662 | Primary | 3080
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 24.38 | 22.595 | 22.231 | 21.838 | 21.549 | 21.284 | 20.966 | 19.61 | 16.81 | 14.674 | 12.619 | Primary | 3081
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NPg Best View | 5.32 | 4.857 | 4.504 | 4.106 | 3.763 | 3.434 | 3.056 | 1.29 | -3.383 | -7.33 | -11.162 | Primary | 3082
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NPg Best View | 1.551 | 0.813 | 0.225 | -0.38 | -0.837 | -1.216 | -1.658 | -3.652 | -9.522 | -14.333 | -19.222 | Primary | 3083
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NPg Best View | 3.163 | 3.141 | 1.776 | 1.711 | 1.654 | 1.591 | 1.504 | 1.083 | 0.637 | 0.363 | 0.114 | Primary | 3084
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NPg Best View | 7.613 | 7.216 | 8.902 | 8.567 | 8.302 | 8.045 | 7.717 | 6.082 | 1.126 | -2.78 | -6.48 | Primary | 3085
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NPg Best View | 5.672 | 5.562 | 5.269 | 4.901 | 4.724 | 4.632 | 4.516 | 3.849 | -1.189 | -5.342 | -9.712 | Primary | 3086
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NPg Best View | 32.137 | 30.778 | 30.706 | 30.616 | 30.515 | 30.404 | 30.269 | 29.594 | 27.692 | 26.086 | 24.605 | Primary | 3087
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NPg Best View | 12.267 | 12.182 | 11.987 | 11.757 | 11.568 | 11.389 | 11.175 | 10.181 | 6.413 | 3.26 | 0.315 | Primary | 3088
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NPg Best View | 8.856 | 8.162 | 7.848 | 7.568 | 7.346 | 7.144 | 6.905 | 6.033 | 3.792 | 2.045 | 0.385 | Primary | 3089
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NPg Best View | 6.582 | 6.696 | 6.756 | 6.781 | 6.847 | 6.916 | 6.96 | 7.052 | 6.061 | 5.287 | 4.456 | Primary | 3090
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NPg Best View | 13.533 | 13.524 | 13.442 | 13.324 | 13.209 | 13.095 | 12.954 | 12.219 | 9.319 | 6.962 | 4.801 | Primary | 3091
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 14.737 | 14.747 | 14.666 | 14.493 | 14.253 | 13.925 | 13.484 | 10.655 | 7.501 | 5.685 | 4.195 | Primary | 3092
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 13.059 | 12.962 | 12.775 | 12.534 | 12.391 | 12.273 | 12.127 | 11.281 | 7.912 | 4.978 | 1.945 | Primary | 3093
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NPg Best View | 4.659 | 3.646 | 3.294 | 2.882 | 2.531 | 2.206 | 1.845 | 0.123 | -3.915 | -7.239 | -10.569 | Primary | 3094
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NPg Best View | 4.957 | 3.396 | 2.175 | 0.807 | -0.246 | -1.153 | -2.186 | -6.558 | -14.714 | -20.798 | -26.98 | Primary | 3095
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NPg Best View | 11.673 | 10.831 | 10.346 | 9.901 | 9.578 | 9.304 | 8.974 | 7.514 | 4.285 | 1.882 | -0.558 | Primary | 3096
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NPg Best View | 15.841 | 15.055 | 14.616 | 14.127 | 13.758 | 13.436 | 13.057 | 11.416 | 6.689 | 2.983 | -0.602 | Primary | 3097
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NPg Best View | 8.178 | 8.064 | 7.783 | 7.449 | 7.185 | 6.949 | 6.66 | 5.305 | 1.175 | -2.092 | -5.19 | Primary | 3098
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NPg Best View | 12.802 | 12.864 | 12.916 | 12.961 | 13 | 13.032 | 13.054 | 13.112 | 13.041 | 12.971 | 12.894 | Primary | 3099
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NPg Best View | 21.738 | 21.696 | 21.581 | 21.428 | 21.325 | 21.24 | 21.134 | 20.658 | 19.146 | 17.969 | 16.772 | Primary | 3100
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NPg Best View | 15.142 | 15.341 | 15.506 | 15.646 | 15.779 | 15.9 | 15.999 | 16.388 | 15.808 | 15.344 | 14.895 | Primary | 3101
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 10.755 | 10.402 | 9.847 | 9.248 | 8.789 | 8.394 | 7.947 | 5.977 | 1.16 | -2.558 | -6.302 | Primary | 3102
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 21.937 | 21.931 | 21.892 | 21.847 | 21.82 | 21.8 | 21.768 | 21.611 | 21.011 | 20.531 | 20.024 | Primary | 3103
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NPg Best View | 2.646 | 2.461 | 2.077 | 1.638 | 1.325 | 1.073 | 0.775 | -0.457 | -5.108 | -8.796 | -12.444 | Primary | 3104
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NPg Best View | 6.606 | 6.598 | 6.577 | 6.552 | 6.537 | 6.523 | 6.506 | 6.419 | 6.077 | 5.809 | 5.548 | Primary | 3105
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NPg Best View | 6.12 | 5.368 | 5.065 | 4.766 | 4.539 | 4.374 | 4.178 | 3.412 | 1.053 | -0.692 | -2.582 | Primary | 3106
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NPg Best View | 12.099 | 11.587 | 10.749 | 9.801 | 8.969 | 8.178 | 7.252 | 2.695 | -7.2 | -14.844 | -22.103 | Primary | 3107
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NPg Best View | 10.566 | 9.13 | 8.246 | 7.724 | 7.311 | 6.927 | 6.46 | 4.252 | -1.338 | -5.576 | -9.662 | Primary | 3108
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NPg Best View | 15.194 | 15.055 | 14.845 | 14.613 | 14.378 | 14.134 | 13.85 | 12.39 | 9.669 | 7.488 | 5.451 | Primary | 3109
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NPg Best View | 15.984 | 15.955 | 15.911 | 15.859 | 15.803 | 15.74 | 15.663 | 15.279 | 14.778 | 14.331 | 13.904 | Primary | 3110
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NPg Best View | 2.142 | 1.778 | 22.828 | 22.508 | 22.249 | 21.998 | 21.675 | 19.72 | 16.02 | 13.459 | 10.901 | Primary | 3111
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NPg Best View | 13.753 | 13.264 | 12.899 | 12.515 | 12.207 | 11.918 | 11.563 | 10.002 | 7.887 | 6.548 | 5.311 | Primary | 3112
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NPg Best View | 3.305 | 3.138 | 2.89 | 2.624 | 2.427 | 2.246 | 2.036 | 1.129 | -0.618 | -1.952 | -3.246 | Primary | 3113
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NPg Best View | 2.856 | 2.739 | 2.568 | 2.386 | 2.217 | 2.044 | 1.839 | 0.795 | -0.785 | -1.96 | -3.052 | Primary | 3114
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 12.485 | 11.909 | 11.524 | 11.06 | 10.694 | 10.371 | 9.978 | 8.047 | 2.117 | -2.58 | -7.112 | Primary | 3115
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NPg Best View | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 3116
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NPg Best View | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 3117
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NPg Best View | 17.692 | 17.209 | 17.006 | 16.768 | 16.602 | 16.46 | 16.284 | 15.512 | 12.537 | 10.137 | 7.792 | Primary | 3118
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NPg Best View | 11.241 | 10.209 | 10.117 | 9.997 | 9.86 | 9.701 | 9.495 | 8.456 | 6.907 | 5.737 | 4.67 | Primary | 3119
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NPg Best View | 10.522 | 10.321 | 9.968 | 9.592 | 9.323 | 9.098 | 8.824 | 7.499 | 4.221 | 1.811 | -0.666 | Primary | 3120
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NPg Best View | 13.052 | 12.821 | 12.482 | 12.144 | 11.858 | 11.583 | 11.252 | 9.617 | 6.696 | 4.503 | 2.378 | Primary | 3121
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NPg Best View | 10.549 | 9.799 | 9.599 | 9.352 | 9.143 | 8.945 | 8.707 | 7.593 | 4.442 | 1.857 | -0.622 | Primary | 3122
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NPg Best View | 10.371 | 10.245 | 9.979 | 9.665 | 9.45 | 9.273 | 9.052 | 7.953 | 4.651 | 2.105 | -0.494 | Primary | 3123
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NPg Best View | 16.893 | 16.153 | 16.141 | 16.09 | 16.069 | 16.058 | 16.015 | 15.68 | 13.602 | 11.954 | 10.321 | Primary | 3124
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NPg Best View | 15.836 | 15.557 | 15.08 | 14.546 | 14.128 | 13.726 | 13.233 | 10.661 | 5.851 | 2.44 | -0.876 | Primary | 3125
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | 5.614 | 5.522 | 5.366 | 5.194 | 5.058 | 4.92 | 4.741 | 3.825 | 2.333 | 1.281 | 0.319 | Primary | 3126
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NPg Best View | 12.532 | 12.124 | 10.164 | 9.541 | 9.088 | 8.693 | 8.223 | 6.044 | 0.32 | -3.82 | -7.899 | Primary | 3127
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NPg Best View | 23.294 | 13.78 | 2.638 | 1.954 | 1.41 | 0.919 | 0.331 | -2.133 | -7.074 | -10.746 | -14.412 | Primary | 3128
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NPg Best View | 0.835 | 0.105 | -0.57 | -3.026 | -3.547 | -3.998 | -4.549 | -6.955 | -12.403 | -16.585 | -20.762 | Primary | 3129
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NPg Best View | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | Primary | 3130
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NPg Best View | 3.307 | 3.181 | 2.983 | 2.744 | 2.556 | 2.374 | 2.16 | 0.933 | -2.013 | -4.385 | -6.714 | Primary | 3131
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NPg Best View | 12.117 | 11.335 | 10.967 | 10.498 | 10.132 | 9.809 | 9.44 | 7.781 | 3.779 | 0.842 | -2.067 | Primary | 3132
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 5.948 | 4.336 | 4.181 | 3.945 | 3.818 | 3.722 | 3.575 | 2.773 | -0.513 | -2.995 | -5.472 | Primary | 3133
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 27.967 | 27.997 | 28.024 | 28.049 | 28.072 | 28.094 | 28.112 | 28.193 | 28.257 | 28.31 | 28.358 | Primary | 3134
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NPg Best View | 20.025 | 18.997 | 18.591 | 18.139 | 17.805 | 17.52 | 17.193 | 15.793 | 12.165 | 9.297 | 6.413 | Primary | 3135
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NPg Best View | 8.53 | 8.027 | 8.23 | 8.33 | 8.343 | 8.254 | 8.035 | 6.348 | 4.359 | 3.538 | 3.012 | Primary | 3136
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NPg Best View | 3.242 | 3.207 | 3.229 | 3.239 | 3.237 | 3.222 | 3.188 | 2.973 | 2.624 | 2.242 | 1.854 | Primary | 3137
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NPg Best View | 13.887 | 13.571 | 13.072 | 12.543 | 12.196 | 11.924 | 11.606 | 10.148 | 4.907 | 0.585 | -3.801 | Primary | 3138
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NPg Best View | 2.413 | 2.153 | 1.762 | 1.328 | 0.932 | 0.528 | 0.046 | -2.428 | -6.595 | -9.778 | -12.775 | Primary | 3139
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NPg Best View | 7.857 | 6.95 | 6.62 | 6.272 | 5.971 | 5.698 | 5.372 | 3.928 | 1.789 | 0.321 | -1.142 | Primary | 3140
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 23.611 | 23.098 | 22.601 | 22.037 | 21.579 | 21.153 | 20.655 | 18.245 | 12.133 | 7.25 | 2.582 | Primary | 3141
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NPg Best View | 11.27 | 10.981 | 10.445 | 9.829 | 9.406 | 9.073 | 8.681 | 6.981 | 1.977 | -1.794 | -5.688 | Primary | 3142
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NPg Best View | 11.202 | 10.892 | 10.395 | 9.855 | 9.45 | 9.101 | 8.698 | 6.77 | 1.498 | -2.742 | -6.965 | Primary | 3143
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NPg Best View | 12.977 | 12.854 | 12.995 | 13.106 | 13.229 | 13.351 | 13.449 | 13.826 | 13.099 | 12.524 | 11.908 | Primary | 3144
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NPg Best View | 6.108 | 5.748 | 5.23 | 4.698 | 4.255 | 3.827 | 3.33 | 0.97 | -4.819 | -9.667 | -14.344 | Primary | 3145
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NPg Best View | 8.627 | 7.094 | 7.04 | 6.945 | 6.867 | 6.771 | 6.62 | 5.779 | 3.555 | 1.872 | 0.335 | Primary | 3146
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NPg Best View | 7.849 | 7.163 | 6.799 | 6.396 | 6.047 | 5.728 | 5.363 | 3.754 | -0.836 | -4.632 | -8.301 | Primary | 3147
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NPg Best View | 31.102 | 31.112 | 31.121 | 31.128 | 31.136 | 31.144 | 31.151 | 31.181 | 31.178 | 31.176 | 31.17 | Primary | 3148
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NPg Best View | 10.328 | 10.334 | 10.278 | 10.199 | 25.563 | 25.551 | 25.527 | 25.405 | 23.845 | 22.548 | 21.209 | Primary | 3149
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NPg Best View | 7.685 | 6.042 | 20.602 | 20.134 | 19.745 | 19.374 | 18.925 | 16.969 | 11.886 | 7.854 | 4.047 | Primary | 3150
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NPg Best View | 9.035 | 8.817 | 8.499 | 8.14 | 7.798 | 7.455 | 7.053 | 4.944 | 1.366 | -1.44 | -4.157 | Primary | 3151
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NPg Best View | 11.714 | 11.632 | 11.503 | 11.37 | 11.262 | 11.158 | 11.031 | 10.494 | 9.285 | 8.331 | 7.471 | Primary | 3152
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NPg Best View | 19.977 | 19.485 | 19.407 | 19.305 | 19.239 | 19.182 | 19.098 | 18.685 | 16.165 | 14.027 | 11.986 | Primary | 3153
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NPg Best View | 10.765 | 10.425 | 9.885 | 9.348 | 8.935 | 8.549 | 8.065 | 5.688 | 0.854 | -2.632 | -5.987 | Primary | 3154
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NPg Best View | 11.967 | 11.602 | 11.282 | 10.916 | 10.642 | 10.408 | 10.138 | 8.935 | 4.608 | 0.985 | -2.575 | Primary | 3155
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NPg Best View | 10.986 | 10.449 | 10.111 | 9.734 | 9.434 | 9.156 | 8.82 | 7.28 | 3.395 | 0.277 | -2.69 | Primary | 3156
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NPg Best View | 13.931 | 13.931 | 13.893 | 13.837 | 13.808 | 13.787 | 13.758 | 13.584 | 12.547 | 11.74 | 10.944 | Primary | 3157
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NPg Best View | 14.122 | 14.123 | 14.086 | 14.028 | 13.979 | 13.933 | 13.874 | 13.518 | 12.354 | 11.508 | 10.704 | Primary | 3158
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NPg Best View | 18.69 | 18.601 | 18.444 | 18.27 | 18.134 | 18.016 | 17.874 | 17.187 | 15.792 | 14.793 | 13.799 | Primary | 3159
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NPg Best View | 18.893 | 18.8 | 18.64 | 18.455 | 18.32 | 18.21 | 18.082 | 17.468 | 15.696 | 14.349 | 12.993 | Primary | 3160
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NPg Best View | 12.176 | 11.992 | 11.683 | 11.352 | 11.053 | 10.768 | 10.442 | 9.032 | 4.583 | 0.693 | -2.982 | Primary | 3161
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 22.233 | 21.909 | 21.431 | 20.971 | 20.637 | 20.349 | 19.998 | 18.341 | 14.821 | 12.228 | 9.594 | Primary | 3162
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NPg Best View | 26.986 | 26.072 | 25.976 | 25.879 | 25.768 | 25.638 | 25.474 | 24.907 | 24.472 | 24.13 | 23.812 | Primary | 3163
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NPg Best View | 5.602 | 5.191 | 5.161 | 5.126 | 5.097 | 5.073 | 5.042 | 4.902 | 4.413 | 4.023 | 3.644 | Primary | 3164
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NPg Best View | 11.223 | 11.295 | 11.312 | 11.305 | 11.314 | 11.327 | 11.324 | 11.275 | 9.561 | 8.122 | 6.767 | Primary | 3165

## Generation Headroom
Version 1.1
Please filter on your selected substation
Licence Area | Substation Name | Voltage (kV) | Supply Voltage (kV) | BSP Group | GSP | Substation Location | Scenario Name | Generation Headroom Capacity (MW) 2024 | Generation Headroom Capacity (MW) 2025 | Generation Headroom Capacity (MW) 2026 | Generation Headroom Capacity (MW) 2027 | Generation Headroom Capacity (MW) 2028 | Generation Headroom Capacity (MW) 2029 | Generation Headroom Capacity (MW) 2030 | Generation Headroom Capacity (MW) 2035 | Generation Headroom Capacity (MW) 2040 | Generation Headroom Capacity (MW) 2045 | Generation Headroom Capacity (MW) 2050 | Bulk Supply Point or Primary | Row Number
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Consumer Transformation | 27.415 | 27.294 | 74.953 | 74.445 | 74.297 | 74.095 | 73.793 | 71.733 | 63.886 | 58.126 | 52.782 | BSP | 1
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Consumer Transformation | 37.242 | 35.553 | 33.144 | 30.299 | 28.209 | 26.007 | 23.336 | -5.46 | -28.645 | -45.954 | -61.996 | BSP | 2
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Consumer Transformation | 138.656 | 137.578 | 136.017 | 134.331 | 133.161 | 131.84 | 130.1 | 120.901 | 98.12 | 81.465 | 66.9 | BSP | 3
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Consumer Transformation | 19.081 | 17.092 | 14.169 | 10.661 | 8.161 | 5.554 | 2.376 | -11.864 | -41.35 | -64.372 | -86.353 | BSP | 4
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 68.992 | 67.956 | 66.349 | 64.4 | 63.033 | 61.588 | 59.776 | 51.592 | 35.44 | 23.604 | 12.836 | BSP | 5
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Consumer Transformation | 16.932 | 17.106 | 17.119 | 16.987 | 17.028 | 16.985 | 16.831 | 14.946 | 8.5 | 4.067 | 0.321 | BSP | 6
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Consumer Transformation | 31.546 | 30.118 | 28.172 | 25.927 | 24.052 | 22.09 | 19.737 | 8.843 | -9.273 | -23.176 | -35.881 | BSP | 7
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Consumer Transformation | 44.715 | 43.214 | 41.084 | 38.744 | 37.221 | 35.581 | 33.48 | 23.629 | 2.928 | -12.047 | -25.795 | BSP | 8
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 53.412 | 49.594 | 48.85 | 47.956 | 47.353 | 46.627 | 38.291 | 12.044 | -1.093 | -10.145 | -17.833 | BSP | 9
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Consumer Transformation | 72.476 | 71.844 | 70.749 | 69.362 | 68.476 | 67.562 | 66.412 | 61.53 | 48.392 | 37.965 | 28.019 | BSP | 10
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Consumer Transformation | 51.343 | 50.452 | 48.97 | 47.123 | 45.901 | 44.57 | 42.857 | 7.795 | -9.411 | -21.886 | -33.261 | BSP | 11
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Consumer Transformation | 113.495 | 109.983 | 105.107 | 99.488 | 95.086 | 90.414 | 84.749 | 33.424 | -19.224 | -58.558 | -93.681 | BSP | 12
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Consumer Transformation | 91.413 | 90.938 | 90.231 | 89.374 | 88.798 | 88.186 | 87.427 | 83.968 | 77.119 | 71.872 | 66.812 | BSP | 13
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Consumer Transformation | 42.513 | 41.643 | 40.333 | 38.654 | 37.409 | 36.05 | 34.426 | 25.56 | 0.389 | -20.331 | -39.621 | BSP | 14
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Consumer Transformation | 44.084 | 41.971 | 39.049 | 35.586 | 32.816 | 29.845 | 26.272 | 8.203 | -22.395 | -44.503 | -64.051 | BSP | 15
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Consumer Transformation | 64.919 | 64.809 | 64.416 | 63.805 | 63.651 | 63.457 | 63.149 | 61.418 | 51.846 | 44.455 | 37.45 | BSP | 16
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 44.694 | 44.43 | 43.961 | 43.347 | 42.933 | 42.479 | 41.883 | 39.048 | 32.523 | 27.632 | 23.135 | BSP | 17
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Consumer Transformation | 17.338 | 16.455 | 15.069 | 13.389 | 12.288 | 11.095 | 9.59 | 2.345 | -10.474 | -19.248 | -27.218 | BSP | 18
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Consumer Transformation | 58.445 | 56.653 | 53.94 | 50.712 | 48.684 | 46.566 | 43.943 | 32.293 | 8.749 | -8.529 | -24.78 | BSP | 19
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Consumer Transformation | 58.333 | 57.514 | 56.174 | 93.47 | 92.126 | 90.681 | 88.874 | 80.168 | 64.4 | 52.842 | 42.602 | BSP | 20
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Consumer Transformation | 48.869 | 48.01 | 46.49 | 44.499 | 43.111 | 41.614 | 39.677 | 30.514 | 7.428 | -10.544 | -27.171 | BSP | 21
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Consumer Transformation | 65.967 | 64.617 | 62.686 | 60.446 | 58.723 | 56.909 | 54.703 | 44.504 | 26.597 | 13.509 | 1.765 | BSP | 22
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Consumer Transformation | 91.063 | 90.557 | 89.71 | 88.641 | 87.921 | 87.173 | 86.233 | 82.168 | 72.315 | 64.657 | 57.525 | BSP | 23
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Consumer Transformation | 84.852 | 84.115 | 83.083 | 81.862 | 80.847 | 79.786 | 78.51 | 72.732 | 64.198 | 58.046 | 52.539 | BSP | 24
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Consumer Transformation | 97.219 | 96.393 | 95.267 | 94.003 | 93.077 | 92.111 | 90.936 | 85.573 | 75.208 | 67.42 | 60.212 | BSP | 25
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Consumer Transformation | 66.73 | 66.335 | 65.735 | 64.94 | 64.105 | 63.086 | 61.808 | 53.17 | 40.995 | 33.78 | 29.001 | BSP | 26
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Consumer Transformation | 59.814 | 58.949 | 57.727 | 56.282 | 55.215 | 54.077 | 52.711 | 45.956 | 33.167 | 23.455 | 14.453 | BSP | 27
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 69.241 | 69.379 | 69.445 | 69.487 | 69.606 | 69.699 | 69.733 | 69.733 | 65.498 | 62.086 | 58.958 | BSP | 28
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Consumer Transformation | 38.457 | 33.518 | 28.251 | 24.305 | 21.392 | 18.398 | 14.783 | -1.062 | -31.867 | -55.007 | -75.955 | BSP | 29
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Consumer Transformation | 49.921 | 49.66 | 49.129 | 48.438 | 47.951 | 47.349 | 46.526 | 41.353 | 26.965 | 16.541 | 7.813 | BSP | 30
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Consumer Transformation | 61.354 | 59.391 | 57.034 | 54.921 | 53.213 | 51.429 | 49.178 | 39.398 | 21.125 | 7.426 | -4.717 | BSP | 31
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Consumer Transformation | 48.823 | 47.331 | 45.024 | 42.271 | 40.315 | 38.266 | 35.698 | 24.398 | 0.659 | -17.241 | -33.641 | BSP | 32
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Consumer Transformation | 139.027 | 138.943 | 138.548 | 137.89 | 137.524 | 136.982 | 136.181 | 110.374 | 91.802 | 78.825 | 68.171 | BSP | 33
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Consumer Transformation | 60.147 | 60.129 | 59.939 | 59.598 | 59.391 | 59.108 | 58.707 | 55.834 | 48.12 | 42.25 | 37.058 | BSP | 34
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Consumer Transformation | 68.454 | 67.277 | 65.708 | 64.086 | 62.978 | 61.816 | 60.357 | 53.973 | 40.359 | 30.285 | 20.969 | BSP | 35
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Consumer Transformation | 27.569 | 27.63 | 27.584 | 27.434 | 27.365 | 27.272 | 27.113 | 26.109 | 19.56 | 14.091 | 9.092 | BSP | 36
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP | 37
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Consumer Transformation | 58.124 | 57.665 | 57.047 | 56.287 | 55.472 | 54.537 | 53.408 | 46.546 | 36.641 | 29.96 | 24.897 | BSP | 38
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Consumer Transformation | 51.216 | 49.512 | 47.214 | 44.821 | 43.209 | 41.517 | 39.39 | 30.056 | 11.922 | -1.224 | -13.316 | BSP | 39
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 9.371 | 9.08 | 8.443 | 7.552 | 7.195 | 6.763 | 6.169 | 2.54 | -11.127 | -21.717 | -31.593 | BSP | 40
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Consumer Transformation | 40.728 | 40.732 | 40.734 | 40.732 | 106.929 | 106.922 | 106.912 | 106.83 | 106.701 | 106.554 | 106.405 | BSP | 41
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 28.997 | 28.112 | 27.091 | 25.961 | 24.909 | 23.781 | 22.536 | 15.402 | 5.503 | -2.486 | -9.509 | BSP | 42
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Consumer Transformation | 54.483 | 53.762 | 52.858 | 51.754 | 50.693 | 49.494 | 48.107 | 39.407 | 25.147 | 14.756 | 6.059 | BSP | 43
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Consumer Transformation | 80.836 | 80.358 | 79.738 | 79.021 | 78.377 | 77.714 | 76.96 | 73.419 | 67.877 | 63.352 | 59.208 | BSP | 44
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Consumer Transformation | 30.311 | 28.925 | 26.765 | 24.163 | 22.149 | 20.012 | 17.287 | 4.901 | -21.585 | -41.625 | -59.513 | BSP | 45
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Consumer Transformation | 53.698 | 52.53 | 50.705 | 48.502 | 46.96 | 45.308 | 43.216 | 33.412 | 12.73 | -2.705 | -16.699 | BSP | 46
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Consumer Transformation | 53.638 | 52.831 | 51.396 | 49.54 | 48.391 | 47.106 | 45.43 | 36.802 | 18.566 | 5.916 | -5.353 | BSP | 47
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 33.714 | 31.842 | 28.955 | 25.47 | 23.111 | 20.587 | 17.409 | 2.633 | -23.46 | -41.807 | -58.817 | BSP | 48
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Consumer Transformation | 72.557 | 71.83 | 70.817 | 69.572 | 68.811 | 67.985 | 67.025 | 61.63 | 47.937 | 37.102 | 26.732 | BSP | 49
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Consumer Transformation | 35.61 | 33.33 | 30.2 | 26.65 | 24.15 | 21.524 | 18.37 | 3.646 | -21.321 | -39.12 | -55.51 | BSP | 50
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Consumer Transformation | 63.873 | 61.109 | 57.406 | 53.288 | 49.877 | 46.328 | 42.068 | 22.78 | -10.611 | -35.48 | -57.804 | BSP | 51
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Consumer Transformation | 57.045 | 54.916 | 52.148 | 49.305 | 47.11 | 44.839 | 42.058 | 30.144 | 10.604 | -3.331 | -15.765 | BSP | 52
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Consumer Transformation | 52.615 | 51.203 | 49.276 | 47.041 | 45.232 | 43.364 | 41.126 | 31.217 | 14.556 | 1.502 | -10.828 | BSP | 53
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Consumer Transformation | 59.155 | 58.552 | 57.471 | 56.089 | 55.034 | 53.914 | 52.472 | 45.904 | 29.438 | 16.673 | 5.285 | BSP | 54
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Falling Short | 26.957 | 26.939 | 74.859 | 74.702 | 74.465 | 74.157 | 73.813 | 71.775 | 69.345 | 67.572 | 66.604 | BSP | 55
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Falling Short | 37.021 | 35.978 | 34.711 | 33.198 | 31.36 | 29.23 | 27.119 | 0.992 | -7.343 | -13.111 | -17.029 | BSP | 56
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Falling Short | 138.576 | 138.045 | 137.386 | 136.571 | 135.458 | 134.075 | 132.646 | 125.479 | 118.776 | 114.474 | 112.49 | BSP | 57
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Falling Short | 18.631 | 17.424 | 15.921 | 14.1 | 11.872 | 9.29 | 6.77 | -4.444 | -13.466 | -19.842 | -24.562 | BSP | 58
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 69.051 | 68.583 | 67.933 | 67.097 | 66.005 | 64.686 | 63.392 | 57.778 | 53.598 | 51.151 | 49.897 | BSP | 59
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Falling Short | 16.192 | 16.171 | 16.089 | 15.933 | 15.696 | 15.377 | 14.994 | 12.334 | 8.781 | 5.892 | 4.122 | BSP | 60
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Falling Short | 31.289 | 30.194 | 28.916 | 27.444 | 25.706 | 23.727 | 21.773 | 12.748 | 5.14 | -0.467 | -4.633 | BSP | 61
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Falling Short | 44.836 | 44.24 | 43.488 | 42.567 | 41.335 | 39.832 | 38.347 | 31.574 | 26.099 | 22.819 | 21.133 | BSP | 62
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 52.786 | 49.078 | 48.621 | 48.049 | 47.317 | 46.433 | 38.062 | 12.053 | 5.475 | 0.49 | -2.345 | BSP | 63
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Falling Short | 72.27 | 71.947 | 71.477 | 70.856 | 70.049 | 69.084 | 68.154 | 64.35 | 61.876 | 60.431 | 59.433 | BSP | 64
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Falling Short | 51.1 | 50.727 | 50.168 | 49.405 | 48.379 | 47.118 | 45.856 | 13.111 | 8.133 | 5.032 | 3.469 | BSP | 65
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Falling Short | 113.65 | 111.533 | 108.969 | 105.914 | 102.148 | 97.732 | 93.312 | 48.6 | 30.602 | 18.536 | 11.444 | BSP | 66
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Falling Short | 91.239 | 90.964 | 90.616 | 90.187 | 89.659 | 89.044 | 88.44 | 85.686 | 83.358 | 81.667 | 80.398 | BSP | 67
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Falling Short | 41.241 | 40.194 | 38.988 | 37.583 | 35.959 | 34.145 | 32.283 | 22.627 | 12.771 | 4.59 | -1.949 | BSP | 68
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Falling Short | 43.855 | 42.43 | 40.723 | 38.689 | 36.235 | 33.387 | 30.491 | 16.109 | 2.493 | -7.267 | -13.202 | BSP | 69
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Falling Short | 64.486 | 64.504 | 64.446 | 64.296 | 64.047 | 63.719 | 63.381 | 61.669 | 59.992 | 58.882 | 58.217 | BSP | 70
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 44.584 | 44.467 | 44.283 | 44.023 | 43.669 | 43.235 | 42.804 | 40.802 | 39.15 | 38.138 | 37.577 | BSP | 71
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Falling Short | 17.094 | 16.765 | 16.277 | 15.626 | 14.761 | 13.7 | 12.63 | 7.537 | 2.947 | -0.036 | -1.494 | BSP | 72
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Falling Short | 58.519 | 57.805 | 56.821 | 55.568 | 53.951 | 52.005 | 50.115 | 42.08 | 36.258 | 32.873 | 31.112 | BSP | 73
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Falling Short | 57.975 | 57.374 | 56.584 | 94.592 | 93.347 | 91.873 | 90.394 | 83.416 | 77.348 | 73.081 | 70.417 | BSP | 74
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Falling Short | 48.568 | 48.148 | 47.517 | 46.644 | 45.484 | 44.082 | 42.696 | 36.431 | 31.57 | 28.746 | 27.231 | BSP | 75
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Falling Short | 65.925 | 65.095 | 64.077 | 62.861 | 61.361 | 59.602 | 57.863 | 49.955 | 43.366 | 38.796 | 35.864 | BSP | 76
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Falling Short | 90.985 | 90.765 | 90.433 | 89.987 | 89.401 | 88.696 | 88.016 | 85.226 | 83.427 | 82.491 | 81.991 | BSP | 77
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Falling Short | 84.654 | 84.098 | 83.429 | 82.639 | 81.698 | 80.62 | 79.556 | 74.667 | 70.69 | 67.936 | 65.958 | BSP | 78
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Falling Short | 97.278 | 96.837 | 96.306 | 95.68 | 94.906 | 94.002 | 93.114 | 89.148 | 86.043 | 84.066 | 82.84 | BSP | 79
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Falling Short | 66.425 | 65.999 | 65.476 | 64.825 | 64.008 | 63.009 | 61.871 | 54.725 | 45.924 | 39.317 | 36.181 | BSP | 80
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Falling Short | 59.186 | 58.414 | 57.526 | 56.507 | 55.318 | 53.976 | 52.623 | 45.933 | 39.524 | 34.346 | 30.297 | BSP | 81
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 68.899 | 68.975 | 69.031 | 69.056 | 69.032 | 68.97 | 68.9 | 68.456 | 67.913 | 67.539 | 67.286 | BSP | 82
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Falling Short | 41.516 | 39.23 | 37.093 | 35.159 | 32.746 | 29.902 | 27.147 | 15.705 | 8.065 | 3.627 | 0.905 | BSP | 83
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Falling Short | 49.616 | 49.438 | 49.167 | 48.777 | 48.216 | 47.497 | 46.707 | 42.263 | 37.452 | 34.181 | 32.797 | BSP | 84
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Falling Short | 62.296 | 61.337 | 60.319 | 59.248 | 57.872 | 56.223 | 54.635 | 48.1 | 43.852 | 41.532 | 40.249 | BSP | 85
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Falling Short | 48.863 | 48.157 | 47.197 | 45.974 | 44.387 | 42.476 | 40.628 | 32.829 | 27.389 | 24.294 | 22.581 | BSP | 86
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Falling Short | 138.486 | 138.451 | 138.313 | 138.021 | 137.541 | 136.88 | 136.095 | 111.253 | 104.486 | 99.778 | 97.983 | BSP | 87
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Falling Short | 59.165 | 58.801 | 58.366 | 57.847 | 57.233 | 56.529 | 55.772 | 51.408 | 46.381 | 41.936 | 38.433 | BSP | 88
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Falling Short | 68.778 | 68.262 | 67.657 | 66.956 | 66.042 | 64.943 | 63.877 | 59.379 | 56.222 | 54.434 | 53.43 | BSP | 89
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Falling Short | 27.291 | 27.293 | 27.252 | 27.155 | 27.003 | 26.809 | 26.605 | 25.534 | 24.512 | 23.867 | 23.467 | BSP | 90
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Falling Short | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP | 91
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Falling Short | 57.537 | 56.865 | 56.11 | 55.252 | 54.26 | 53.131 | 51.918 | 45.049 | 37.309 | 30.985 | 26.76 | BSP | 92
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Falling Short | 51.705 | 50.954 | 50.064 | 49.037 | 47.705 | 46.102 | 44.541 | 37.971 | 33.379 | 30.751 | 29.311 | BSP | 93
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 8.849 | 8.749 | 8.553 | 8.247 | 7.815 | 7.272 | 6.694 | 3.566 | 0.359 | -1.801 | -2.904 | BSP | 94
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Falling Short | 40.598 | 40.54 | 40.479 | 40.415 | 106.547 | 106.477 | 106.404 | 106.006 | 105.563 | 105.089 | 104.603 | BSP | 95
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 27.387 | 25.785 | 24.119 | 22.38 | 20.552 | 18.631 | 16.643 | 5.993 | -5.477 | -16.403 | -26.265 | BSP | 96
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Falling Short | 53.56 | 52.548 | 51.452 | 50.235 | 48.882 | 47.387 | 45.782 | 36.508 | 25.719 | 16.543 | 9.952 | BSP | 97
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Falling Short | 80.387 | 79.766 | 79.089 | 78.35 | 77.538 | 76.659 | 75.783 | 71.572 | 67.617 | 64.031 | 60.762 | BSP | 98
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Falling Short | 30.374 | 29.658 | 28.684 | 27.437 | 25.805 | 23.836 | 21.912 | 13.532 | 7.333 | 3.765 | 1.87 | BSP | 99
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Falling Short | 53.648 | 53.117 | 52.378 | 51.416 | 50.152 | 48.62 | 47.104 | 40.269 | 34.882 | 31.643 | 29.973 | BSP | 100
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Falling Short | 53.194 | 52.918 | 52.439 | 51.737 | 50.759 | 49.529 | 48.264 | 41.941 | 35.862 | 31.928 | 30.2 | BSP | 101
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 33.162 | 32.356 | 31.223 | 29.754 | 27.849 | 25.54 | 23.259 | 12.642 | 3.285 | -2.923 | -6.463 | BSP | 102
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Falling Short | 71.944 | 71.337 | 70.65 | 69.864 | 68.97 | 67.981 | 66.955 | 61.398 | 55.352 | 50.307 | 46.371 | BSP | 103
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Falling Short | 35.417 | 34.141 | 32.611 | 30.82 | 28.642 | 26.111 | 23.596 | 11.849 | 1.485 | -5.898 | -10.783 | BSP | 104
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Falling Short | 64.009 | 62.23 | 60.142 | 57.722 | 54.793 | 51.405 | 48.076 | 33.068 | 21.163 | 13.381 | 8.25 | BSP | 105
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Falling Short | 57.724 | 56.669 | 55.433 | 54.022 | 52.238 | 50.117 | 48.06 | 39.503 | 33.639 | 30.268 | 28.447 | BSP | 106
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Falling Short | 52.454 | 51.411 | 50.197 | 48.803 | 47.166 | 45.321 | 43.524 | 35.531 | 29.125 | 24.366 | 20.508 | BSP | 107
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Falling Short | 58.944 | 58.591 | 58.065 | 57.355 | 56.411 | 55.26 | 54.131 | 49.211 | 45.601 | 43.507 | 42.376 | BSP | 108
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - Leading the Way | 27.416 | 27.257 | 74.864 | 74.318 | 74.137 | 73.882 | 73.28 | 64.455 | 57.545 | 52.889 | 54.054 | BSP | 109
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - Leading the Way | 37.317 | 35.588 | 33.097 | 30.214 | 28.174 | 25.986 | 22.757 | -21.502 | -42.675 | -57.536 | -57.505 | BSP | 110
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - Leading the Way | 138.741 | 137.627 | 135.935 | 134.142 | 132.921 | 131.499 | 129.036 | 102.375 | 82.158 | 68.399 | 70.834 | BSP | 111
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - Leading the Way | 19.153 | 17.135 | 14.137 | 10.61 | 8.222 | 5.696 | 1.85 | -33.661 | -61.089 | -81.402 | -81.208 | BSP | 112
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 69.056 | 68.028 | 66.392 | 64.433 | 63.125 | 61.714 | 59.473 | 39.727 | 25.262 | 15.497 | 16.825 | BSP | 113
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - Leading the Way | 16.915 | 17.042 | 16.991 | 16.793 | 16.761 | 16.617 | 16.177 | 9.162 | 3.749 | 0.367 | 1.317 | BSP | 114
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - Leading the Way | 31.585 | 30.144 | 28.143 | 25.85 | 24.013 | 22.059 | 19.31 | -2.448 | -19.131 | -31.317 | -32.521 | BSP | 115
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - Leading the Way | 44.835 | 43.339 | 41.148 | 38.793 | 37.344 | 35.754 | 33.177 | 7.68 | -10.807 | -23.074 | -20.702 | BSP | 116
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 53.427 | 49.55 | 48.696 | 47.698 | 46.975 | 46.076 | 37.323 | 2.252 | -9.133 | -16.588 | -16.049 | BSP | 117
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - Leading the Way | 72.506 | 71.868 | 70.742 | 69.332 | 68.505 | 67.635 | 66.053 | 50.519 | 38.287 | 29.241 | 30.342 | BSP | 118
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - Leading the Way | 51.37 | 50.448 | 48.898 | 47.008 | 45.816 | 44.49 | 42.307 | -5.542 | -20.977 | -31.293 | -29.616 | BSP | 119
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - Leading the Way | 113.61 | 110.026 | 104.928 | 99.1 | 94.671 | 89.854 | 82.694 | -3.371 | -50.89 | -84.33 | -84.066 | BSP | 120
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - Leading the Way | 91.429 | 90.948 | 90.225 | 89.367 | 88.822 | 88.237 | 87.336 | 78.941 | 72.64 | 68.112 | 68.227 | BSP | 121
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - Leading the Way | 42.515 | 41.544 | 40.097 | 38.323 | 37.034 | 35.593 | 33.268 | 5.565 | -17.781 | -36.278 | -37.073 | BSP | 122
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - Leading the Way | 44.096 | 41.906 | 38.825 | 35.202 | 32.332 | 29.171 | 24.782 | -11.481 | -38.953 | -57.864 | -59.158 | BSP | 123
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - Leading the Way | 64.941 | 64.8 | 64.367 | 63.746 | 63.605 | 63.412 | 62.788 | 51.951 | 43.46 | 37.492 | 39.51 | BSP | 124
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 44.705 | 44.424 | 43.93 | 43.308 | 42.921 | 42.491 | 41.761 | 33.757 | 27.849 | 23.74 | 24.51 | BSP | 125
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - Leading the Way | 17.361 | 16.448 | 15.005 | 13.283 | 12.185 | 10.964 | 9.073 | -6.802 | -18.119 | -25.169 | -24.259 | BSP | 126
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - Leading the Way | 58.547 | 56.784 | 54.051 | 50.811 | 48.878 | 46.81 | 43.454 | 14.75 | -6.349 | -20.484 | -18.519 | BSP | 127
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - Leading the Way | 58.348 | 57.507 | 56.103 | 93.331 | 91.989 | 90.508 | 88.254 | 69.323 | 55.144 | 45.399 | 45.648 | BSP | 128
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - Leading the Way | 48.908 | 48.005 | 46.402 | 44.367 | 43.064 | 41.64 | 39.112 | 11.396 | -9.85 | -25.31 | -23.332 | BSP | 129
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - Leading the Way | 66.025 | 64.673 | 62.693 | 60.411 | 58.709 | 56.876 | 54.21 | 32.627 | 16.547 | 5.532 | 5.805 | BSP | 130
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - Leading the Way | 91.084 | 90.573 | 89.705 | 88.622 | 87.95 | 87.239 | 85.997 | 74.188 | 65.188 | 58.765 | 59.733 | BSP | 131
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - Leading the Way | 84.923 | 84.196 | 83.153 | 81.927 | 80.943 | 79.891 | 78.447 | 67.877 | 60.124 | 54.848 | 54.496 | BSP | 132
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - Leading the Way | 97.276 | 96.453 | 95.296 | 94.012 | 93.114 | 92.158 | 90.727 | 78.167 | 68.698 | 62.015 | 62.263 | BSP | 133
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - Leading the Way | 66.667 | 66.192 | 65.45 | 64.462 | 63.384 | 62.041 | 60.245 | 46.516 | 36.643 | 31.279 | 30.553 | BSP | 134
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - Leading the Way | 59.833 | 58.936 | 57.657 | 56.174 | 55.097 | 53.924 | 52.245 | 37.374 | 25.731 | 17.307 | 16.602 | BSP | 135
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 69.261 | 69.38 | 69.415 | 69.448 | 69.576 | 69.678 | 69.6 | 64.896 | 61.093 | 58.25 | 59.656 | BSP | 136
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - Leading the Way | 38.959 | 34.238 | 28.868 | 24.832 | 22.002 | 19.041 | 14.452 | -22.546 | -50.537 | -69.882 | -67.926 | BSP | 137
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - Leading the Way | 49.92 | 49.593 | 48.94 | 48.12 | 47.529 | 46.777 | 45.388 | 29.246 | 16.699 | 8.234 | 9.782 | BSP | 138
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - Leading the Way | 61.56 | 59.686 | 57.302 | 55.183 | 53.583 | 51.889 | 49.194 | 26.531 | 10.131 | -1.099 | 0.641 | BSP | 139
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - Leading the Way | 48.901 | 47.407 | 45.044 | 42.257 | 40.414 | 38.449 | 35.229 | 6.315 | -15.146 | -30.011 | -27.874 | BSP | 140
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - Leading the Way | 138.997 | 138.79 | 138.213 | 137.383 | 136.837 | 136.051 | 134.54 | 94.246 | 78.368 | 68.07 | 70.521 | BSP | 141
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - Leading the Way | 60.137 | 60.082 | 59.836 | 59.437 | 59.172 | 58.806 | 58.126 | 49.84 | 43.033 | 38.106 | 38.031 | BSP | 142
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - Leading the Way | 68.567 | 67.414 | 65.815 | 64.195 | 63.153 | 62.042 | 60.28 | 43.579 | 31.291 | 22.841 | 24.28 | BSP | 143
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - Leading the Way | 27.569 | 27.601 | 27.516 | 27.344 | 27.279 | 27.183 | 26.802 | 19.591 | 13.53 | 8.758 | 9.696 | BSP | 144
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - Leading the Way | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP | 145
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - Leading the Way | 58.089 | 57.574 | 56.86 | 55.976 | 55.024 | 53.9 | 52.43 | 41.387 | 32.922 | 27.43 | 25.962 | BSP | 146
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - Leading the Way | 51.369 | 49.716 | 47.391 | 44.995 | 43.474 | 41.844 | 39.242 | 16.826 | 0.699 | -9.93 | -7.993 | BSP | 147
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 9.391 | 9.057 | 8.344 | 7.384 | 7.004 | 6.524 | 5.407 | -9.834 | -22.138 | -30.961 | -29.44 | BSP | 148
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - Leading the Way | 40.728 | 40.732 | 40.734 | 40.733 | 106.93 | 106.924 | 106.914 | 106.813 | 106.686 | 106.541 | 106.413 | BSP | 149
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 28.967 | 28.049 | 26.972 | 25.766 | 24.634 | 23.397 | 21.877 | 11.419 | 2.434 | -4.635 | -8.575 | BSP | 150
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - Leading the Way | 54.432 | 53.629 | 52.596 | 51.343 | 50.098 | 48.651 | 46.84 | 31.445 | 18.888 | 9.902 | 7.24 | BSP | 151
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - Leading the Way | 80.842 | 80.36 | 79.727 | 78.995 | 78.352 | 77.68 | 76.807 | 70.557 | 65.386 | 61.29 | 60.029 | BSP | 152
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - Leading the Way | 30.395 | 28.997 | 26.76 | 24.118 | 22.217 | 20.171 | 16.789 | -15.424 | -39.236 | -55.792 | -53.172 | BSP | 153
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - Leading the Way | 53.72 | 52.519 | 50.618 | 48.36 | 46.872 | 45.249 | 42.578 | 17.546 | -1.022 | -13.753 | -11.955 | BSP | 154
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - Leading the Way | 53.656 | 52.806 | 51.285 | 49.353 | 48.172 | 46.803 | 44.548 | 22.634 | 6.681 | -3.441 | -1.519 | BSP | 155
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 33.748 | 31.799 | 28.792 | 25.245 | 22.951 | 20.447 | 16.576 | -16.174 | -39.658 | -54.869 | -53.209 | BSP | 156
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - Leading the Way | 72.543 | 71.731 | 70.622 | 69.321 | 68.517 | 67.626 | 66.267 | 51.009 | 38.401 | 28.889 | 28.221 | BSP | 157
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - Leading the Way | 35.682 | 33.348 | 30.11 | 26.496 | 24.012 | 21.343 | 17.5 | -12.803 | -35.137 | -49.901 | -49.85 | BSP | 158
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - Leading the Way | 64.097 | 61.335 | 57.534 | 53.363 | 50.046 | 46.524 | 41.497 | 1.211 | -29.323 | -50.837 | -51.057 | BSP | 159
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - Leading the Way | 57.243 | 55.186 | 52.385 | 49.513 | 47.405 | 45.172 | 41.878 | 17.455 | -0.047 | -11.58 | -10.373 | BSP | 160
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - Leading the Way | 52.683 | 51.275 | 49.326 | 47.099 | 45.389 | 43.607 | 41.119 | 20.741 | 5.223 | -6.357 | -7.281 | BSP | 161
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - Leading the Way | 59.187 | 58.566 | 57.434 | 56.013 | 55.005 | 53.907 | 51.946 | 32.562 | 17.679 | 7.033 | 8.801 | BSP | 162
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NG FES - System Transformation | 27.011 | 26.902 | 74.676 | 74.36 | 74.035 | 73.646 | 73.167 | 70.081 | 64.753 | 58.601 | 50.168 | BSP | 163
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NG FES - System Transformation | 36.528 | 34.904 | 32.864 | 30.579 | 28.265 | 25.827 | 23.218 | -6.294 | -22.088 | -39.282 | -62.234 | BSP | 164
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NG FES - System Transformation | 137.914 | 136.738 | 135.366 | 134.002 | 132.573 | 130.976 | 129.16 | 118.936 | 102.494 | 86.025 | 64.598 | BSP | 165
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NG FES - System Transformation | 18.152 | 16.149 | 13.582 | 10.681 | 7.846 | 4.891 | 1.744 | -13.639 | -34.868 | -58.064 | -89.324 | BSP | 166
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 68.6 | 67.589 | 66.229 | 64.677 | 63.18 | 61.604 | 59.912 | 51.586 | 40.837 | 29.325 | 13.43 | BSP | 167
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NG FES - System Transformation | 16.451 | 16.481 | 16.409 | 16.238 | 16.017 | 15.697 | 15.262 | 11.84 | 6.085 | 0.495 | -6.217 | BSP | 168
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NG FES - System Transformation | 31.029 | 29.551 | 27.744 | 25.742 | 23.684 | 21.532 | 19.264 | 7.923 | -5.809 | -19.97 | -38.059 | BSP | 169
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NG FES - System Transformation | 43.999 | 42.53 | 40.777 | 38.994 | 37.256 | 35.4 | 33.359 | 22.967 | 8.681 | -6.124 | -25.985 | BSP | 170
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 52.815 | 48.941 | 48.273 | 47.529 | 46.683 | 45.698 | 37.131 | 9.638 | -1.265 | -11.333 | -22.933 | BSP | 171
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NG FES - System Transformation | 72.082 | 71.423 | 70.469 | 69.342 | 68.284 | 67.187 | 66.029 | 60.457 | 52.116 | 41.823 | 26.592 | BSP | 172
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NG FES - System Transformation | 50.774 | 49.88 | 48.631 | 47.177 | 45.744 | 44.201 | 42.5 | 6.784 | -5.164 | -17.62 | -34.489 | BSP | 173
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NG FES - System Transformation | 112.332 | 108.88 | 104.651 | 100.011 | 95.275 | 90.247 | 84.851 | 33.095 | -3.804 | -41.816 | -91.579 | BSP | 174
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NG FES - System Transformation | 91.139 | 90.667 | 90.059 | 89.367 | 88.685 | 87.968 | 87.195 | 83.344 | 78.35 | 72.896 | 65.591 | BSP | 175
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NG FES - System Transformation | 41.577 | 40.507 | 39.17 | 37.61 | 35.951 | 34.146 | 32.146 | 20.812 | 0.258 | -21.814 | -49.767 | BSP | 176
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NG FES - System Transformation | 43.317 | 41.207 | 38.608 | 35.671 | 32.646 | 29.406 | 25.893 | 7.257 | -15.852 | -37.908 | -64.889 | BSP | 177
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NG FES - System Transformation | 64.504 | 64.362 | 64.067 | 63.667 | 63.324 | 62.929 | 62.446 | 59.599 | 53.007 | 45.301 | 34.538 | BSP | 178
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 44.492 | 44.201 | 43.786 | 43.287 | 42.803 | 42.28 | 41.692 | 38.634 | 33.686 | 28.783 | 22.371 | BSP | 179
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NG FES - System Transformation | 16.82 | 16.062 | 14.998 | 13.756 | 12.483 | 11.115 | 9.62 | 1.859 | -6.126 | -14.871 | -26.948 | BSP | 180
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NG FES - System Transformation | 57.742 | 56.105 | 53.939 | 51.496 | 49.205 | 46.823 | 44.301 | 32.056 | 17.9 | 0.828 | -24.265 | BSP | 181
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NG FES - System Transformation | 57.877 | 56.963 | 55.683 | 93.155 | 91.611 | 89.959 | 88.173 | 78.865 | 66.955 | 55.107 | 39.778 | BSP | 182
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NG FES - System Transformation | 48.327 | 47.448 | 46.149 | 44.576 | 43.02 | 41.354 | 39.52 | 29.932 | 13.834 | -3.29 | -26.884 | BSP | 183
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NG FES - System Transformation | 65.472 | 64.078 | 62.331 | 60.407 | 58.5 | 56.494 | 54.362 | 43.757 | 30.754 | 17.461 | 0.221 | BSP | 184
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NG FES - System Transformation | 90.821 | 90.342 | 89.642 | 88.805 | 88.001 | 87.166 | 86.281 | 82.021 | 75.847 | 68.535 | 57.856 | BSP | 185
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NG FES - System Transformation | 84.508 | 83.818 | 82.934 | 81.913 | 80.799 | 79.631 | 78.403 | 72.354 | 66.515 | 60.225 | 52.146 | BSP | 186
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NG FES - System Transformation | 96.928 | 96.153 | 95.221 | 94.225 | 93.225 | 92.18 | 91.066 | 85.594 | 78.671 | 71.171 | 61.011 | BSP | 187
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NG FES - System Transformation | 66.479 | 65.981 | 65.319 | 64.494 | 63.532 | 62.381 | 61.022 | 52.055 | 41.03 | 33.487 | 26.721 | BSP | 188
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NG FES - System Transformation | 59.22 | 58.255 | 57.075 | 55.76 | 54.424 | 53.005 | 51.469 | 43.377 | 32.892 | 22.062 | 8.664 | BSP | 189
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 68.957 | 68.989 | 68.996 | 69.005 | 68.995 | 68.95 | 68.853 | 68.056 | 64.338 | 60.474 | 55.511 | BSP | 190
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NG FES - System Transformation | 37.342 | 32.38 | 27.901 | 24.741 | 21.605 | 18.359 | 15.002 | -0.927 | -18.985 | -41.169 | -73.27 | BSP | 191
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NG FES - System Transformation | 49.493 | 49.128 | 48.617 | 48.022 | 47.353 | 46.552 | 45.594 | 39.521 | 28.756 | 18.336 | 5.147 | BSP | 192
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NG FES - System Transformation | 60.834 | 58.776 | 56.66 | 54.836 | 53.011 | 51.107 | 49.1 | 39.519 | 27.01 | 13.861 | -4.122 | BSP | 193
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NG FES - System Transformation | 48.215 | 46.731 | 44.756 | 42.532 | 40.371 | 38.111 | 35.715 | 24.071 | 8.601 | -8.726 | -33.204 | BSP | 194
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NG FES - System Transformation | 138.465 | 138.249 | 137.872 | 137.353 | 136.746 | 135.945 | 134.897 | 107.786 | 93.121 | 80.025 | 64.445 | BSP | 195
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NG FES - System Transformation | 59.57 | 59.307 | 58.92 | 58.422 | 57.881 | 57.246 | 56.499 | 51.66 | 43.829 | 36.137 | 27.141 | BSP | 196
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NG FES - System Transformation | 68.026 | 66.831 | 65.494 | 64.209 | 62.975 | 61.682 | 60.293 | 53.654 | 44.363 | 34.367 | 20.738 | BSP | 197
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NG FES - System Transformation | 27.364 | 27.378 | 27.325 | 27.21 | 27.058 | 26.872 | 26.641 | 25.091 | 20.416 | 15.026 | 7.573 | BSP | 198
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NG FES - System Transformation | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | 27.801 | BSP | 199
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NG FES - System Transformation | 57.78 | 57.176 | 56.442 | 55.58 | 54.573 | 53.434 | 52.156 | 44.436 | 35.345 | 28.289 | 21.72 | BSP | 200
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NG FES - System Transformation | 50.623 | 48.912 | 46.967 | 45.072 | 43.262 | 41.368 | 39.349 | 29.637 | 17.981 | 4.852 | -13.645 | BSP | 201
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 8.89 | 8.64 | 8.195 | 7.619 | 7.06 | 6.418 | 5.66 | 0.946 | -8.002 | -18.704 | -34.033 | BSP | 202
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NG FES - System Transformation | 40.663 | 40.633 | 40.598 | 40.558 | 106.713 | 106.663 | 106.609 | 106.273 | 105.838 | 105.386 | 104.936 | BSP | 203
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 28.123 | 26.813 | 25.386 | 23.855 | 22.262 | 20.565 | 18.757 | 8.364 | -3.799 | -15.643 | -28.232 | BSP | 204
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NG FES - System Transformation | 53.947 | 53.023 | 51.954 | 50.729 | 49.39 | 47.895 | 46.214 | 36.002 | 21.8 | 9.777 | -2.389 | BSP | 205
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NG FES - System Transformation | 80.566 | 79.965 | 79.26 | 78.478 | 77.674 | 76.841 | 75.976 | 71.635 | 66.574 | 61.621 | 56.147 | BSP | 206
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NG FES - System Transformation | 29.722 | 28.27 | 26.345 | 24.169 | 21.985 | 19.676 | 17.186 | 4.696 | -13.851 | -33.008 | -58.829 | BSP | 207
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NG FES - System Transformation | 53.154 | 51.983 | 50.421 | 48.648 | 46.918 | 45.079 | 43.083 | 32.888 | 18.659 | 3.628 | -16.974 | BSP | 208
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NG FES - System Transformation | 52.974 | 52.215 | 51.072 | 49.676 | 48.272 | 46.722 | 44.977 | 35.436 | 22.854 | 10.086 | -6.832 | BSP | 209
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 32.541 | 30.853 | 28.562 | 25.903 | 23.146 | 20.212 | 17.055 | 0.933 | -15.536 | -34.111 | -59.881 | BSP | 210
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NG FES - System Transformation | 71.98 | 71.257 | 70.397 | 69.421 | 68.42 | 67.336 | 66.132 | 59.217 | 49.153 | 37.671 | 22.799 | BSP | 211
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NG FES - System Transformation | 34.641 | 32.501 | 29.912 | 27.107 | 24.269 | 21.286 | 18.112 | 2.151 | -14.009 | -32.266 | -56.85 | BSP | 212
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NG FES - System Transformation | 62.95 | 60.317 | 57.155 | 53.761 | 50.158 | 46.388 | 42.427 | 23.017 | 0.777 | -23.37 | -55.388 | BSP | 213
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NG FES - System Transformation | 56.428 | 54.338 | 51.967 | 49.626 | 47.268 | 44.82 | 42.263 | 30.368 | 18.056 | 4.338 | -14.777 | BSP | 214
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NG FES - System Transformation | 52.14 | 50.667 | 48.875 | 46.897 | 44.928 | 42.895 | 40.76 | 30.48 | 17.535 | 4.107 | -13.07 | BSP | 215
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NG FES - System Transformation | 58.739 | 58.061 | 57.069 | 55.879 | 54.665 | 53.373 | 51.983 | 44.909 | 33.634 | 21.203 | 3.923 | BSP | 216
NPgY | ATTERCLIFFE | 33 | 132 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3FA | NPg Best View | 27.518 | 27.477 | 75.139 | 74.658 | 74.427 | 74.134 | 73.749 | 71.655 | 64.415 | 59.043 | 53.793 | BSP | 217
NPgY | BARUGH 132/66KV | 66 | 132 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1LR | NPg Best View | 37.77 | 36.411 | 34.35 | 31.864 | 30.172 | 28.338 | 26.149 | -0.469 | -21.746 | -38.037 | -53.69 | BSP | 218
NPgY | BEESTON ROYDS 132/33KV | 33 | 132 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6NJ | NPg Best View | 139.4 | 138.712 | 137.399 | 135.925 | 134.859 | 133.595 | 131.957 | 123.718 | 102.876 | 87.355 | 73.108 | BSP | 219
NPgY | BEVERLEY 132/33KV | 33 | 132 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0RW | NPg Best View | 19.822 | 18.293 | 15.871 | 12.895 | 10.989 | 8.945 | 6.479 | -4.645 | -32.028 | -54.009 | -75.536 | BSP | 220
NPgY | BINGLEY 132/33KV | 33 | 132 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 69.346 | 68.553 | 67.202 | 65.536 | 64.47 | 63.312 | 61.888 | 55.496 | 40.744 | 29.619 | 19.135 | BSP | 221
NPgY | BLACKBURN MEADOWS B | 33 | 132 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1DA | NPg Best View | 17.316 | 17.634 | 17.747 | 17.673 | 17.73 | 17.651 | 17.403 | 15.189 | 9.458 | 5.516 | 1.841 | BSP | 222
NPgY | BLYTON | 33 | 132 | BLYTON | KEADBY | DN21 3NS | NPg Best View | 31.992 | 30.849 | 29.218 | 27.303 | 25.794 | 24.173 | 22.26 | 13.309 | -3.146 | -16.175 | -28.544 | BSP | 223
NPgY | BRADFORD | 33 | 132 | BRADFORD | BRADFORD WEST | BD1 4RF | NPg Best View | 45.312 | 44.192 | 42.348 | 40.315 | 39.034 | 37.64 | 35.93 | 28.16 | 9.136 | -4.93 | -18.291 | BSP | 224
NPgY | BRAMHAM | 33 | 132 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 53.691 | 50.042 | 49.316 | 48.439 | 47.658 | 46.72 | 38.167 | 11.621 | 0.098 | -7.881 | -15.302 | BSP | 225
NPgY | BRANSHOLME | 33 | 132 | BRANSHOLME | CREYKE BECK | HU7 4ZN | NPg Best View | 72.82 | 72.407 | 71.545 | 70.413 | 69.798 | 69.137 | 68.296 | 64.833 | 52.489 | 42.406 | 32.634 | BSP | 226
NPgY | BRIGHOUSE 132/33KV | 33 | 132 | BRIGHOUSE 132/33kV | ELLAND | HD6 1PZ | NPg Best View | 51.682 | 51.037 | 49.741 | 48.127 | 47.07 | 45.898 | 44.445 | 10.884 | -4.83 | -16.468 | -27.521 | BSP | 227
NPgY | DONCASTER B/THORPE MARSH | 66 | 132 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 8UX | NPg Best View | 114.547 | 111.682 | 107.46 | 102.477 | 98.746 | 94.644 | 89.731 | 42.151 | -5.751 | -42.439 | -76.697 | BSP | 228
NPgY | DONCASTER CENTRAL | 33 | 132 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1RE | NPg Best View | 91.552 | 91.182 | 90.563 | 89.819 | 89.336 | 88.823 | 88.208 | 85.467 | 79.121 | 74.129 | 69.183 | BSP | 229
NPgY | DRIFFIELD/BEVERLEY GROUP | 66 | 132 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5NW | NPg Best View | 42.776 | 42.143 | 40.89 | 39.361 | 37.998 | 36.518 | 34.825 | 26.433 | 2.755 | -17.064 | -36.103 | BSP | 230
NPgY | FEATHERSTONE | 33 | 132 | FEATHERSTONE | FERRYBRIDGE B | WF7 6HE | NPg Best View | 44.705 | 42.955 | 40.394 | 37.273 | 34.845 | 32.125 | 28.873 | 12.528 | -14.764 | -34.923 | -53.907 | BSP | 231
NPgY | GIRLINGTON | 33 | 132 | GIRLINGTON | BRADFORD WEST | BD7 2NB | NPg Best View | 65.054 | 65.068 | 64.711 | 64.188 | 63.997 | 63.772 | 63.47 | 62.101 | 53.005 | 45.868 | 38.94 | BSP | 232
NPgY | HALIFAX 132/33KV | 33 | 132 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 44.855 | 44.689 | 44.306 | 43.792 | 43.47 | 43.109 | 42.644 | 40.436 | 34.356 | 29.714 | 25.331 | BSP | 233
NPgY | HECKMONDWIKE | 33 | 132 | HECKMONDWIKE | SKELTON GRANGE | WF16 9LU | NPg Best View | 17.515 | 16.791 | 15.519 | 13.989 | 12.979 | 11.866 | 10.52 | 4.308 | -7.139 | -15.137 | -22.849 | BSP | 234
NPgY | HOLMFIELD | 33 | 132 | HOLMFIELD | BRADFORD WEST | HX2 9AY | NPg Best View | 58.952 | 57.518 | 55.213 | 52.429 | 50.894 | 49.24 | 47.219 | 38.304 | 16.808 | 0.534 | -15.312 | BSP | 235
NPgY | HULL EAST 132/33KV | 33 | 132 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NL | NPg Best View | 58.713 | 58.131 | 57.032 | 94.583 | 93.497 | 92.274 | 90.748 | 83.417 | 69.256 | 58.589 | 48.647 | BSP | 236
NPgY | HULL SOUTH | 33 | 132 | HULL SOUTH | CREYKE BECK | HU3 5JA | NPg Best View | 49.323 | 48.759 | 47.528 | 45.866 | 44.815 | 43.654 | 42.183 | 35.094 | 13.467 | -3.754 | -20.073 | BSP | 237
NPgY | HULL WEST | 33 | 132 | HULL WEST | CREYKE BECK | HU13 0FA | NPg Best View | 66.465 | 65.421 | 63.814 | 61.901 | 60.526 | 59.023 | 57.209 | 48.853 | 32.741 | 20.604 | 9.202 | BSP | 238
NPgY | HUMBERSTON | 33 | 132 | HUMBERSTON | GRIMSBY WEST | DN36 4AW | NPg Best View | 91.255 | 90.885 | 90.196 | 89.306 | 88.788 | 88.235 | 87.546 | 84.585 | 75.385 | 68.026 | 61.034 | BSP | 239
NPgY | HUNNINGLEY | 33 | 132 | HUNNINGLEY | WEST MELTON SECTION 3 | S70 3ET | NPg Best View | 85.122 | 84.554 | 83.717 | 82.705 | 81.923 | 81.079 | 80.07 | 75.444 | 67.822 | 62.134 | 56.808 | BSP | 240
NPgY | HUNSHELF | 66 | 132 | HUNSHELF | WEST MELTON SECTION 3 | S36 8WR | NPg Best View | 97.75 | 97.197 | 96.332 | 95.316 | 94.642 | 93.896 | 92.967 | 88.699 | 79.197 | 71.848 | 64.808 | BSP | 241
NPgY | IMMINGHAM | 33 | 132 | IMMINGHAM | GRIMSBY WEST | DN40 1QT | NPg Best View | 67.011 | 66.712 | 66.129 | 65.285 | 64.311 | 63.054 | 61.457 | 51.865 | 41.949 | 36.286 | 31.795 | BSP | 242
NPgY | KIRKHAW LANE | 33 | 132 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8SB | NPg Best View | 60.173 | 59.513 | 58.449 | 57.171 | 56.214 | 55.16 | 53.903 | 47.88 | 36.156 | 27.057 | 18.258 | BSP | 243
NPgY | KIRKSTALL C 2/5 | 33 | 132 | KIRKSTALL C 2/5 | KIRKSTALL B | LS18 4EL | NPg Best View | 69.61 | 69.917 | 70.095 | 70.231 | 70.391 | 70.514 | 70.571 | 70.736 | 66.63 | 63.278 | 60.158 | BSP | 244
NPgY | KIRKSTALL C/RING ROAD HORSFORTH | 33 | 132 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS18 4EL | NPg Best View | 41.045 | 37.365 | 33.123 | 29.863 | 27.656 | 25.313 | 22.513 | 10.687 | -17.591 | -39.532 | -59.889 | BSP | 245
NPgY | LEEDS EAST | 33 | 132 | LEEDS EAST | SKELTON GRANGE | LS9 6ED | NPg Best View | 50.27 | 50.222 | 49.755 | 49.134 | 48.518 | 47.758 | 46.786 | 41.588 | 28.648 | 19.114 | 10.552 | BSP | 246
NPgY | LEEDS NORTH | 33 | 132 | LEEDS NORTH | SKELTON GRANGE | LS7 2AU | NPg Best View | 62.692 | 61.397 | 59.707 | 58.135 | 57.079 | 55.915 | 54.417 | 47.687 | 31.092 | 18.143 | 6.344 | BSP | 247
NPgY | LINDLEY | 33 | 132 | LINDLEY | ELLAND | HD3 3NY | NPg Best View | 49.491 | 48.424 | 46.585 | 44.329 | 42.93 | 41.416 | 39.533 | 31.226 | 9.385 | -7.618 | -23.626 | BSP | 248
NPgY | LOW ROAD | 33 | 132 | LOW ROAD | SKELTON GRANGE | LS10 1RH | NPg Best View | 139.516 | 139.634 | 139.32 | 138.678 | 138.196 | 137.46 | 136.407 | 109.904 | 93.211 | 81.501 | 71.054 | BSP | 249
NPgY | MALLARD WAY | 33 | 132 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DB | NPg Best View | 60.615 | 60.807 | 60.752 | 60.531 | 60.355 | 60.056 | 59.59 | 56.652 | 49.686 | 44.301 | 39.209 | BSP | 250
NPgY | MENSTON | 33 | 132 | MENSTON | BRADFORD WEST | LS29 6BP | NPg Best View | 69.052 | 68.207 | 66.942 | 65.6 | 64.783 | 63.901 | 62.804 | 58.089 | 45.536 | 35.968 | 26.879 | BSP | 251
NPgY | MOSS ROAD | 33 | 132 | MOSS ROAD | GRIMSBY WEST | DN32 0LW | NPg Best View | 27.69 | 27.832 | 27.823 | 27.732 | 27.666 | 27.575 | 27.43 | 26.611 | 20.299 | 14.954 | 9.985 | BSP | 252
NPgY | OSGODBY 1/2 | 33 | 132 | OSGODBY 1/2 | DRAX | YO8 5HY | NPg Best View | 27.81 | 27.814 | 27.817 | 27.819 | 27.821 | 27.822 | 27.823 | 27.824 | 27.824 | 27.824 | 27.824 | BSP | 253
NPgY | OSGODBY 3/4 | 33 | 132 | OSGODBY 3/4 | DRAX | YO8 5HY | NPg Best View | 58.441 | 58.125 | 57.59 | 56.884 | 56.045 | 55.022 | 53.758 | 46.58 | 38.177 | 32.491 | 27.622 | BSP | 254
NPgY | RODLEY | 33 | 132 | RODLEY | SKELTON GRANGE | LS13 1PZ | NPg Best View | 51.994 | 50.735 | 48.849 | 46.843 | 45.634 | 44.327 | 42.705 | 35.726 | 19.168 | 6.781 | -4.975 | BSP | 255
NPgY | SAINT ANDREWS ROAD 132/33KV | 33 | 132 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 9.45 | 9.264 | 8.621 | 7.783 | 7.317 | 6.779 | 6.115 | 2.655 | -10.093 | -20.108 | -29.814 | BSP | 256
NPgY | SALTEND 132/33KV | 33 | 132 | SALTEND 132/33kV | SALTEND NORTH | HU12 8EY | NPg Best View | 40.792 | 40.823 | 40.847 | 40.865 | 107.076 | 107.08 | 107.074 | 107.008 | 106.884 | 106.742 | 106.594 | BSP | 257
NPgY | SANTON | 33 | 132 | SANTON | KEADBY | DN16 1XP | NPg Best View | 29.18 | 28.279 | 27.046 | 25.626 | 24.181 | 22.585 | 20.718 | 11.44 | 1.509 | -6.119 | -12.993 | BSP | 258
NPgY | SCUNTHORPE NORTH | 33 | 132 | SCUNTHORPE NORTH | KEADBY | DN15 8GN | NPg Best View | 55.038 | 54.548 | 53.767 | 52.739 | 51.626 | 50.28 | 48.644 | 39.253 | 26.752 | 17.578 | 9.128 | BSP | 259
NPgY | SCUNTHORPE SOUTH | 33 | 132 | SCUNTHORPE SOUTH | KEADBY | DN16 1BD | NPg Best View | 81.089 | 80.755 | 80.278 | 79.713 | 79.204 | 78.657 | 78.023 | 75.05 | 70.008 | 65.742 | 61.696 | BSP | 260
NPgY | SILSDEN | 33 | 132 | SILSDEN | BRADFORD WEST | BD20 0ND | NPg Best View | 31.066 | 30.136 | 28.458 | 26.358 | 24.911 | 23.322 | 21.311 | 11.979 | -12.467 | -31.503 | -48.973 | BSP | 261
NPgY | SOWERBY BRIDGE 132/33KV | 33 | 132 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EL | NPg Best View | 54.215 | 53.359 | 51.862 | 49.998 | 48.833 | 47.535 | 45.905 | 38.186 | 19.172 | 4.639 | -8.984 | BSP | 262
NPgY | STAYGATE | 33 | 132 | STAYGATE | SKELTON GRANGE | BD6 1YA | NPg Best View | 53.942 | 53.352 | 52.059 | 50.378 | 49.306 | 48.067 | 46.503 | 38.832 | 22.472 | 10.924 | -0.021 | BSP | 263
NPgY | THORNHILL 132KV | 33 | 132 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 34.518 | 33.122 | 30.745 | 27.783 | 26.006 | 24.016 | 21.517 | 9.739 | -13.727 | -30.69 | -47.193 | BSP | 264
NPgY | WAKEFIELD MONCKTON ROAD | 33 | 132 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7AL | NPg Best View | 72.733 | 72.118 | 71.151 | 69.966 | 69.175 | 68.301 | 67.297 | 61.967 | 49.069 | 38.732 | 28.47 | BSP | 265
NPgY | WAKEFIELD NORTH | 33 | 132 | WAKEFIELD NORTH | SKELTON GRANGE | WF1 3HN | NPg Best View | 36.311 | 34.455 | 31.758 | 28.633 | 26.58 | 24.347 | 21.685 | 9.324 | -13.165 | -29.639 | -45.572 | BSP | 266
NPgY | WEST MELTON | 66 | 132 | WEST MELTON | WEST MELTON SECTION 3 | S63 6EZ | NPg Best View | 64.7 | 62.473 | 59.315 | 55.755 | 52.938 | 49.947 | 46.436 | 30.71 | 0.25 | -23.11 | -44.828 | BSP | 267
NPgY | WHINMOOR | 33 | 132 | WHINMOOR | FERRYBRIDGE B | LS14 2DG | NPg Best View | 58.112 | 56.557 | 54.421 | 52.134 | 50.618 | 48.97 | 46.931 | 38.136 | 20.726 | 7.789 | -4.243 | BSP | 268
NPgY | WOLD NEWTON | 33 | 132 | WOLD NEWTON | KEADBY | DN37 0SW | NPg Best View | 53.051 | 51.922 | 50.314 | 48.425 | 47.017 | 45.544 | 43.819 | 36.083 | 20.687 | 8.242 | -3.793 | BSP | 269
NPgY | YARBOROUGH ROAD 132/33KV | 33 | 132 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4JJ | NPg Best View | 59.619 | 59.287 | 58.492 | 57.406 | 56.672 | 55.843 | 54.757 | 49.799 | 34.535 | 22.364 | 11.214 | BSP | 270
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Consumer Transformation | 13.035 | 12.763 | 12.518 | 12.428 | 12.41 | 12.388 | 12.352 | 12.14 | 10.539 | 9.233 | 8 | Primary | 271
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Consumer Transformation | 12.597 | 10.967 | 10.895 | 10.771 | 10.699 | 10.594 | 10.443 | 9.241 | 6.398 | 4.504 | 3.014 | Primary | 272
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Consumer Transformation | 11.561 | 11.285 | 10.914 | 10.461 | 9.991 | 9.504 | 8.935 | 6.343 | 1.786 | -1.787 | -4.935 | Primary | 273
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Consumer Transformation | 5.928 | 4.543 | 4.567 | 4.548 | 4.535 | 4.504 | 4.442 | 3.951 | 1.803 | 0.246 | -1.051 | Primary | 274
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 5.351 | 5.025 | 4.619 | 4.232 | 3.939 | 3.638 | 3.27 | 1.739 | -1.13 | -3.322 | -5.329 | Primary | 275
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Consumer Transformation | 5.346 | 5.338 | 5.309 | 5.273 | 5.266 | 5.256 | 5.231 | 5.114 | 4.43 | 3.878 | 3.344 | Primary | 276
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Consumer Transformation | 10.066 | 9.573 | 8.906 | 8.14 | 7.588 | 7.022 | 6.358 | 3.433 | -1.809 | -5.773 | -9.558 | Primary | 277
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Consumer Transformation | 17.135 | 17.166 | 17.174 | 17.161 | 17.176 | 17.188 | 17.189 | 17.183 | 15.908 | 14.855 | 13.871 | Primary | 278
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Consumer Transformation | 1.402 | 1.217 | 0.948 | 0.617 | 0.316 | 0.003 | -0.372 | -2.094 | -5.939 | -9.048 | -11.844 | Primary | 279
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Consumer Transformation | 2.978 | 2.454 | 2.571 | 2.659 | 2.765 | 2.863 | 2.944 | 3.278 | 2.64 | 2.15 | 1.681 | Primary | 280
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Consumer Transformation | 12.159 | 11.937 | 11.601 | 11.195 | 10.914 | 10.622 | 10.264 | 8.691 | 5.664 | 3.353 | 1.112 | Primary | 281
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Consumer Transformation | 2.594 | 2.298 | 1.918 | 1.541 | 1.243 | 0.909 | 0.471 | -1.751 | -5.587 | -8.138 | -10.327 | Primary | 282
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Consumer Transformation | 3.091 | 3.087 | 3.074 | 3.054 | 3.039 | 3.021 | 2.996 | 2.85 | 2.511 | 2.251 | 2.016 | Primary | 283
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Consumer Transformation | 15.827 | 15.638 | 15.343 | 14.987 | 14.778 | 14.562 | 14.295 | 13.153 | 10.154 | 7.836 | 5.601 | Primary | 284
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Consumer Transformation | 12.947 | 12.484 | 12.453 | 12.404 | 12.39 | 12.372 | 12.346 | 12.198 | 11.391 | 10.706 | 10.032 | Primary | 285
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Consumer Transformation | 10.595 | 10.599 | 10.561 | 10.482 | 10.446 | 10.398 | 10.324 | 9.867 | 7.889 | 6.46 | 5.229 | Primary | 286
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Consumer Transformation | 15.623 | 15.283 | 14.802 | 14.244 | 13.816 | 13.367 | 12.826 | 10.305 | 6.43 | 3.745 | 1.373 | Primary | 287
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Consumer Transformation | 8.451 | 8.48 | 8.486 | 8.466 | 8.461 | 8.446 | 8.414 | 8.123 | 6.793 | 5.799 | 4.978 | Primary | 288
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Consumer Transformation | 6.686 | 6.57 | 6.392 | 6.158 | 6.002 | 5.837 | 5.645 | 4.663 | 1.33 | -1.528 | -4.303 | Primary | 289
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Consumer Transformation | 21.811 | 21.773 | 21.677 | 21.54 | 21.444 | 21.343 | 21.208 | 20.654 | 19.423 | 18.49 | 17.642 | Primary | 290
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Consumer Transformation | 3.809 | 3.682 | 3.52 | 3.334 | 3.216 | 3.095 | 2.96 | 2.258 | 0.419 | -1.18 | -2.764 | Primary | 291
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Consumer Transformation | 11.545 | 11.082 | 10.429 | 9.655 | 9.092 | 8.499 | 7.784 | 4.375 | -1.634 | -6.028 | -10.07 | Primary | 292
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Consumer Transformation | 9.539 | 9.175 | 8.682 | 8.159 | 7.762 | 7.349 | 6.84 | 4.586 | 0.266 | -2.963 | -5.877 | Primary | 293
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Consumer Transformation | 14.891 | 14.622 | 14.273 | 13.922 | 13.65 | 13.37 | 13.027 | 11.607 | 9.447 | 7.915 | 6.524 | Primary | 294
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Consumer Transformation | 2.557 | 2.515 | 2.363 | 2.124 | 2.025 | 1.893 | 1.698 | 0.424 | -3.285 | -5.884 | -8.19 | Primary | 295
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Consumer Transformation | 5.913 | 5.714 | 5.429 | 5.089 | 4.817 | 4.529 | 4.183 | 2.491 | -0.089 | -1.898 | -3.475 | Primary | 296
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 15.138 | 15.119 | 15.084 | 15.034 | 15 | 14.961 | 14.909 | 14.589 | 13.243 | 12.191 | 11.269 | Primary | 297
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Consumer Transformation | 4.309 | 1.26 | 1.222 | 1.129 | 1.069 | 0.974 | 0.822 | -0.39 | -4.554 | -7.554 | -10.022 | Primary | 298
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Consumer Transformation | 8.297 | 8.198 | 8.016 | 7.761 | 7.583 | 7.37 | 7.098 | 5.378 | 1.542 | -1.157 | -3.446 | Primary | 299
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Consumer Transformation | 11.759 | 11.47 | 11.025 | 10.481 | 10.11 | 9.726 | 9.254 | 7.169 | 2.406 | -1.34 | -4.841 | Primary | 300
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Consumer Transformation | 6.154 | 5.724 | 5.081 | 4.306 | 3.718 | 3.094 | 2.326 | -1.338 | -8.245 | -13.364 | -17.933 | Primary | 301
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Consumer Transformation | 6.843 | 6.826 | 6.806 | 6.779 | 6.757 | 6.734 | 6.71 | 6.593 | 6.262 | 5.972 | 5.689 | Primary | 302
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Consumer Transformation | 4.338 | 4.307 | 4.263 | 4.209 | 4.161 | 4.106 | 4.038 | 3.689 | 3.075 | 2.611 | 2.197 | Primary | 303
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Consumer Transformation | 13.781 | 13.462 | 12.999 | 12.451 | 12.103 | 11.74 | 11.296 | 9.327 | 5.447 | 2.517 | -0.326 | Primary | 304
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 13.961 | 13.88 | 13.795 | 13.7 | 13.602 | 13.504 | 13.404 | 12.89 | 11.709 | 10.546 | 9.377 | Primary | 305
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Consumer Transformation | 5.537 | 5.459 | 5.35 | 5.222 | 5.123 | 5.021 | 4.899 | 4.372 | 3.605 | 3.047 | 2.532 | Primary | 306
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Consumer Transformation | 10.599 | 10.302 | 9.846 | 9.301 | 8.932 | 8.546 | 8.058 | 5.923 | 1.446 | -1.926 | -5.088 | Primary | 307
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Consumer Transformation | 11.531 | 11.266 | 10.858 | 10.375 | 9.985 | 9.571 | 9.049 | 6.659 | 2.354 | -0.798 | -3.566 | Primary | 308
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Consumer Transformation | 9.31 | 9.34 | 9.324 | 9.27 | 9.283 | 9.283 | 9.259 | 8.996 | 7.251 | 5.933 | 4.718 | Primary | 309
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Consumer Transformation | 10.353 | 10.345 | 10.285 | 10.19 | 10.121 | 10.038 | 9.91 | 9.336 | 8.165 | 7.346 | 6.601 | Primary | 310
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Consumer Transformation | 17.45 | 17.281 | 17.043 | 16.764 | 16.542 | 16.303 | 16.013 | 14.607 | 12.73 | 11.536 | 10.563 | Primary | 311
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Consumer Transformation | 7.901 | 22.421 | 22.157 | 21.85 | 21.604 | 21.347 | 21.028 | 19.619 | 16.307 | 13.689 | 11.336 | Primary | 312
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Consumer Transformation | 10.732 | 10.322 | 9.724 | 9.004 | 8.42 | 7.828 | 7.127 | 4.147 | -1.727 | -6.488 | -10.929 | Primary | 313
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Consumer Transformation | 3.852 | 3.736 | 3.586 | 3.44 | 3.342 | 3.241 | 3.116 | 2.614 | 1.798 | 1.228 | 0.675 | Primary | 314
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Consumer Transformation | 6.224 | 5.576 | 4.786 | 4.011 | 3.358 | 2.678 | 1.872 | -1.794 | -7.438 | -11.532 | -15.027 | Primary | 315
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Consumer Transformation | 4.637 | 4.264 | 3.741 | 3.107 | 2.435 | 1.726 | 0.861 | -3.128 | -10.052 | -15.63 | -20.61 | Primary | 316
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Consumer Transformation | 5.992 | 5.454 | 4.683 | 3.761 | 3.025 | 2.268 | 1.369 | -2.63 | -10.168 | -16.142 | -21.683 | Primary | 317
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Consumer Transformation | 4.316 | 4.377 | 4.43 | 4.473 | 4.514 | 4.548 | 4.574 | 4.624 | 4.4 | 4.274 | 4.192 | Primary | 318
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Consumer Transformation | 7.945 | 7.49 | 6.803 | 5.962 | 5.319 | 4.614 | 3.745 | -0.777 | -8.121 | -13.122 | -17.348 | Primary | 319
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Consumer Transformation | 13.031 | 13.118 | 13.194 | 13.247 | 13.295 | 13.336 | 13.368 | 13.424 | 12.629 | 12.062 | 11.603 | Primary | 320
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Consumer Transformation | 10.29 | 10.419 | 10.54 | 10.652 | 10.757 | 10.858 | 10.952 | 11.361 | 11.459 | 11.548 | 11.631 | Primary | 321
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Consumer Transformation | 11.049 | 11.142 | 11.213 | 11.282 | 11.371 | 11.447 | 11.499 | 11.655 | 9.934 | 8.586 | 7.377 | Primary | 322
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Consumer Transformation | 11.735 | 11.79 | 11.824 | 11.843 | 11.879 | 11.909 | 11.922 | 11.975 | 11.359 | 10.891 | 10.451 | Primary | 323
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Consumer Transformation | 10.926 | 10.637 | 10.201 | 9.686 | 9.315 | 8.907 | 8.394 | 5.774 | 1.673 | -0.969 | -3.188 | Primary | 324
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Consumer Transformation | 4.283 | 4.208 | 4.099 | 3.975 | 3.845 | 3.711 | 3.545 | 2.872 | 2.467 | 2.253 | 2.105 | Primary | 325
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Consumer Transformation | 5.255 | 5.235 | 5.193 | 5.136 | 5.089 | 5.037 | 4.969 | 4.627 | 4.022 | 3.485 | 2.955 | Primary | 326
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Consumer Transformation | 13.699 | 13.225 | 12.63 | 12.043 | 11.581 | 11.101 | 10.511 | 7.905 | 3.066 | -0.552 | -3.767 | Primary | 327
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Consumer Transformation | 0.005 | 0.006 | -0.005 | -0.026 | -0.042 | -0.063 | -0.093 | -0.272 | -0.665 | -0.97 | -1.247 | Primary | 328
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Consumer Transformation | 3.318 | 3.116 | 2.853 | 2.556 | 2.316 | 2.068 | 1.769 | 0.489 | -1.243 | -2.509 | -3.694 | Primary | 329
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Consumer Transformation | 9.658 | 9.442 | 9.095 | 8.661 | 8.379 | 8.071 | 7.683 | 5.762 | 2.297 | -0.03 | -2.15 | Primary | 330
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Consumer Transformation | 9.173 | 9.041 | 8.872 | 8.727 | 8.628 | 8.517 | 8.359 | 7.634 | 5.405 | 3.676 | 2.103 | Primary | 331
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Consumer Transformation | 5.399 | 5.107 | 4.711 | 4.259 | 3.93 | 3.587 | 3.179 | 1.243 | -2.741 | -5.87 | -8.84 | Primary | 332
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Consumer Transformation | 4.798 | 4.822 | 4.841 | 4.853 | 4.864 | 4.871 | 4.872 | 4.831 | 4.589 | 4.425 | 4.299 | Primary | 333
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Consumer Transformation | 21.963 | 21.777 | 21.52 | 21.244 | 21.072 | 20.894 | 20.67 | 19.711 | 17.097 | 15.064 | 13.166 | Primary | 334
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Consumer Transformation | 7.932 | 7.979 | 8.003 | 8.018 | 8.065 | 8.102 | 8.124 | 8.185 | 7.074 | 6.192 | 5.357 | Primary | 335
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Consumer Transformation | 13.472 | 13.127 | 12.711 | 12.338 | 12.047 | 11.744 | 11.364 | 9.753 | 6.649 | 4.298 | 2.199 | Primary | 336
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Consumer Transformation | 7.275 | 7.252 | 7.149 | 6.981 | 6.853 | 6.706 | 6.494 | 5.465 | 2.654 | 0.498 | -1.442 | Primary | 337
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Consumer Transformation | 4.723 | 4.037 | 3.11 | 2.125 | 1.459 | 0.768 | -0.08 | -3.785 | -10.811 | -15.952 | -20.715 | Primary | 338
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Consumer Transformation | 0.957 | 0.922 | 0.878 | 0.824 | 0.773 | 0.718 | 0.655 | 0.325 | -0.359 | -0.93 | -1.466 | Primary | 339
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Consumer Transformation | 3.191 | 3.084 | 2.93 | 2.73 | 2.556 | 2.359 | 2.124 | 0.722 | -2.12 | -4.291 | -6.196 | Primary | 340
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Consumer Transformation | 12.976 | 12.923 | 12.806 | 12.642 | 12.505 | 12.361 | 12.174 | 11.373 | 9.613 | 8.303 | 7.179 | Primary | 341
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Consumer Transformation | 14.821 | 14.621 | 15.294 | 14.881 | 14.59 | 14.288 | 13.905 | 12.249 | 8.676 | 5.904 | 3.308 | Primary | 342
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Consumer Transformation | 22.332 | 22.338 | 22.261 | 22.083 | 21.896 | 21.637 | 21.283 | 18.534 | 13.043 | 9.634 | 7.246 | Primary | 343
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Consumer Transformation | 9.824 | 9.532 | 9.128 | 8.651 | 8.263 | 7.859 | 7.381 | 5.166 | 0.977 | -2.345 | -5.439 | Primary | 344
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Consumer Transformation | 2.434 | 2.196 | 1.881 | 1.517 | 1.271 | 1.014 | 0.704 | -0.722 | -3.203 | -5.062 | -6.876 | Primary | 345
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Consumer Transformation | 8.157 | 7.777 | 7.15 | 6.374 | 5.933 | 5.48 | 4.917 | 2.522 | -3.89 | -8.959 | -13.907 | Primary | 346
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Consumer Transformation | 6.097 | 3.811 | 3.8 | 3.768 | 3.74 | 3.702 | 3.644 | 3.258 | 1.991 | 1.032 | 0.216 | Primary | 347
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Consumer Transformation | 7.456 | 6.98 | 6.294 | 5.505 | 4.918 | 4.31 | 3.555 | 0.34 | -5.126 | -9.145 | -12.837 | Primary | 348
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Consumer Transformation | 3.905 | 3.643 | 17.947 | 17.476 | 17.083 | 16.67 | 16.154 | 13.761 | 8.816 | 5.083 | 1.853 | Primary | 349
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Consumer Transformation | -0.178 | -0.315 | -0.507 | -0.738 | -0.933 | -1.133 | -1.371 | -2.417 | -4.468 | -6.161 | -7.761 | Primary | 350
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Consumer Transformation | 2.851 | 2.859 | 2.849 | 2.82 | 2.811 | 2.796 | 2.769 | 2.585 | 1.813 | 1.264 | 0.789 | Primary | 351
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Consumer Transformation | 10.428 | 10.133 | 9.673 | 9.121 | 8.708 | 8.282 | 7.755 | 5.557 | 1.449 | -1.636 | -4.45 | Primary | 352
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Consumer Transformation | 8.547 | 8.191 | 7.656 | 7.023 | 6.628 | 6.209 | 5.685 | 3.263 | -1.641 | -5.214 | -8.591 | Primary | 353
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Consumer Transformation | 12.473 | 12.36 | 12.175 | 11.948 | 11.778 | 11.593 | 11.357 | 10.231 | 8.506 | 7.329 | 6.283 | Primary | 354
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Consumer Transformation | 3.817 | 2.888 | 2.904 | 2.866 | 2.866 | 2.839 | 2.771 | 2.143 | -0.345 | -2.121 | -3.602 | Primary | 355
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Consumer Transformation | 15.285 | 15.209 | 15.1 | 14.953 | 14.818 | 14.662 | 14.477 | 13.291 | 10.888 | 9.134 | 7.64 | Primary | 356
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Consumer Transformation | 4.094 | 3.994 | 3.851 | 3.686 | 3.56 | 3.431 | 3.279 | 2.613 | 1.233 | 0.137 | -0.898 | Primary | 357
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Consumer Transformation | 2.456 | 2.39 | 2.287 | 2.161 | 2.073 | 1.981 | 1.866 | 1.375 | 0.193 | -0.721 | -1.562 | Primary | 358
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Consumer Transformation | 14.966 | 14.617 | 14.103 | 13.487 | 13.041 | 12.562 | 11.974 | 9.082 | 3.676 | -0.337 | -4.016 | Primary | 359
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Consumer Transformation | 1.958 | 1.803 | 1.516 | 1.137 | 0.821 | 0.48 | 0.03 | -2.053 | -7.037 | -10.948 | -14.476 | Primary | 360
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Consumer Transformation | 14.832 | 14.76 | 14.618 | 14.429 | 14.368 | 14.298 | 14.203 | 13.681 | 11.402 | 9.65 | 7.967 | Primary | 361
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Consumer Transformation | 4.717 | 4.617 | 4.483 | 4.326 | 4.188 | 4.046 | 3.878 | 3.135 | 1.83 | 0.811 | -0.119 | Primary | 362
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Consumer Transformation | 6.897 | 6.436 | 5.782 | 5.024 | 4.426 | 3.801 | 3.038 | -0.299 | -5.229 | -8.783 | -12.088 | Primary | 363
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Consumer Transformation | 12.608 | 12.252 | 11.756 | 11.191 | 10.784 | 10.364 | 9.859 | 7.723 | 4.122 | 1.396 | -1.248 | Primary | 364
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Consumer Transformation | 12.907 | 11.26 | 11.174 | 11.014 | 10.905 | 10.737 | 10.501 | 8.56 | 4.887 | 2.775 | 1.345 | Primary | 365
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Consumer Transformation | 2.917 | 2.637 | 2.333 | 2.103 | 1.906 | 1.705 | 1.458 | 0.467 | -0.588 | -1.229 | -1.763 | Primary | 366
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Consumer Transformation | 7.97 | 7.267 | 6.326 | 5.265 | 4.505 | 3.729 | 2.819 | -1.132 | -7.291 | -11.756 | -15.997 | Primary | 367
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Consumer Transformation | 8.537 | 8.535 | 8.526 | 8.511 | 8.496 | 8.478 | 8.454 | 8.31 | 8.12 | 7.933 | 7.745 | Primary | 368
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Consumer Transformation | 2.007 | 1.818 | 1.533 | 1.161 | 0.763 | 0.282 | -0.321 | -4.319 | -9.612 | -12.584 | -14.393 | Primary | 369
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Consumer Transformation | 11.771 | 11.39 | 10.916 | 10.459 | 10.154 | 9.832 | 9.439 | 7.597 | 3.115 | -0.345 | -3.534 | Primary | 370
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Consumer Transformation | 9.311 | 8.915 | 8.318 | 7.593 | 7.105 | 6.587 | 5.951 | 2.922 | -2.471 | -6.319 | -9.828 | Primary | 371
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Consumer Transformation | 0.886 | 0.783 | 0.635 | 0.45 | 0.276 | 0.072 | -0.178 | -1.722 | -3.736 | -4.944 | -5.799 | Primary | 372
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Consumer Transformation | 7.414 | 7.066 | 6.546 | 5.926 | 5.461 | 4.983 | 4.402 | 1.935 | -3.379 | -7.592 | -11.553 | Primary | 373
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Consumer Transformation | 0.9 | 0.869 | 0.775 | 0.636 | 0.586 | 0.524 | 0.432 | -0.084 | -2.409 | -4.158 | -5.755 | Primary | 374
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Consumer Transformation | 1.488 | 1.487 | 1.487 | 1.486 | 1.485 | 1.483 | 1.482 | 1.473 | 1.457 | 1.44 | 1.425 | Primary | 375
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 10.478 | 10.508 | 10.497 | 10.448 | 10.457 | 10.459 | 10.442 | 10.358 | 8.789 | 7.545 | 6.345 | Primary | 376
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Consumer Transformation | 7.122 | 7.084 | 7.017 | 6.931 | 6.879 | 6.822 | 6.746 | 6.403 | 5.479 | 4.781 | 4.111 | Primary | 377
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 8.498 | 8.413 | 8.289 | 8.143 | 8.009 | 7.872 | 7.707 | 7.03 | 6.172 | 5.555 | 5.012 | Primary | 378
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Consumer Transformation | 3.914 | 3.708 | 3.425 | 3.11 | 2.882 | 2.636 | 2.335 | 0.807 | -1.786 | -3.622 | -5.247 | Primary | 379
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Consumer Transformation | 14.545 | 14.254 | 13.851 | 14.369 | 13.918 | 13.461 | 12.926 | 10.67 | 7.246 | 4.709 | 2.475 | Primary | 380
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Consumer Transformation | 10.096 | 9.016 | 8.611 | 8.115 | 7.794 | 7.461 | 7.049 | 5.278 | 1.484 | -1.445 | -4.289 | Primary | 381
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Consumer Transformation | 3.259 | 3.081 | 2.843 | 2.561 | 2.28 | 1.972 | 1.597 | -0.432 | -3.443 | -5.587 | -7.346 | Primary | 382
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Consumer Transformation | 10.667 | 9.94 | 9.193 | 8.692 | 8.371 | 8.042 | 7.635 | 5.843 | 1.601 | -1.645 | -4.684 | Primary | 383
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Consumer Transformation | 10.773 | 10.722 | 10.648 | 10.554 | 10.498 | 10.438 | 10.371 | 9.989 | 8.566 | 7.263 | 5.965 | Primary | 384
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Consumer Transformation | -2.998 | -3.691 | -4.658 | -5.775 | -6.651 | -7.551 | -8.624 | -13.323 | -21.511 | -27.763 | -33.545 | Primary | 385
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Consumer Transformation | 7.014 | 6.331 | 5.465 | 4.607 | 4.013 | 3.409 | 2.682 | -0.29 | -5.009 | -8.275 | -11.316 | Primary | 386
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Consumer Transformation | 5.264 | 5.276 | 5.194 | 5.041 | 5.08 | 5.105 | 5.099 | 4.906 | 1.985 | -0.443 | -2.937 | Primary | 387
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Consumer Transformation | 17.262 | 14.224 | 14.034 | 13.813 | 13.635 | 13.454 | 13.247 | 12.301 | 10.22 | 8.433 | 6.672 | Primary | 388
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Consumer Transformation | 13.888 | 13.855 | 13.8 | 13.719 | 13.644 | 13.553 | 13.442 | 12.699 | 11.186 | 10.083 | 9.15 | Primary | 389
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Consumer Transformation | 9.622 | 9.429 | 9.188 | 8.891 | 8.591 | 8.246 | 7.845 | 5.264 | 1.343 | -1.397 | -3.58 | Primary | 390
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Consumer Transformation | 12.753 | 12.741 | 12.674 | 12.563 | 12.535 | 12.502 | 12.447 | 12.183 | 10.166 | 8.531 | 6.932 | Primary | 391
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Consumer Transformation | 11.523 | 11.567 | 11.575 | 11.553 | 11.574 | 11.588 | 11.585 | 11.552 | 10.761 | 10.176 | 9.615 | Primary | 392
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Consumer Transformation | 4.187 | 4.025 | 3.834 | 3.602 | 3.352 | 3.064 | 2.732 | 0.522 | -2.606 | -4.762 | -6.434 | Primary | 393
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Consumer Transformation | 16.339 | 16.273 | 16.164 | 16.024 | 15.961 | 15.888 | 15.798 | 15.212 | 13.424 | 12.037 | 10.746 | Primary | 394
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Consumer Transformation | 10.803 | 10.512 | 10.058 | 9.511 | 9.2 | 8.876 | 8.476 | 6.723 | 2.504 | -0.67 | -3.738 | Primary | 395
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Consumer Transformation | 10.321 | 10.212 | 10.001 | 9.718 | 9.611 | 9.489 | 9.327 | 8.408 | 5.015 | 2.443 | 0.022 | Primary | 396
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Consumer Transformation | 7.07 | 6.705 | 6.142 | 5.456 | 4.971 | 4.452 | 3.798 | 0.72 | -4.544 | -8.196 | -11.416 | Primary | 397
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Consumer Transformation | 4.522 | 4.149 | 3.631 | 3.042 | 2.592 | 2.111 | 1.532 | -1.364 | -6.375 | -9.908 | -12.979 | Primary | 398
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Consumer Transformation | 11.735 | 11.73 | 11.69 | 11.625 | 11.548 | 11.435 | 11.272 | 10.104 | 8.599 | 7.884 | 7.553 | Primary | 399
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Consumer Transformation | 15.409 | 15.085 | 14.586 | 13.978 | 13.63 | 13.275 | 12.842 | 11.012 | 6.837 | 3.628 | 0.461 | Primary | 400
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Consumer Transformation | 9.265 | 8.808 | 8.14 | 7.335 | 6.694 | 5.992 | 5.127 | 0.648 | -6.217 | -10.891 | -14.847 | Primary | 401
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Consumer Transformation | 3.291 | 3.174 | 3.012 | 3.326 | 3.172 | 3.014 | 2.823 | 1.971 | 0.624 | -0.42 | -1.393 | Primary | 402
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Consumer Transformation | 8.024 | 7.806 | 7.453 | 7.03 | 6.679 | 6.319 | 5.865 | 3.963 | -0.683 | -4.359 | -7.633 | Primary | 403
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Consumer Transformation | 4.125 | 3.915 | 3.611 | 3.263 | 3.046 | 2.825 | 2.554 | 1.426 | -0.771 | -2.428 | -4.058 | Primary | 404
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 12.299 | 12.288 | 12.251 | 12.192 | 12.162 | 12.126 | 12.076 | 11.778 | 10.696 | 9.799 | 8.929 | Primary | 405
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Consumer Transformation | 25.328 | 25.291 | 25.232 | 25.151 | 25.101 | 25.048 | 24.984 | 24.655 | 23.414 | 22.386 | 21.396 | Primary | 406
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Consumer Transformation | 14.613 | 14.455 | 14.244 | 13.996 | 13.764 | 13.519 | 13.227 | 11.834 | 10.13 | 9.017 | 8.144 | Primary | 407
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Consumer Transformation | 12.696 | 12.754 | 12.79 | 12.801 | 12.825 | 12.843 | 12.847 | 12.844 | 11.855 | 11.071 | 10.35 | Primary | 408
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Consumer Transformation | 19.833 | 19.816 | 19.79 | 19.752 | 19.727 | 19.701 | 19.672 | 19.52 | 18.819 | 18.185 | 17.55 | Primary | 409
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Consumer Transformation | 6.785 | 6.513 | 6.096 | 5.595 | 5.274 | 4.942 | 4.532 | 2.819 | -0.39 | -2.696 | -4.914 | Primary | 410
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Consumer Transformation | 22.482 | 22.48 | 22.406 | 22.273 | 22.23 | 22.173 | 22.076 | 21.549 | 19.146 | 17.298 | 15.562 | Primary | 411
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Consumer Transformation | 14.569 | 14.501 | 14.377 | 14.219 | 14.187 | 14.152 | 14.1 | 13.805 | 11.417 | 9.472 | 7.578 | Primary | 412
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Consumer Transformation | 4.73 | 4.642 | 4.508 | 4.347 | 4.248 | 4.142 | 4.009 | 3.411 | 2.234 | 1.369 | 0.548 | Primary | 413
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Consumer Transformation | 4.522 | 4.503 | 4.479 | 4.45 | 4.423 | 4.394 | 4.36 | 4.15 | 3.862 | 3.651 | 3.474 | Primary | 414
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Consumer Transformation | 15.693 | 15.625 | 15.507 | 15.342 | 15.231 | 15.105 | 14.949 | 13.996 | 11.342 | 9.294 | 7.432 | Primary | 415
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 9.653 | 9.512 | 9.295 | 9.035 | 8.823 | 8.603 | 8.33 | 7.15 | 4.96 | 3.315 | 1.877 | Primary | 416
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Consumer Transformation | 11.532 | 11.436 | 11.287 | 11.105 | 10.984 | 10.86 | 10.705 | 10.037 | 8.341 | 7.008 | 5.776 | Primary | 417
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Consumer Transformation | 2.323 | 2.177 | 1.987 | 1.777 | 1.57 | 1.358 | 1.106 | -0.009 | -1.757 | -3.179 | -4.459 | Primary | 418
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Consumer Transformation | 3.476 | 3.283 | 3.009 | 2.67 | 2.479 | 2.264 | 2.006 | 0.48 | -3.772 | -7.149 | -10.372 | Primary | 419
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Consumer Transformation | 18.932 | 18.915 | 18.883 | 18.837 | 18.804 | 18.76 | 18.703 | 18.297 | 17.577 | 17.122 | 16.775 | Primary | 420
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Consumer Transformation | 4.842 | 4.76 | 4.638 | 4.495 | 4.39 | 4.281 | 4.146 | 3.562 | 2.231 | 1.175 | 0.211 | Primary | 421
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Consumer Transformation | 14.795 | 14.782 | 14.754 | 14.726 | 14.713 | 14.692 | 14.655 | 14.385 | 13.294 | 12.45 | 11.709 | Primary | 422
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Consumer Transformation | 12.648 | 12.744 | 12.825 | 12.889 | 12.961 | 13.024 | 13.077 | 13.224 | 12.88 | 12.67 | 12.506 | Primary | 423
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Consumer Transformation | 2.211 | 1.901 | 1.464 | 0.95 | 0.524 | 0.081 | -0.453 | -2.852 | -5.899 | -7.946 | -9.712 | Primary | 424
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 5.914 | 5.885 | 5.829 | 5.754 | 5.714 | 5.669 | 5.612 | 5.285 | 4.207 | 3.366 | 2.579 | Primary | 425
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Consumer Transformation | 5.276 | 5.237 | 5.166 | 5.073 | 5.011 | 4.936 | 4.839 | 4.211 | 2.957 | 2.101 | 1.381 | Primary | 426
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Consumer Transformation | 5.241 | 4.912 | 4.451 | 3.911 | 3.483 | 3.032 | 2.491 | -0.03 | -4.34 | -7.597 | -10.559 | Primary | 427
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Consumer Transformation | 15.34 | 15.264 | 15.149 | 15.001 | 14.918 | 14.829 | 14.725 | 14.149 | 12.27 | 10.76 | 9.337 | Primary | 428
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Consumer Transformation | 8.149 | 7.571 | 6.842 | 6.128 | 5.513 | 4.879 | 4.094 | 0.792 | -4.752 | -8.959 | -12.704 | Primary | 429
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Consumer Transformation | 4.887 | 4.82 | 4.7 | 4.552 | 4.468 | 4.361 | 4.212 | 3.275 | -0.116 | -2.699 | -4.971 | Primary | 430
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Consumer Transformation | 10.384 | 10.081 | 9.591 | 8.98 | 8.566 | 8.141 | 7.623 | 5.372 | -0.501 | -5.239 | -9.729 | Primary | 431
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Consumer Transformation | 0.258 | 0.185 | 0.083 | -0.047 | -0.135 | -0.231 | -0.344 | -0.97 | -2.57 | -3.856 | -5.064 | Primary | 432
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Consumer Transformation | 13.431 | 13.124 | 12.674 | 12.162 | 11.775 | 11.37 | 10.867 | 8.646 | 4.604 | 1.62 | -1.083 | Primary | 433
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Consumer Transformation | 18.433 | 18.429 | 18.41 | 18.377 | 18.355 | 18.327 | 18.289 | 18.067 | 17.162 | 16.47 | 15.863 | Primary | 434
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Consumer Transformation | 12.617 | 12.397 | 12.1 | 11.758 | 11.586 | 11.405 | 11.198 | 10.165 | 7.329 | 4.986 | 2.566 | Primary | 435
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Consumer Transformation | 7.168 | 7.057 | 6.892 | 6.681 | 6.51 | 6.327 | 6.108 | 4.94 | 2.047 | -0.283 | -2.378 | Primary | 436
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Consumer Transformation | 8.254 | 8.13 | 7.917 | 7.628 | 7.433 | 7.199 | 6.906 | 4.929 | 0.176 | -3.388 | -6.482 | Primary | 437
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Consumer Transformation | 16.349 | 16.336 | 16.32 | 16.303 | 16.284 | 16.263 | 16.239 | 16.1 | 15.921 | 15.729 | 15.536 | Primary | 438
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Consumer Transformation | 16.963 | 16.877 | 16.731 | 16.544 | 16.38 | 16.206 | 15.984 | 15.012 | 13.117 | 11.687 | 10.418 | Primary | 439
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Consumer Transformation | 18.992 | 18.949 | 18.885 | 18.804 | 18.746 | 18.687 | 18.616 | 18.298 | 17.303 | 16.474 | 15.693 | Primary | 440
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Consumer Transformation | 9.081 | 8.526 | 7.888 | 7.351 | 7.028 | 6.695 | 6.286 | 4.53 | 0.48 | -2.559 | -5.482 | Primary | 441
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Consumer Transformation | 10.426 | 9.976 | 9.368 | 8.724 | 8.266 | 7.79 | 7.192 | 4.626 | 0.021 | -3.4 | -6.593 | Primary | 442
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Consumer Transformation | -6.477 | -6.357 | -6.261 | -6.186 | -6.11 | -6.047 | -6.003 | -5.92 | -6.391 | -6.652 | -6.819 | Primary | 443
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Consumer Transformation | 10.09 | 9.397 | 8.612 | 7.953 | 7.466 | 6.969 | 6.358 | 3.746 | -1.894 | -6.293 | -10.355 | Primary | 444
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Consumer Transformation | 11.425 | 11.32 | 11.15 | 10.921 | 10.766 | 10.585 | 10.36 | 8.949 | 5.42 | 2.771 | 0.409 | Primary | 445
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Consumer Transformation | 5.217 | 4.911 | 4.485 | 3.985 | 3.598 | 3.204 | 2.736 | 0.746 | -2.878 | -5.731 | -8.452 | Primary | 446
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Consumer Transformation | 24.502 | 24.485 | 24.4 | 24.254 | 24.219 | 24.176 | 24.107 | 23.72 | 20.927 | 18.692 | 16.563 | Primary | 447
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Consumer Transformation | 6.493 | 6.312 | 6.059 | 5.758 | 5.529 | 5.286 | 4.998 | 3.56 | 0.946 | -1.058 | -2.925 | Primary | 448
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Consumer Transformation | 6.768 | 6.759 | 6.743 | 6.722 | 6.709 | 6.694 | 6.676 | 6.59 | 6.409 | 6.276 | 6.153 | Primary | 449
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Consumer Transformation | 11.664 | 11.087 | 10.236 | 9.225 | 8.582 | 7.917 | 7.115 | 3.585 | -3.385 | -8.707 | -13.912 | Primary | 450
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Consumer Transformation | 21.999 | 22.028 | 22.029 | 21.995 | 21.935 | 21.832 | 21.682 | 20.317 | 18.512 | 17.721 | 17.463 | Primary | 451
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Consumer Transformation | 11.262 | 11.015 | 10.637 | 10.185 | 9.901 | 9.602 | 9.23 | 7.561 | 3.698 | 0.816 | -1.881 | Primary | 452
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Consumer Transformation | 12.127 | 12.015 | 11.836 | 11.581 | 11.294 | 10.935 | 10.486 | 7.253 | 2.006 | -1.266 | -3.492 | Primary | 453
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Consumer Transformation | 0.761 | 0.674 | 0.547 | 0.39 | 0.245 | 0.086 | -0.11 | -1.131 | -2.855 | -4.142 | -5.268 | Primary | 454
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Consumer Transformation | 7.064 | 1.318 | 0.97 | 0.565 | 0.246 | -0.083 | -0.478 | -2.229 | -4.927 | -6.876 | -8.649 | Primary | 455
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 456
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Consumer Transformation | 5.062 | 4.802 | 4.439 | 4.018 | 3.712 | 3.394 | 3.014 | 1.321 | -1.652 | -3.984 | -6.255 | Primary | 457
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Consumer Transformation | 12.931 | 12.743 | 12.463 | 12.114 | 11.791 | 11.392 | 10.88 | 7.412 | 2.134 | -0.907 | -2.913 | Primary | 458
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Consumer Transformation | 2.303 | 2.066 | 1.713 | 1.322 | 1.08 | 0.817 | 0.478 | -1.114 | -4.319 | -6.532 | -8.536 | Primary | 459
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Consumer Transformation | 2.25 | 2.05 | 1.808 | 1.598 | 1.463 | 1.322 | 1.148 | 0.442 | -0.773 | -1.621 | -2.442 | Primary | 460
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Consumer Transformation | 12.982 | 12.835 | 12.581 | 12.261 | 12.092 | 11.91 | 11.673 | 10.575 | 7.763 | 5.648 | 3.638 | Primary | 461
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Consumer Transformation | 7.9 | 7.95 | 7.984 | 8.01 | 8.041 | 8.067 | 8.076 | 8.1 | 6.897 | 5.96 | 5.123 | Primary | 462
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Consumer Transformation | 13.581 | 13.513 | 13.377 | 13.186 | 13.127 | 13.057 | 12.963 | 12.432 | 9.995 | 8.093 | 6.249 | Primary | 463
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Consumer Transformation | 7.113 | 6.719 | 6.178 | 5.552 | 5.001 | 4.427 | 3.733 | 0.62 | -3.691 | -6.954 | -9.924 | Primary | 464
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Consumer Transformation | 12.796 | 12.767 | 12.678 | 12.535 | 12.445 | 12.311 | 12.124 | 10.608 | 7.829 | 6.192 | 5.032 | Primary | 465
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Consumer Transformation | 13.776 | 13.821 | 13.861 | 13.893 | 13.926 | 13.956 | 13.982 | 14.089 | 13.941 | 13.826 | 13.719 | Primary | 466
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Consumer Transformation | 5.911 | 5.894 | 5.862 | 5.824 | 5.803 | 5.779 | 5.745 | 5.595 | 5.348 | 5.174 | 4.995 | Primary | 467
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Consumer Transformation | 14.197 | 14.231 | 14.242 | 14.227 | 14.228 | 14.225 | 14.211 | 14.131 | 13.012 | 12.146 | 11.366 | Primary | 468
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Consumer Transformation | -4.042 | -4.333 | -4.788 | -5.344 | -5.685 | -6.039 | -6.471 | -8.374 | -12.308 | -15.199 | -17.932 | Primary | 469
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Consumer Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 470
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Consumer Transformation | 8.941 | 7.827 | 7.179 | 6.417 | 5.867 | 5.304 | 4.631 | 1.739 | -4.291 | -9.025 | -13.456 | Primary | 471
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Consumer Transformation | 8.894 | 8.275 | 7.42 | 6.493 | 11.899 | 11.287 | 10.529 | 7.324 | 1.465 | -2.866 | -7.075 | Primary | 472
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Consumer Transformation | 4.05 | 4.137 | 4.198 | 4.226 | 4.25 | 4.264 | 4.259 | 4.148 | 2.408 | 0.985 | -0.263 | Primary | 473
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Consumer Transformation | 2.286 | 1.973 | 1.529 | 0.998 | 0.453 | -0.105 | -0.769 | -3.557 | -8.617 | -12.747 | -16.406 | Primary | 474
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Consumer Transformation | 14.378 | 14.189 | 13.908 | 13.586 | 13.338 | 13.083 | 12.766 | 11.401 | 8.165 | 5.615 | 3.288 | Primary | 475
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Consumer Transformation | 5.589 | 5.071 | 4.288 | 3.345 | 2.718 | 2.06 | 1.254 | -2.372 | -8.741 | -13.401 | -17.896 | Primary | 476
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Consumer Transformation | 5.165 | 4.166 | 3.809 | 3.432 | 3.182 | 2.907 | 2.549 | 0.792 | -3.1 | -5.956 | -8.511 | Primary | 477
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Consumer Transformation | 15.084 | 14.916 | 14.665 | 14.379 | 14.21 | 14.036 | 13.817 | 12.884 | 10.696 | 9.004 | 7.345 | Primary | 478
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Consumer Transformation | 4.16 | 3.861 | 3.405 | 2.865 | 2.511 | 2.133 | 1.656 | -0.579 | -4.896 | -8.026 | -10.936 | Primary | 479
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Consumer Transformation | 7.896 | 7.655 | 7.321 | 6.909 | 6.626 | 6.32 | 5.961 | 3.983 | -0.182 | -3.294 | -6.157 | Primary | 480
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Consumer Transformation | 8.904 | 8.455 | 7.806 | 7.042 | 6.527 | 5.995 | 5.35 | 2.585 | -2.016 | -5.221 | -8.283 | Primary | 481
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Consumer Transformation | 6.802 | 6.457 | 5.984 | 5.44 | 4.963 | 4.478 | 3.901 | 1.477 | -1.694 | -3.919 | -5.847 | Primary | 482
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Consumer Transformation | 2.255 | 1.493 | 0.591 | -0.209 | -0.862 | -1.536 | -2.37 | -5.943 | -13.014 | -18.441 | -23.214 | Primary | 483
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Consumer Transformation | 9.656 | 9.111 | 8.397 | 7.676 | 7.247 | 6.806 | 6.262 | 3.94 | -1.135 | -4.967 | -8.679 | Primary | 484
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Consumer Transformation | 10.588 | 10.065 | 9.394 | 8.726 | 8.214 | 7.664 | 6.975 | 3.639 | -1.77 | -5.469 | -8.636 | Primary | 485
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Consumer Transformation | 13.419 | 13.428 | 13.39 | 13.303 | 13.244 | 13.154 | 13.026 | 11.991 | 9.54 | 8.003 | 6.868 | Primary | 486
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Consumer Transformation | 8.81 | 8.687 | 8.497 | 8.267 | 8.094 | 7.912 | 7.678 | 6.63 | 4.361 | 2.608 | 1.001 | Primary | 487
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Consumer Transformation | 3.591 | 3.535 | 3.419 | 3.255 | 3.165 | 3.051 | 2.896 | 1.848 | -0.295 | -1.637 | -2.718 | Primary | 488
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Consumer Transformation | 12.891 | 12.662 | 12.306 | 11.879 | 11.596 | 11.304 | 10.94 | 9.396 | 6.05 | 3.498 | 1.09 | Primary | 489
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Consumer Transformation | 17.595 | 17.494 | 17.314 | 17.081 | 16.887 | 16.685 | 16.429 | 15.336 | 13.351 | 11.84 | 10.483 | Primary | 490
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Consumer Transformation | 15.444 | 15.336 | 15.169 | 14.955 | 14.855 | 14.75 | 14.627 | 14.021 | 11.805 | 10.002 | 8.183 | Primary | 491
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Consumer Transformation | 4.162 | 4.005 | 3.774 | 3.466 | 3.198 | 2.867 | 2.457 | -0.421 | -5.284 | -8.397 | -10.732 | Primary | 492
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Consumer Transformation | 10.147 | 10.195 | 10.213 | 10.197 | 10.208 | 10.207 | 10.186 | 9.962 | 8.382 | 7.226 | 6.222 | Primary | 493
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Consumer Transformation | -1.195 | -1.286 | -1.422 | -1.594 | -1.701 | -1.822 | -1.971 | -2.904 | -5.073 | -6.676 | -8.099 | Primary | 494
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Consumer Transformation | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary | 495
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Consumer Transformation | 6.75 | 6.228 | 5.552 | 4.85 | 4.389 | 3.9 | 3.292 | 0.491 | -4.258 | -7.608 | -10.768 | Primary | 496
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Consumer Transformation | 14.344 | 14.023 | 13.545 | 12.966 | 12.631 | 12.284 | 11.861 | 9.965 | 5.868 | 2.702 | -0.412 | Primary | 497
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Consumer Transformation | 3.456 | 3.311 | 3.111 | 2.881 | 2.709 | 2.532 | 2.32 | 1.389 | -0.296 | -1.633 | -2.933 | Primary | 498
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Consumer Transformation | 8.846 | 8.553 | 8.135 | 7.586 | 7.101 | 6.506 | 5.773 | 0.581 | -7.702 | -12.839 | -16.61 | Primary | 499
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Consumer Transformation | 13.018 | 12.504 | 11.884 | 11.301 | 10.878 | 10.44 | 9.898 | 7.545 | 3.268 | 0.083 | -2.895 | Primary | 500
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Consumer Transformation | 5.061 | 4.97 | 4.842 | 4.696 | 4.578 | 4.459 | 4.317 | 3.704 | 2.496 | 1.523 | 0.619 | Primary | 501
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Consumer Transformation | 6.722 | 6.285 | 5.667 | 4.938 | 4.413 | 3.873 | 3.228 | 0.433 | -5.373 | -9.985 | -14.454 | Primary | 502
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Consumer Transformation | 10.158 | 9.88 | 9.44 | 8.907 | 8.545 | 8.172 | 7.712 | 5.727 | 0.992 | -2.666 | -6.032 | Primary | 503
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Consumer Transformation | 14.827 | 14.483 | 14.047 | 13.619 | 13.283 | 12.944 | 12.537 | 10.887 | 7.675 | 5.213 | 2.979 | Primary | 504
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Consumer Transformation | 6.44 | 6.242 | 5.9 | 5.458 | 5.209 | 4.94 | 4.597 | 3.017 | -0.992 | -3.976 | -6.795 | Primary | 505
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Consumer Transformation | 14.012 | 13.636 | 13.141 | 12.575 | 12.019 | 11.434 | 10.734 | 7.452 | 2.522 | -1.189 | -4.407 | Primary | 506
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Consumer Transformation | 13.128 | 13.084 | 13.006 | 12.9 | 12.855 | 12.806 | 12.744 | 12.423 | 11.001 | 9.852 | 8.735 | Primary | 507
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Consumer Transformation | 9.269 | 8.928 | 8.447 | 7.904 | 7.527 | 7.126 | 6.635 | 4.289 | 0.547 | -2.01 | -4.342 | Primary | 508
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Consumer Transformation | 12.454 | 12.474 | 12.45 | 12.383 | 12.338 | 12.266 | 12.156 | 11.3 | 9.473 | 8.368 | 7.566 | Primary | 509
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Consumer Transformation | 6.959 | 6.907 | 6.769 | 6.557 | 6.447 | 6.301 | 6.099 | 4.7 | 1.412 | -0.743 | -2.538 | Primary | 510
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Consumer Transformation | 25.647 | 25.545 | 25.378 | 25.16 | 24.983 | 24.779 | 24.524 | 23.02 | 20.562 | 18.924 | 17.588 | Primary | 511
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Consumer Transformation | 4.555 | 4.365 | 4.125 | 3.844 | 3.631 | 3.408 | 3.158 | 1.756 | -1.852 | -5.017 | -8.038 | Primary | 512
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Consumer Transformation | 1.869 | 1.829 | 1.767 | 1.692 | 1.63 | 1.564 | 1.483 | 1.135 | 0.684 | 0.336 | 0.008 | Primary | 513
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Consumer Transformation | 12.478 | 12.178 | 11.776 | 11.321 | 10.997 | 10.661 | 10.257 | 8.432 | 4.775 | 1.934 | -0.79 | Primary | 514
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Consumer Transformation | 10.198 | 10.205 | 10.175 | 10.11 | 10.097 | 10.072 | 10.024 | 9.685 | 8.157 | 7.007 | 5.953 | Primary | 515
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Consumer Transformation | 10.309 | 10.239 | 10.078 | 9.836 | 9.708 | 9.569 | 9.39 | 8.438 | 3.468 | -0.702 | -4.59 | Primary | 516
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Consumer Transformation | 0.736 | 0.678 | 0.592 | 0.48 | 0.394 | 0.295 | 0.177 | -0.548 | -2.095 | -3.246 | -4.259 | Primary | 517
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Consumer Transformation | 9.459 | 9.486 | 9.456 | 9.35 | 9.192 | 8.954 | 8.628 | 5.868 | 1.184 | -1.411 | -2.894 | Primary | 518
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Consumer Transformation | 16.447 | 16.404 | 16.336 | 16.263 | 16.219 | 16.165 | 16.087 | 15.662 | 14.557 | 13.778 | 13.093 | Primary | 519
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Consumer Transformation | 8.965 | 7.81 | 7.275 | 6.644 | 6.147 | 5.633 | 5.019 | 2.255 | -3.197 | -7.531 | -11.602 | Primary | 520
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Consumer Transformation | 12.233 | 12.129 | 11.941 | 11.707 | 11.544 | 11.372 | 11.15 | 10.217 | 8.045 | 6.372 | 4.856 | Primary | 521
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Consumer Transformation | 18.152 | 18.221 | 18.211 | 18.115 | 17.961 | 17.708 | 17.34 | 14.216 | 9.921 | 7.914 | 7.101 | Primary | 522
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Consumer Transformation | 10.205 | 9.84 | 9.269 | 8.581 | 8.192 | 7.781 | 7.261 | 4.86 | -0.663 | -4.758 | -8.64 | Primary | 523
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Consumer Transformation | 4.303 | 4.245 | 4.159 | 4.055 | 3.981 | 3.902 | 3.805 | 3.374 | 2.629 | 2.052 | 1.503 | Primary | 524
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Consumer Transformation | 9.451 | 9.111 | 8.653 | 8.174 | 7.904 | 7.62 | 7.262 | 5.637 | 1.64 | -1.348 | -4.153 | Primary | 525
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 15.277 | 15.128 | 14.892 | 14.585 | 14.382 | 14.158 | 13.89 | 12.445 | 8.775 | 5.859 | 3.111 | Primary | 526
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Consumer Transformation | 13.7 | 13.582 | 13.381 | 13.095 | 12.902 | 12.687 | 12.43 | 10.954 | 6.325 | 2.538 | -1.031 | Primary | 527
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Consumer Transformation | 13.396 | 13.406 | 13.385 | 13.335 | 13.311 | 13.276 | 13.217 | 12.828 | 11.371 | 10.362 | 9.517 | Primary | 528
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Consumer Transformation | 8.171 | 8.206 | 8.2 | 8.158 | 8.186 | 8.21 | 8.22 | 8.228 | 6.921 | 5.842 | 4.773 | Primary | 529
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Consumer Transformation | 17.576 | 17.445 | 17.24 | 16.994 | 16.834 | 16.667 | 16.461 | 15.561 | 13.977 | 12.875 | 11.84 | Primary | 530
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Consumer Transformation | 5.826 | 5.829 | 5.817 | 5.789 | 5.754 | 5.706 | 5.642 | 5.148 | 4.241 | 3.526 | 2.918 | Primary | 531
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Consumer Transformation | 2.151 | 1.649 | 1.004 | 0.362 | -0.047 | -0.468 | -0.99 | -3.229 | -8.104 | -11.778 | -15.236 | Primary | 532
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Consumer Transformation | 12.717 | 12.348 | 11.871 | 11.382 | 11.026 | 10.661 | 10.217 | 8.341 | 4.476 | 1.539 | -1.157 | Primary | 533
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Consumer Transformation | 10 | 9.485 | 8.775 | 8.01 | 7.522 | 6.996 | 6.342 | 3.109 | -2.959 | -7.113 | -10.768 | Primary | 534
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Consumer Transformation | 11.65 | 11.674 | 11.658 | 11.598 | 11.539 | 11.449 | 11.313 | 10.223 | 8.224 | 7.115 | 6.428 | Primary | 535
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Consumer Transformation | 16.035 | 15.816 | 15.473 | 15.061 | 14.802 | 14.534 | 14.2 | 12.788 | 10.062 | 8.044 | 6.121 | Primary | 536
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Consumer Transformation | 12.896 | 12.792 | 12.603 | 12.352 | 12.139 | 11.913 | 11.621 | 10.313 | 7.187 | 4.765 | 2.649 | Primary | 537
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Consumer Transformation | 9.414 | 9.157 | 8.751 | 8.257 | 7.928 | 7.569 | 7.11 | 4.836 | 0.581 | -2.343 | -4.926 | Primary | 538
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Consumer Transformation | 11.539 | 9.792 | 9.59 | 9.326 | 9.167 | 9.001 | 8.786 | 7.888 | 5.284 | 3.222 | 1.246 | Primary | 539
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Consumer Transformation | 5.204 | 5.115 | 4.991 | 4.856 | 4.741 | 4.62 | 4.473 | 3.841 | 2.864 | 2.134 | 1.472 | Primary | 540
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Consumer Transformation | 14.274 | 13.825 | 13.187 | 12.463 | 11.93 | 11.376 | 10.691 | 7.746 | 2.974 | -0.572 | -3.935 | Primary | 541
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Consumer Transformation | 3.133 | 2.796 | 2.259 | 1.607 | 1.113 | 0.601 | -0.04 | -2.775 | -8.925 | -13.69 | -17.994 | Primary | 542
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Consumer Transformation | 14.842 | 14.561 | 14.156 | 13.703 | 13.386 | 13.053 | 12.638 | 10.837 | 7.694 | 5.411 | 3.275 | Primary | 543
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Consumer Transformation | 7.077 | 6.605 | 5.928 | 5.162 | 4.67 | 4.16 | 3.53 | 0.846 | -4.911 | -9.288 | -13.526 | Primary | 544
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Consumer Transformation | 19.376 | 19.432 | 19.412 | 19.315 | 19.281 | 19.227 | 19.127 | 18.454 | 14.844 | 11.992 | 9.418 | Primary | 545
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Consumer Transformation | 12.535 | 12.382 | 12.168 | 11.926 | 11.722 | 11.507 | 11.242 | 10.048 | 8.078 | 6.752 | 5.662 | Primary | 546
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Consumer Transformation | 4.577 | 4.259 | 3.793 | 3.233 | 2.823 | 2.39 | 1.857 | -0.634 | -5.127 | -8.516 | -11.679 | Primary | 547
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Consumer Transformation | 8.789 | 8.079 | 7.151 | 6.109 | 5.039 | 3.936 | 2.629 | -3.128 | -10.799 | -16.535 | -21.363 | Primary | 548
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Consumer Transformation | 4.565 | 4.228 | 3.774 | 3.296 | 2.918 | 2.526 | 2.04 | -0.109 | -5.205 | -9.24 | -12.893 | Primary | 549
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Consumer Transformation | 12.946 | 12.453 | 11.779 | 11.01 | 10.489 | 9.959 | 9.332 | 6.69 | 2.105 | -1.396 | -4.846 | Primary | 550
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Consumer Transformation | 20.883 | 17.794 | 17.829 | 17.857 | 17.883 | 17.907 | 17.931 | 18.036 | 17.809 | 17.627 | 17.466 | Primary | 551
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Consumer Transformation | 3.507 | 3.302 | 3.016 | 2.66 | 2.355 | 1.987 | 1.541 | -1.506 | -6.436 | -9.617 | -12.085 | Primary | 552
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Consumer Transformation | 13.874 | 13.764 | 13.574 | 13.338 | 13.274 | 13.202 | 13.104 | 12.577 | 9.732 | 7.403 | 5.054 | Primary | 553
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Consumer Transformation | 14.304 | 14.363 | 14.405 | 14.435 | 14.487 | 14.536 | 14.576 | 14.738 | 14.462 | 14.249 | 14.022 | Primary | 554
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Consumer Transformation | 15.689 | 15.726 | 15.742 | 15.738 | 15.755 | 15.768 | 15.769 | 15.758 | 15.023 | 14.443 | 13.892 | Primary | 555
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Consumer Transformation | 9.621 | 9.06 | 8.251 | 7.305 | 6.642 | 5.961 | 5.142 | 1.622 | -4.211 | -8.489 | -12.554 | Primary | 556
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Consumer Transformation | 14.757 | 14.657 | 14.502 | 14.304 | 14.211 | 14.108 | 13.987 | 13.257 | 10.509 | 8.226 | 6.017 | Primary | 557
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Consumer Transformation | 6.032 | 5.96 | 5.806 | 5.587 | 5.5 | 5.404 | 5.274 | 4.592 | 1.182 | -1.539 | -4.13 | Primary | 558
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Consumer Transformation | 14.001 | 13.819 | 13.535 | 13.191 | 12.935 | 12.665 | 12.327 | 10.819 | 8.068 | 6.107 | 4.344 | Primary | 559
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Consumer Transformation | 17.532 | 13.967 | 13.916 | 13.858 | 13.816 | 13.77 | 13.704 | 13.434 | 13.032 | 12.799 | 12.61 | Primary | 560
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Consumer Transformation | 10.948 | 10.691 | 10.337 | 9.944 | 9.678 | 9.399 | 9.061 | 7.516 | 4.83 | 2.851 | 0.958 | Primary | 561
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Consumer Transformation | 2.71 | 2.514 | 2.232 | 1.895 | 1.64 | 1.357 | 1.014 | -0.877 | -3.772 | -5.667 | -7.233 | Primary | 562
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Consumer Transformation | 11.13 | 10.751 | 10.227 | 9.663 | 9.311 | 8.949 | 8.503 | 6.685 | 3.504 | 1.191 | -1.136 | Primary | 563
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Consumer Transformation | 12.603 | 12.39 | 12.058 | 11.662 | 11.42 | 11.165 | 10.843 | 9.405 | 6.373 | 4.146 | 2.045 | Primary | 564
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Consumer Transformation | 5.61 | 5.455 | 5.223 | 4.908 | 4.623 | 4.287 | 3.88 | 1.176 | -4.281 | -8.247 | -11.508 | Primary | 565
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Consumer Transformation | 16.526 | 16.384 | 16.187 | 15.952 | 15.755 | 15.55 | 15.306 | 14.174 | 12.195 | 10.638 | 9.217 | Primary | 566
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Consumer Transformation | 11.725 | 9.958 | 9.638 | 9.234 | 8.946 | 8.618 | 8.229 | 5.746 | 0.211 | -3.901 | -7.451 | Primary | 567
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Consumer Transformation | 4.698 | 4.576 | 4.411 | 4.22 | 4.063 | 3.901 | 3.707 | 2.874 | 1.679 | 0.772 | -0.081 | Primary | 568
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Consumer Transformation | 14.8 | 14.512 | 14.079 | 13.563 | 13.195 | 12.813 | 12.344 | 10.344 | 7.126 | 4.882 | 2.834 | Primary | 569
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Consumer Transformation | 0.025 | -0.152 | -0.401 | -0.694 | -0.946 | -1.212 | -1.536 | -3.07 | -5.88 | -8.018 | -9.927 | Primary | 570
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Consumer Transformation | 9.318 | 8.976 | 8.487 | 7.91 | 7.47 | 7.013 | 6.461 | 3.995 | -0.884 | -4.686 | -8.257 | Primary | 571
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Consumer Transformation | 8.424 | 8.121 | 7.646 | 7.068 | 6.683 | 6.274 | 5.756 | 3.41 | -1.281 | -4.72 | -7.914 | Primary | 572
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Consumer Transformation | 5.533 | 5.087 | 4.452 | 3.696 | 3.142 | 2.564 | 1.868 | -1.269 | -7.744 | -12.851 | -17.77 | Primary | 573
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Consumer Transformation | 16.05 | 15.755 | 15.31 | 14.775 | 14.39 | 13.98 | 13.466 | 11.12 | 7.191 | 4.455 | 1.972 | Primary | 574
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Consumer Transformation | 8.271 | 8.311 | 8.307 | 8.256 | 8.255 | 8.238 | 8.197 | 7.809 | 5.918 | 4.581 | 3.439 | Primary | 575
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Consumer Transformation | 16.408 | 17.192 | 16.903 | 8.368 | 8.055 | 7.735 | 7.35 | 5.688 | 2.376 | -0.34 | -2.788 | Primary | 576
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Consumer Transformation | 10.962 | 10.51 | 9.874 | 9.121 | 8.502 | 7.861 | 7.093 | 3.682 | -1.612 | -5.506 | -9.015 | Primary | 577
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Consumer Transformation | 8.803 | 8.813 | 8.785 | 8.719 | 8.709 | 8.69 | 8.652 | 8.388 | 6.735 | 5.451 | 4.25 | Primary | 578
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Consumer Transformation | 10.772 | 10.305 | 9.639 | 8.866 | 8.348 | 7.816 | 7.165 | 4.424 | -0.564 | -4.27 | -7.803 | Primary | 579
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Consumer Transformation | 5.074 | 4.55 | 3.835 | 2.979 | 2.245 | 1.457 | 0.511 | -4.293 | -12.021 | -17.852 | -23.137 | Primary | 580
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Consumer Transformation | 13.01 | 13.079 | 13.144 | 13.2 | 13.253 | 13.303 | 13.351 | 13.554 | 13.479 | 13.426 | 13.381 | Primary | 581
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Consumer Transformation | 13.761 | 13.852 | 13.925 | 13.976 | 14.008 | 14.019 | 14.007 | 13.677 | 12.888 | 12.522 | 12.375 | Primary | 582
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Consumer Transformation | 2.767 | 2.852 | 2.926 | 2.988 | 3.049 | 3.105 | 3.151 | 3.327 | 3.089 | 2.942 | 2.829 | Primary | 583
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Consumer Transformation | 6.342 | 6.184 | 5.963 | 5.725 | 5.574 | 5.416 | 5.213 | 4.318 | 2.368 | 0.989 | -0.242 | Primary | 584
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Consumer Transformation | 1.865 | 1.707 | 1.503 | 1.281 | 1.083 | 0.877 | 0.629 | -0.521 | -2.164 | -3.363 | -4.402 | Primary | 585
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Consumer Transformation | 12.678 | 12.433 | 12.064 | 11.612 | 11.246 | 10.852 | 10.373 | 8.054 | 4.345 | 1.75 | -0.442 | Primary | 586
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Consumer Transformation | 12.617 | 10.64 | 10.646 | 10.629 | 10.607 | 10.574 | 10.521 | 10.138 | 8.595 | 7.487 | 6.589 | Primary | 587
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Consumer Transformation | 9.171 | 8.791 | 15.295 | 14.798 | 14.438 | 14.062 | 13.591 | 11.574 | 7.753 | 4.895 | 2.252 | Primary | 588
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Consumer Transformation | 11.49 | 11.383 | 11.223 | 11.017 | 10.896 | 10.755 | 10.586 | 9.443 | 6.385 | 4.011 | 1.852 | Primary | 589
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Consumer Transformation | 3.11 | 1.442 | 0.91 | 0.486 | 0.177 | -0.148 | -0.559 | -2.432 | -7.286 | -11.132 | -14.648 | Primary | 590
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Consumer Transformation | 12.954 | 12.932 | 12.888 | 12.822 | 12.797 | 12.768 | 12.729 | 12.503 | 11.457 | 10.54 | 9.623 | Primary | 591
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Consumer Transformation | 8.521 | 8.363 | 15.074 | 14.702 | 14.511 | 14.304 | 14.029 | 12.728 | 9.095 | 6.394 | 3.852 | Primary | 592
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Consumer Transformation | 5.153 | 3.919 | 3.314 | 2.82 | 2.418 | 1.99 | 1.464 | -1.134 | -5.931 | -9.462 | -12.591 | Primary | 593
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Consumer Transformation | 10.172 | 9.698 | 8.993 | 8.166 | 7.672 | 7.163 | 6.542 | 3.929 | -1.546 | -5.678 | -9.732 | Primary | 594
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Consumer Transformation | 12.836 | 12.711 | 10.432 | 10.17 | 9.931 | 9.625 | 9.238 | 6.402 | 2.286 | -0.094 | -1.677 | Primary | 595
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Consumer Transformation | 9.441 | 9.016 | 8.419 | 7.731 | 7.239 | 6.724 | 6.097 | 3.239 | -1.144 | -4.262 | -7.159 | Primary | 596
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Consumer Transformation | 7.784 | 5.814 | 5.349 | 4.842 | 4.516 | 4.174 | 3.749 | 1.826 | -2.653 | -6.033 | -9.187 | Primary | 597
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Consumer Transformation | 8.563 | 7.895 | 7.965 | 7.99 | 7.996 | 7.976 | 7.926 | 7.324 | 5.259 | 3.963 | 3.052 | Primary | 598
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Consumer Transformation | 18.889 | 18.869 | 18.818 | 18.73 | 18.629 | 18.491 | 18.31 | 16.893 | 14.705 | 13.536 | 12.876 | Primary | 599
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Consumer Transformation | 8.635 | 8.514 | 8.28 | 7.979 | 7.816 | 7.645 | 7.416 | 6.452 | 3.671 | 1.504 | -0.614 | Primary | 600
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Consumer Transformation | 10.564 | 10.397 | 10.14 | 9.824 | 9.497 | 9.146 | 8.71 | 6.657 | 3.272 | 0.714 | -1.416 | Primary | 601
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Consumer Transformation | 12.427 | 12.183 | 11.8 | 11.327 | 11.041 | 10.744 | 10.377 | 8.789 | 4.759 | 1.67 | -1.273 | Primary | 602
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Consumer Transformation | 12.365 | 12.35 | 12.286 | 12.186 | 12.156 | 12.115 | 12.051 | 11.623 | 9.915 | 8.7 | 7.592 | Primary | 603
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Consumer Transformation | 8.405 | 8.529 | 8.644 | 8.758 | 8.868 | 8.967 | 9.053 | 9.407 | 9.081 | 8.841 | 8.626 | Primary | 604
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Consumer Transformation | 8.256 | 6.392 | 6.219 | 6.001 | 5.943 | 5.865 | 5.746 | 4.931 | 1.801 | -0.53 | -2.708 | Primary | 605
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Consumer Transformation | 10.373 | 9.199 | 9.267 | 9.311 | 9.359 | 9.402 | 9.432 | 9.555 | 8.801 | 8.226 | 7.707 | Primary | 606
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Consumer Transformation | 1.697 | 1.513 | 1.261 | 0.969 | 0.745 | 0.51 | 0.226 | -1.065 | -3.338 | -5.125 | -6.84 | Primary | 607
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Consumer Transformation | 3.426 | 3.388 | 3.328 | 3.261 | 3.248 | 3.233 | 3.21 | 3.093 | 2.284 | 1.629 | 0.943 | Primary | 608
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Consumer Transformation | 13.863 | 13.78 | 13.643 | 13.458 | 13.307 | 13.123 | 12.894 | 11.366 | 8.823 | 7.229 | 6.019 | Primary | 609
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Consumer Transformation | 24.617 | 24.651 | 24.681 | 24.696 | 24.708 | 24.718 | 24.726 | 24.735 | 24.11 | 23.535 | 22.977 | Primary | 610
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Consumer Transformation | 14.97 | 14.996 | 14.993 | 14.968 | 14.973 | 14.974 | 14.961 | 14.914 | 14.066 | 13.378 | 12.719 | Primary | 611
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Consumer Transformation | -0.824 | -0.922 | -1.07 | -1.263 | -1.419 | -1.591 | -1.793 | -2.919 | -5.25 | -7.12 | -8.832 | Primary | 612
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Consumer Transformation | 3.752 | 3.528 | 3.208 | 2.784 | 2.426 | 1.996 | 1.473 | -2.09 | -8.865 | -13.574 | -17.439 | Primary | 613
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Consumer Transformation | 11.081 | 10.898 | 10.584 | 10.192 | 9.946 | 9.691 | 9.366 | 8.014 | 4.829 | 2.424 | 0.151 | Primary | 614
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Consumer Transformation | 11.733 | 11.844 | 11.939 | 12.018 | 12.082 | 12.129 | 12.156 | 12.095 | 11.776 | 11.706 | 11.764 | Primary | 615
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Consumer Transformation | 8.611 | 8.219 | 7.639 | 6.945 | 6.449 | 5.922 | 5.28 | 2.161 | -3.996 | -8.532 | -12.605 | Primary | 616
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Consumer Transformation | 17.103 | 16.434 | 16.358 | 16.261 | 16.203 | 16.144 | 16.076 | 15.735 | 14.213 | 12.881 | 11.581 | Primary | 617
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Consumer Transformation | 4.926 | 4.616 | 4.226 | 3.846 | 3.539 | 3.227 | 2.848 | 1.291 | -1.812 | -4.232 | -6.408 | Primary | 618
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Consumer Transformation | 8.595 | 8.368 | 7.972 | 7.459 | 7.08 | 6.685 | 6.189 | 4.05 | -0.953 | -4.931 | -8.63 | Primary | 619
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Consumer Transformation | -1.179 | -1.381 | -1.672 | -2.008 | -2.236 | -2.472 | -2.759 | -4.014 | -7.094 | -9.521 | -11.815 | Primary | 620
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Consumer Transformation | 15.398 | 15.355 | 15.278 | 15.159 | 15.043 | 14.905 | 14.734 | 13.572 | 10.912 | 9.005 | 7.444 | Primary | 621
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Consumer Transformation | 15.759 | 15.175 | 14.591 | 14.209 | 13.892 | 13.557 | 13.144 | 11.187 | 7.644 | 5.049 | 2.808 | Primary | 622
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Consumer Transformation | 10.773 | 10.406 | 9.841 | 9.17 | 8.756 | 8.323 | 7.786 | 5.489 | 1.402 | -1.523 | -4.404 | Primary | 623
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Consumer Transformation | 24.272 | 24.316 | 24.355 | 24.394 | 24.433 | 24.468 | 24.498 | 24.621 | 24.437 | 24.291 | 24.157 | Primary | 624
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Consumer Transformation | 8.481 | 8.512 | 8.538 | 8.558 | 8.575 | 8.589 | 8.599 | 8.63 | 7.687 | 6.93 | 6.259 | Primary | 625
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Consumer Transformation | 11.261 | 10.953 | 10.471 | 9.887 | 9.533 | 9.169 | 8.718 | 6.853 | 3.094 | 0.274 | -2.516 | Primary | 626
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Consumer Transformation | -0.7 | -0.722 | -0.763 | -0.818 | -0.84 | -0.866 | -0.898 | -1.105 | -1.829 | -2.482 | -3.138 | Primary | 627
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Consumer Transformation | 9.306 | 9.206 | 9.062 | 8.88 | 8.757 | 8.627 | 8.474 | 7.66 | 5.532 | 3.781 | 2.095 | Primary | 628
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Consumer Transformation | 13.414 | 13.117 | 12.67 | 12.144 | 11.807 | 11.458 | 11.026 | 9.17 | 5.095 | 1.903 | -1.189 | Primary | 629
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Consumer Transformation | 11.59 | 11.353 | 11.021 | 10.627 | 10.34 | 10.042 | 9.69 | 8.051 | 4.816 | 2.381 | 0.147 | Primary | 630
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Consumer Transformation | 8.312 | 7.961 | 7.467 | 6.88 | 6.344 | 5.784 | 5.113 | 2.089 | -2.326 | -5.55 | -8.356 | Primary | 631
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Consumer Transformation | 13.557 | 13.351 | 13.096 | 12.792 | 12.517 | 12.217 | 11.874 | 9.846 | 5.978 | 2.932 | 0.232 | Primary | 632
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Consumer Transformation | 7.706 | 7.686 | 7.585 | 7.41 | 7.291 | 7.141 | 6.934 | 5.524 | 1.253 | -1.888 | -4.522 | Primary | 633
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Consumer Transformation | 14.047 | 13.791 | 13.398 | 12.931 | 12.649 | 12.357 | 11.997 | 10.482 | 7.329 | 4.959 | 2.619 | Primary | 634
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Consumer Transformation | 7.395 | 6.988 | 6.458 | 5.924 | 5.537 | 5.135 | 4.637 | 2.472 | -2.46 | -6.306 | -9.859 | Primary | 635
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Consumer Transformation | 8.096 | 7.948 | 7.738 | 7.469 | 7.277 | 7.064 | 6.816 | 5.399 | 1.641 | -1.405 | -4.297 | Primary | 636
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Falling Short | 13.225 | 13.111 | 13.032 | 12.994 | 12.94 | 12.872 | 12.804 | 12.502 | 12.279 | 12.121 | 11.98 | Primary | 637
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Falling Short | 12.519 | 10.893 | 10.865 | 10.812 | 10.727 | 10.61 | 10.467 | 9.494 | 8.244 | 7.364 | 7.053 | Primary | 638
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Falling Short | 11.479 | 11.189 | 10.854 | 10.468 | 10.022 | 9.522 | 9.029 | 6.704 | 4.714 | 3.293 | 2.177 | Primary | 639
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Falling Short | 5.801 | 4.383 | 4.396 | 4.384 | 4.349 | 4.294 | 4.231 | 3.782 | 3.184 | 2.781 | 2.628 | Primary | 640
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 5.489 | 5.328 | 5.151 | 4.961 | 4.721 | 4.438 | 4.168 | 3.101 | 2.478 | 2.156 | 1.965 | Primary | 641
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Falling Short | 5.319 | 5.319 | 5.313 | 5.302 | 5.281 | 5.252 | 5.222 | 5.092 | 4.996 | 4.934 | 4.89 | Primary | 642
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Falling Short | 10.054 | 9.751 | 9.398 | 8.994 | 8.517 | 7.976 | 7.45 | 5.086 | 3.096 | 1.628 | 0.474 | Primary | 643
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Falling Short | 17.051 | 17.071 | 17.085 | 17.087 | 17.076 | 17.059 | 17.04 | 16.945 | 16.839 | 16.768 | 16.715 | Primary | 644
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Falling Short | 1.355 | 1.19 | 0.988 | 0.747 | 0.458 | 0.127 | -0.2 | -1.68 | -2.866 | -3.693 | -4.313 | Primary | 645
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Falling Short | 2.78 | 2.187 | 2.251 | 2.299 | 2.334 | 2.359 | 2.379 | 2.415 | 2.35 | 2.285 | 2.233 | Primary | 646
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Falling Short | 12.056 | 11.929 | 11.766 | 11.563 | 11.315 | 11.026 | 10.744 | 9.491 | 8.481 | 7.764 | 7.236 | Primary | 647
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Falling Short | 2.623 | 2.487 | 2.332 | 2.146 | 1.893 | 1.581 | 1.261 | -0.357 | -1.919 | -2.927 | -3.389 | Primary | 648
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Falling Short | 3.04 | 3.018 | 2.991 | 2.961 | 2.925 | 2.884 | 2.842 | 2.612 | 2.357 | 2.125 | 1.929 | Primary | 649
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Falling Short | 15.803 | 15.734 | 15.634 | 15.504 | 15.334 | 15.132 | 14.938 | 14.145 | 13.614 | 13.318 | 13.129 | Primary | 650
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Falling Short | 12.837 | 12.34 | 12.292 | 12.236 | 12.17 | 12.098 | 12.025 | 11.647 | 11.256 | 10.879 | 10.504 | Primary | 651
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Falling Short | 10.487 | 10.495 | 10.487 | 10.457 | 10.406 | 10.336 | 10.261 | 9.823 | 9.309 | 8.955 | 8.779 | Primary | 652
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Falling Short | 15.568 | 15.361 | 15.106 | 14.8 | 14.427 | 13.992 | 13.56 | 11.558 | 9.883 | 8.758 | 8.074 | Primary | 653
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Falling Short | 8.386 | 8.396 | 8.397 | 8.386 | 8.362 | 8.325 | 8.282 | 7.997 | 7.639 | 7.39 | 7.291 | Primary | 654
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Falling Short | 6.495 | 6.34 | 6.166 | 5.967 | 5.743 | 5.501 | 5.258 | 4.043 | 2.887 | 1.902 | 0.986 | Primary | 655
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Falling Short | 21.767 | 21.738 | 21.686 | 21.613 | 21.515 | 21.394 | 21.277 | 20.803 | 20.515 | 20.35 | 20.246 | Primary | 656
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Falling Short | 3.695 | 3.557 | 3.41 | 3.254 | 3.086 | 2.907 | 2.728 | 1.825 | 0.931 | 0.099 | -0.687 | Primary | 657
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Falling Short | 11.444 | 11.134 | 10.764 | 10.331 | 9.811 | 9.212 | 8.615 | 5.746 | 3.156 | 1.25 | -0.102 | Primary | 658
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Falling Short | 9.667 | 9.484 | 9.265 | 9.012 | 8.69 | 8.306 | 7.933 | 6.36 | 5.285 | 4.678 | 4.363 | Primary | 659
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Falling Short | 14.907 | 14.748 | 14.566 | 14.364 | 14.117 | 13.827 | 13.548 | 12.399 | 11.695 | 11.311 | 11.045 | Primary | 660
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Falling Short | 2.357 | 2.362 | 2.33 | 2.257 | 2.135 | 1.97 | 1.787 | 0.691 | -0.588 | -1.479 | -1.867 | Primary | 661
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Falling Short | 5.809 | 5.64 | 5.44 | 5.207 | 4.932 | 4.617 | 4.3 | 2.744 | 1.27 | 0.121 | -0.698 | Primary | 662
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 15.112 | 15.097 | 15.075 | 15.044 | 15.002 | 14.952 | 14.897 | 14.595 | 14.274 | 14.057 | 13.944 | Primary | 663
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Falling Short | 4.13 | 1.053 | 1.023 | 0.957 | 0.849 | 0.701 | 0.528 | -0.617 | -2.04 | -3.029 | -3.441 | Primary | 664
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Falling Short | 8.122 | 8.029 | 7.904 | 7.739 | 7.529 | 7.275 | 6.997 | 5.391 | 3.564 | 2.194 | 1.429 | Primary | 665
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Falling Short | 11.795 | 11.637 | 11.43 | 11.175 | 10.857 | 10.483 | 10.12 | 8.606 | 7.613 | 7.039 | 6.662 | Primary | 666
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Falling Short | 6.135 | 5.868 | 5.53 | 5.118 | 4.605 | 3.999 | 3.394 | 0.605 | -1.726 | -3.295 | -4.22 | Primary | 667
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Falling Short | 6.826 | 6.806 | 6.784 | 6.759 | 6.732 | 6.704 | 6.675 | 6.538 | 6.406 | 6.287 | 6.174 | Primary | 668
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Falling Short | 4.296 | 4.259 | 4.216 | 4.167 | 4.109 | 4.043 | 3.977 | 3.631 | 3.283 | 2.997 | 2.777 | Primary | 669
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Falling Short | 13.759 | 13.616 | 13.43 | 13.2 | 12.914 | 12.577 | 12.248 | 10.82 | 9.711 | 8.98 | 8.488 | Primary | 670
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 13.763 | 13.585 | 13.405 | 13.218 | 13.027 | 12.833 | 12.637 | 11.617 | 10.518 | 9.398 | 8.263 | Primary | 671
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Falling Short | 5.543 | 5.494 | 5.436 | 5.369 | 5.288 | 5.196 | 5.107 | 4.725 | 4.431 | 4.225 | 4.071 | Primary | 672
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Falling Short | 10.622 | 10.492 | 10.316 | 10.091 | 9.799 | 9.447 | 9.108 | 7.68 | 6.687 | 6.121 | 5.783 | Primary | 673
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Falling Short | 11.584 | 11.443 | 11.254 | 11.015 | 10.705 | 10.327 | 9.957 | 8.337 | 7.134 | 6.439 | 6.122 | Primary | 674
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Falling Short | 9.178 | 9.199 | 9.205 | 9.194 | 9.165 | 9.12 | 9.067 | 8.715 | 8.274 | 7.958 | 7.79 | Primary | 675
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Falling Short | 10.271 | 10.27 | 10.251 | 10.21 | 10.143 | 10.053 | 9.966 | 9.567 | 9.246 | 9.058 | 8.957 | Primary | 676
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Falling Short | 17.459 | 17.36 | 17.234 | 17.083 | 16.894 | 16.671 | 16.446 | 15.36 | 14.35 | 13.645 | 13.251 | Primary | 677
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Falling Short | 7.939 | 22.533 | 22.401 | 22.241 | 22.036 | 21.794 | 21.56 | 20.581 | 19.927 | 19.56 | 19.335 | Primary | 678
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Falling Short | 10.715 | 10.398 | 10.015 | 9.565 | 9.033 | 8.427 | 7.844 | 5.392 | 3.685 | 2.492 | 1.504 | Primary | 679
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Falling Short | 3.862 | 3.813 | 3.757 | 3.695 | 3.614 | 3.517 | 3.425 | 3.06 | 2.84 | 2.726 | 2.66 | Primary | 680
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Falling Short | 6.527 | 6.174 | 5.774 | 5.334 | 4.799 | 4.172 | 3.553 | 0.795 | -1.167 | -2.34 | -3.038 | Primary | 681
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Falling Short | 4.539 | 4.18 | 3.752 | 3.245 | 2.643 | 1.953 | 1.273 | -1.851 | -4.449 | -6.307 | -7.685 | Primary | 682
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Falling Short | 5.929 | 5.523 | 5.037 | 4.468 | 3.796 | 3.029 | 2.282 | -1.003 | -3.55 | -5.401 | -6.847 | Primary | 683
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Falling Short | 4.23 | 4.254 | 4.274 | 4.287 | 4.295 | 4.295 | 4.292 | 4.212 | 4.057 | 3.927 | 3.856 | Primary | 684
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Falling Short | 7.86 | 7.607 | 7.27 | 6.846 | 6.308 | 5.66 | 4.99 | 1.62 | -1.613 | -3.813 | -4.865 | Primary | 685
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Falling Short | 12.915 | 12.955 | 12.988 | 13.008 | 13.018 | 13.021 | 13.019 | 12.924 | 12.72 | 12.571 | 12.508 | Primary | 686
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Falling Short | 10.149 | 10.211 | 10.267 | 10.317 | 10.361 | 10.4 | 10.436 | 10.557 | 10.602 | 10.616 | 10.616 | Primary | 687
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Falling Short | 10.869 | 10.919 | 10.963 | 10.994 | 11.003 | 10.994 | 10.98 | 10.836 | 10.594 | 10.421 | 10.317 | Primary | 688
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Falling Short | 11.643 | 11.673 | 11.696 | 11.709 | 11.71 | 11.702 | 11.692 | 11.626 | 11.543 | 11.485 | 11.446 | Primary | 689
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Falling Short | 10.93 | 10.811 | 10.643 | 10.426 | 10.138 | 9.78 | 9.41 | 7.573 | 5.796 | 4.625 | 4.14 | Primary | 690
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Falling Short | 4.256 | 4.185 | 4.1 | 4 | 3.879 | 3.739 | 3.604 | 3.031 | 2.606 | 2.284 | 2.021 | Primary | 691
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Falling Short | 5.005 | 4.877 | 4.737 | 4.586 | 4.421 | 4.244 | 4.065 | 3.144 | 2.196 | 1.24 | 0.277 | Primary | 692
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Falling Short | 13.906 | 13.674 | 13.414 | 13.127 | 12.765 | 12.333 | 11.917 | 10.18 | 9.014 | 8.368 | 8.039 | Primary | 693
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Falling Short | -0.08 | -0.113 | -0.15 | -0.195 | -0.246 | -0.304 | -0.365 | -0.692 | -1.051 | -1.387 | -1.684 | Primary | 694
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Falling Short | 3.338 | 3.212 | 3.064 | 2.895 | 2.692 | 2.46 | 2.237 | 1.265 | 0.516 | -0.01 | -0.418 | Primary | 695
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Falling Short | 9.514 | 9.444 | 9.328 | 9.165 | 8.945 | 8.672 | 8.393 | 6.982 | 5.504 | 4.456 | 3.889 | Primary | 696
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Falling Short | 9.186 | 9.13 | 9.07 | 9.003 | 8.906 | 8.782 | 8.662 | 8.138 | 7.738 | 7.501 | 7.358 | Primary | 697
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Falling Short | 5.311 | 5.092 | 4.843 | 4.559 | 4.226 | 3.851 | 3.478 | 1.715 | 0.146 | -1.066 | -2.014 | Primary | 698
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Falling Short | 4.763 | 4.773 | 4.78 | 4.784 | 4.782 | 4.777 | 4.769 | 4.7 | 4.597 | 4.524 | 4.495 | Primary | 699
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Falling Short | 22.005 | 21.923 | 21.826 | 21.711 | 21.561 | 21.381 | 21.208 | 20.507 | 20.059 | 19.817 | 19.665 | Primary | 700
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Falling Short | 7.823 | 7.855 | 7.883 | 7.901 | 7.906 | 7.9 | 7.892 | 7.82 | 7.702 | 7.616 | 7.556 | Primary | 701
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Falling Short | 13.624 | 13.46 | 13.285 | 13.101 | 12.865 | 12.579 | 12.306 | 11.214 | 10.547 | 10.196 | 9.997 | Primary | 702
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Falling Short | 7.186 | 7.174 | 7.134 | 7.058 | 6.941 | 6.789 | 6.637 | 5.927 | 5.338 | 5.003 | 4.849 | Primary | 703
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Falling Short | 4.926 | 4.615 | 4.245 | 3.819 | 3.277 | 2.634 | 2.007 | -0.601 | -2.368 | -3.373 | -3.913 | Primary | 704
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Falling Short | 0.931 | 0.89 | 0.846 | 0.796 | 0.74 | 0.679 | 0.616 | 0.289 | -0.056 | -0.349 | -0.586 | Primary | 705
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Falling Short | 2.994 | 2.823 | 2.632 | 2.417 | 2.171 | 1.899 | 1.611 | 0.02 | -1.75 | -3.269 | -4.436 | Primary | 706
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Falling Short | 12.942 | 12.908 | 12.847 | 12.76 | 12.639 | 12.489 | 12.344 | 11.74 | 11.334 | 11.119 | 11.021 | Primary | 707
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Falling Short | 14.805 | 14.715 | 15.584 | 15.408 | 15.181 | 14.907 | 14.645 | 13.568 | 12.878 | 12.524 | 12.333 | Primary | 708
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Falling Short | 22.201 | 22.19 | 22.139 | 22.031 | 21.861 | 21.627 | 21.334 | 19.243 | 16.426 | 14.472 | 13.857 | Primary | 709
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Falling Short | 9.7 | 9.449 | 9.158 | 8.823 | 8.433 | 7.995 | 7.562 | 5.546 | 3.821 | 2.493 | 1.426 | Primary | 710
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Falling Short | 2.461 | 2.34 | 2.192 | 2.014 | 1.797 | 1.547 | 1.3 | 0.172 | -0.756 | -1.384 | -1.797 | Primary | 711
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Falling Short | 8.028 | 7.863 | 7.626 | 7.318 | 6.926 | 6.461 | 6.016 | 4.201 | 3.091 | 2.494 | 2.098 | Primary | 712
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Falling Short | 6.042 | 3.741 | 3.728 | 3.702 | 3.661 | 3.61 | 3.552 | 3.215 | 2.837 | 2.58 | 2.459 | Primary | 713
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Falling Short | 7.554 | 7.328 | 7.036 | 6.676 | 6.221 | 5.678 | 5.153 | 3.012 | 1.589 | 0.781 | 0.314 | Primary | 714
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Falling Short | 3.954 | 3.796 | 18.289 | 18.035 | 17.71 | 17.321 | 16.938 | 15.248 | 13.979 | 13.234 | 12.859 | Primary | 715
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Falling Short | -0.199 | -0.312 | -0.443 | -0.595 | -0.774 | -0.975 | -1.17 | -2.022 | -2.686 | -3.193 | -3.625 | Primary | 716
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Falling Short | 2.809 | 2.816 | 2.816 | 2.808 | 2.791 | 2.767 | 2.741 | 2.57 | 2.356 | 2.209 | 2.142 | Primary | 717
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Falling Short | 10.394 | 10.23 | 10.009 | 9.732 | 9.382 | 8.966 | 8.567 | 6.947 | 5.942 | 5.408 | 5.086 | Primary | 718
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Falling Short | 8.507 | 8.367 | 8.175 | 7.93 | 7.615 | 7.238 | 6.863 | 5.181 | 3.808 | 2.949 | 2.477 | Primary | 719
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Falling Short | 12.355 | 12.263 | 12.147 | 12.003 | 11.825 | 11.615 | 11.404 | 10.383 | 9.437 | 8.717 | 8.2 | Primary | 720
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Falling Short | 3.648 | 2.67 | 2.675 | 2.651 | 2.594 | 2.505 | 2.399 | 1.707 | 0.85 | 0.25 | 0.011 | Primary | 721
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Falling Short | 15.159 | 15.055 | 14.936 | 14.796 | 14.633 | 14.448 | 14.248 | 13.054 | 11.615 | 10.433 | 9.639 | Primary | 722
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Falling Short | 4.061 | 3.989 | 3.903 | 3.803 | 3.684 | 3.549 | 3.417 | 2.837 | 2.382 | 2.048 | 1.775 | Primary | 723
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Falling Short | 2.459 | 2.426 | 2.382 | 2.324 | 2.249 | 2.159 | 2.073 | 1.72 | 1.493 | 1.368 | 1.289 | Primary | 724
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Falling Short | 14.939 | 14.72 | 14.449 | 14.123 | 13.722 | 13.253 | 12.78 | 10.522 | 8.517 | 7.101 | 6.202 | Primary | 725
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Falling Short | 1.897 | 1.804 | 1.662 | 1.464 | 1.198 | 0.874 | 0.554 | -0.875 | -1.956 | -2.562 | -2.891 | Primary | 726
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Falling Short | 14.751 | 14.739 | 14.709 | 14.66 | 14.589 | 14.501 | 14.41 | 13.952 | 13.504 | 13.2 | 13.022 | Primary | 727
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Falling Short | 4.698 | 4.621 | 4.53 | 4.423 | 4.297 | 4.153 | 4.013 | 3.388 | 2.89 | 2.538 | 2.273 | Primary | 728
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Falling Short | 6.85 | 6.581 | 6.249 | 5.848 | 5.354 | 4.777 | 4.215 | 1.749 | -0.182 | -1.488 | -2.369 | Primary | 729
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Falling Short | 12.547 | 12.35 | 12.107 | 11.82 | 11.471 | 11.07 | 10.681 | 9.032 | 7.827 | 7.008 | 6.378 | Primary | 730
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Falling Short | 12.76 | 11.125 | 11.097 | 11.028 | 10.91 | 10.738 | 10.522 | 8.95 | 6.799 | 5.274 | 4.775 | Primary | 731
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Falling Short | 3.083 | 2.952 | 2.826 | 2.707 | 2.555 | 2.372 | 2.199 | 1.516 | 1.085 | 0.843 | 0.703 | Primary | 732
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Falling Short | 7.986 | 7.586 | 7.111 | 6.568 | 5.923 | 5.185 | 4.466 | 1.288 | -1.288 | -3.152 | -4.582 | Primary | 733
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Falling Short | 8.401 | 8.337 | 8.268 | 8.195 | 8.117 | 8.033 | 7.948 | 7.497 | 7.011 | 6.504 | 5.991 | Primary | 734
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Falling Short | 2.029 | 1.896 | 1.718 | 1.484 | 1.174 | 0.779 | 0.323 | -2.565 | -6.116 | -8.606 | -9.465 | Primary | 735
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Falling Short | 11.909 | 11.726 | 11.529 | 11.318 | 11.051 | 10.734 | 10.421 | 9.043 | 8.01 | 7.386 | 7.035 | Primary | 736
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Falling Short | 9.281 | 9.075 | 8.805 | 8.471 | 8.051 | 7.553 | 7.055 | 4.763 | 2.847 | 1.577 | 0.863 | Primary | 737
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Falling Short | 0.79 | 0.682 | 0.553 | 0.4 | 0.217 | 0.001 | -0.235 | -1.614 | -3.214 | -4.459 | -5.169 | Primary | 738
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Falling Short | 7.387 | 7.169 | 6.894 | 6.56 | 6.15 | 5.673 | 5.213 | 3.293 | 1.96 | 1.091 | 0.429 | Primary | 739
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Falling Short | 0.791 | 0.786 | 0.762 | 0.715 | 0.641 | 0.545 | 0.447 | -0.067 | -0.589 | -0.95 | -1.156 | Primary | 740
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Falling Short | 1.481 | 1.479 | 1.475 | 1.471 | 1.467 | 1.463 | 1.458 | 1.435 | 1.411 | 1.385 | 1.359 | Primary | 741
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 10.321 | 10.341 | 10.345 | 10.327 | 10.291 | 10.24 | 10.188 | 9.932 | 9.684 | 9.514 | 9.38 | Primary | 742
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Falling Short | 7.077 | 7.064 | 7.041 | 7.008 | 6.961 | 6.904 | 6.848 | 6.597 | 6.396 | 6.276 | 6.199 | Primary | 743
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 8.488 | 8.421 | 8.339 | 8.241 | 8.124 | 7.987 | 7.856 | 7.309 | 6.922 | 6.651 | 6.436 | Primary | 744
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Falling Short | 3.864 | 3.729 | 3.571 | 3.389 | 3.167 | 2.908 | 2.644 | 1.343 | 0.146 | -0.72 | -1.261 | Primary | 745
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Falling Short | 14.502 | 14.258 | 13.968 | 14.631 | 14.235 | 13.787 | 13.353 | 11.431 | 9.921 | 8.894 | 8.088 | Primary | 746
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Falling Short | 10.041 | 9.1 | 8.934 | 8.721 | 8.449 | 8.129 | 7.819 | 6.519 | 5.627 | 5.086 | 4.724 | Primary | 747
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Falling Short | 3.231 | 3.072 | 2.887 | 2.673 | 2.416 | 2.119 | 1.81 | 0.181 | -1.489 | -2.742 | -3.496 | Primary | 748
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Falling Short | 11.144 | 10.826 | 10.551 | 10.327 | 10.043 | 9.705 | 9.378 | 8.046 | 7.2 | 6.735 | 6.458 | Primary | 749
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Falling Short | 10.578 | 10.452 | 10.32 | 10.178 | 10.028 | 9.872 | 9.714 | 8.883 | 8.006 | 7.132 | 6.249 | Primary | 750
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Falling Short | -3.015 | -3.484 | -4.041 | -4.692 | -5.469 | -6.36 | -7.225 | -10.994 | -13.842 | -15.807 | -17.268 | Primary | 751
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Falling Short | 7.22 | 6.929 | 6.594 | 6.226 | 5.763 | 5.216 | 4.693 | 2.588 | 1.122 | 0.209 | -0.404 | Primary | 752
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Falling Short | 5.088 | 5.128 | 5.146 | 5.139 | 5.107 | 5.055 | 4.996 | 4.658 | 4.318 | 4.087 | 3.93 | Primary | 753
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Falling Short | 17.183 | 14.152 | 14.001 | 13.831 | 13.641 | 13.435 | 13.232 | 12.273 | 11.396 | 10.643 | 9.948 | Primary | 754
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Falling Short | 13.726 | 13.637 | 13.539 | 13.423 | 13.292 | 13.144 | 12.985 | 12.044 | 10.938 | 9.994 | 9.295 | Primary | 755
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Falling Short | 9.387 | 9.107 | 8.803 | 8.464 | 8.086 | 7.665 | 7.208 | 4.521 | 1.344 | -1.34 | -3.198 | Primary | 756
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Falling Short | 12.62 | 12.628 | 12.619 | 12.59 | 12.541 | 12.478 | 12.416 | 12.121 | 11.868 | 11.715 | 11.603 | Primary | 757
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Falling Short | 11.431 | 11.462 | 11.48 | 11.483 | 11.471 | 11.447 | 11.42 | 11.285 | 11.144 | 11.044 | 10.981 | Primary | 758
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Falling Short | 3.923 | 3.65 | 3.36 | 3.042 | 2.695 | 2.314 | 1.898 | -0.575 | -3.539 | -6.104 | -7.95 | Primary | 759
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Falling Short | 16.245 | 16.183 | 16.11 | 16.024 | 15.924 | 15.811 | 15.691 | 15.018 | 14.274 | 13.651 | 13.183 | Primary | 760
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Falling Short | 10.743 | 10.646 | 10.503 | 10.313 | 10.064 | 9.765 | 9.474 | 8.25 | 7.363 | 6.841 | 6.546 | Primary | 761
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Falling Short | 10.228 | 10.202 | 10.151 | 10.072 | 9.959 | 9.819 | 9.672 | 8.92 | 8.185 | 7.692 | 7.43 | Primary | 762
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Falling Short | 7.104 | 6.935 | 6.7 | 6.398 | 6.006 | 5.529 | 5.056 | 2.916 | 1.2 | 0.167 | -0.297 | Primary | 763
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Falling Short | 4.494 | 4.255 | 3.972 | 3.639 | 3.232 | 2.753 | 2.27 | -0.097 | -2.325 | -3.963 | -4.984 | Primary | 764
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Falling Short | 11.686 | 11.679 | 11.655 | 11.611 | 11.533 | 11.422 | 11.287 | 10.387 | 9.236 | 8.436 | 8.191 | Primary | 765
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Falling Short | 15.381 | 15.254 | 15.076 | 14.849 | 14.563 | 14.226 | 13.903 | 12.606 | 11.822 | 11.403 | 11.133 | Primary | 766
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Falling Short | 9.252 | 8.981 | 8.636 | 8.21 | 7.679 | 7.041 | 6.387 | 3.101 | -0.042 | -2.197 | -3.263 | Primary | 767
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Falling Short | 3.266 | 3.176 | 3.07 | 3.449 | 3.307 | 3.148 | 2.991 | 2.29 | 1.717 | 1.28 | 0.928 | Primary | 768
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Falling Short | 8.035 | 7.899 | 7.715 | 7.479 | 7.173 | 6.805 | 6.451 | 5.032 | 4.168 | 3.716 | 3.446 | Primary | 769
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Falling Short | 4.08 | 3.981 | 3.854 | 3.701 | 3.512 | 3.289 | 3.076 | 2.203 | 1.656 | 1.341 | 1.119 | Primary | 770
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 12.147 | 12.093 | 12.028 | 11.952 | 11.863 | 11.764 | 11.661 | 11.112 | 10.51 | 9.954 | 9.447 | Primary | 771
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Falling Short | 25.269 | 25.236 | 25.195 | 25.144 | 25.083 | 25.014 | 24.945 | 24.591 | 24.223 | 23.922 | 23.675 | Primary | 772
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Falling Short | 14.529 | 14.375 | 14.194 | 13.985 | 13.74 | 13.462 | 13.182 | 11.839 | 10.692 | 9.88 | 9.313 | Primary | 773
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Falling Short | 12.588 | 12.617 | 12.637 | 12.643 | 12.637 | 12.623 | 12.608 | 12.509 | 12.38 | 12.295 | 12.234 | Primary | 774
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Falling Short | 19.753 | 19.713 | 19.669 | 19.62 | 19.566 | 19.509 | 19.453 | 19.154 | 18.83 | 18.516 | 18.204 | Primary | 775
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Falling Short | 6.681 | 6.557 | 6.385 | 6.165 | 5.889 | 5.564 | 5.249 | 3.917 | 2.926 | 2.302 | 1.862 | Primary | 776
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Falling Short | 22.332 | 22.336 | 22.317 | 22.27 | 22.192 | 22.087 | 21.98 | 21.435 | 20.901 | 20.53 | 20.295 | Primary | 777
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Falling Short | 14.519 | 14.503 | 14.477 | 14.439 | 14.386 | 14.323 | 14.259 | 13.957 | 13.705 | 13.547 | 13.419 | Primary | 778
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Falling Short | 4.74 | 4.704 | 4.655 | 4.593 | 4.511 | 4.412 | 4.317 | 3.907 | 3.62 | 3.458 | 3.378 | Primary | 779
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Falling Short | 4.47 | 4.429 | 4.386 | 4.339 | 4.29 | 4.235 | 4.178 | 3.866 | 3.517 | 3.189 | 2.908 | Primary | 780
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Falling Short | 15.52 | 15.43 | 15.323 | 15.191 | 15.034 | 14.855 | 14.665 | 13.599 | 12.391 | 11.395 | 10.673 | Primary | 781
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 9.677 | 9.601 | 9.497 | 9.367 | 9.199 | 8.999 | 8.806 | 8.012 | 7.498 | 7.219 | 7.068 | Primary | 782
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Falling Short | 11.531 | 11.485 | 11.422 | 11.342 | 11.242 | 11.121 | 11.006 | 10.536 | 10.247 | 10.096 | 10.001 | Primary | 783
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Falling Short | 2.299 | 2.16 | 2.003 | 1.827 | 1.624 | 1.397 | 1.174 | 0.179 | -0.608 | -1.217 | -1.737 | Primary | 784
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Falling Short | 3.341 | 3.208 | 3.054 | 2.87 | 2.654 | 2.41 | 2.153 | 0.73 | -0.838 | -2.1 | -2.997 | Primary | 785
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Falling Short | 18.887 | 18.866 | 18.838 | 18.804 | 18.759 | 18.705 | 18.643 | 18.256 | 17.778 | 17.407 | 17.207 | Primary | 786
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Falling Short | 4.859 | 4.817 | 4.762 | 4.695 | 4.61 | 4.508 | 4.41 | 4.015 | 3.769 | 3.637 | 3.558 | Primary | 787
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Falling Short | 14.775 | 14.765 | 14.755 | 14.739 | 14.713 | 14.677 | 14.636 | 14.397 | 14.13 | 13.948 | 13.864 | Primary | 788
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Falling Short | 12.524 | 12.571 | 12.613 | 12.643 | 12.666 | 12.679 | 12.687 | 12.641 | 12.493 | 12.375 | 12.33 | Primary | 789
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Falling Short | 2.211 | 2.016 | 1.776 | 1.487 | 1.136 | 0.726 | 0.324 | -1.483 | -2.938 | -3.921 | -4.542 | Primary | 790
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 5.857 | 5.831 | 5.797 | 5.753 | 5.699 | 5.636 | 5.57 | 5.221 | 4.855 | 4.563 | 4.348 | Primary | 791
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Falling Short | 5.206 | 5.167 | 5.118 | 5.056 | 4.978 | 4.884 | 4.78 | 4.174 | 3.47 | 2.919 | 2.593 | Primary | 792
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Falling Short | 5.222 | 5.003 | 4.74 | 4.433 | 4.063 | 3.634 | 3.212 | 1.278 | -0.339 | -1.487 | -2.265 | Primary | 793
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Falling Short | 15.271 | 15.204 | 15.124 | 15.032 | 14.924 | 14.804 | 14.682 | 14.05 | 13.415 | 12.896 | 12.478 | Primary | 794
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Falling Short | 8.402 | 8.09 | 7.736 | 7.342 | 6.848 | 6.264 | 5.703 | 3.448 | 2.084 | 1.362 | 0.935 | Primary | 795
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Falling Short | 4.817 | 4.779 | 4.726 | 4.649 | 4.537 | 4.394 | 4.24 | 3.382 | 2.466 | 1.846 | 1.545 | Primary | 796
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Falling Short | 10.333 | 10.152 | 9.912 | 9.612 | 9.241 | 8.806 | 8.388 | 6.644 | 5.481 | 4.771 | 4.253 | Primary | 797
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Falling Short | 0.178 | 0.1 | 0.015 | -0.084 | -0.194 | -0.316 | -0.442 | -1.12 | -1.873 | -2.522 | -3.052 | Primary | 798
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Falling Short | 13.453 | 13.308 | 13.117 | 12.881 | 12.575 | 12.208 | 11.85 | 10.33 | 9.252 | 8.633 | 8.323 | Primary | 799
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Falling Short | 18.394 | 18.389 | 18.378 | 18.358 | 18.33 | 18.294 | 18.256 | 18.046 | 17.82 | 17.665 | 17.58 | Primary | 800
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Falling Short | 12.463 | 12.324 | 12.164 | 11.984 | 11.782 | 11.559 | 11.335 | 10.227 | 9.147 | 8.235 | 7.43 | Primary | 801
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Falling Short | 7.095 | 6.966 | 6.817 | 6.646 | 6.448 | 6.224 | 5.995 | 4.845 | 3.77 | 2.95 | 2.335 | Primary | 802
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Falling Short | 8.093 | 7.954 | 7.786 | 7.585 | 7.341 | 7.054 | 6.74 | 4.895 | 2.778 | 1.123 | 0.124 | Primary | 803
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Falling Short | 16.234 | 16.165 | 16.092 | 16.018 | 15.941 | 15.862 | 15.782 | 15.35 | 14.878 | 14.378 | 13.868 | Primary | 804
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Falling Short | 16.942 | 16.891 | 16.817 | 16.717 | 16.585 | 16.426 | 16.272 | 15.611 | 15.13 | 14.856 | 14.709 | Primary | 805
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Falling Short | 18.981 | 18.949 | 18.911 | 18.865 | 18.809 | 18.745 | 18.683 | 18.414 | 18.206 | 18.053 | 17.922 | Primary | 806
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Falling Short | 9.328 | 9.11 | 8.894 | 8.686 | 8.415 | 8.09 | 7.778 | 6.498 | 5.642 | 5.159 | 4.865 | Primary | 807
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Falling Short | 10.561 | 10.369 | 10.136 | 9.866 | 9.517 | 9.097 | 8.696 | 7.058 | 6.003 | 5.438 | 5.125 | Primary | 808
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Falling Short | -6.631 | -6.575 | -6.53 | -6.499 | -6.484 | -6.483 | -6.491 | -6.623 | -6.869 | -7.055 | -7.123 | Primary | 809
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Falling Short | 10.474 | 10.15 | 9.827 | 9.511 | 9.115 | 8.646 | 8.198 | 6.396 | 5.282 | 4.683 | 4.314 | Primary | 810
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Falling Short | 11.314 | 11.225 | 11.116 | 10.976 | 10.806 | 10.605 | 10.389 | 9.132 | 7.69 | 6.585 | 5.914 | Primary | 811
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Falling Short | 5.208 | 5.009 | 4.771 | 4.491 | 4.157 | 3.779 | 3.416 | 1.872 | 0.756 | -0.001 | -0.604 | Primary | 812
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Falling Short | 24.376 | 24.382 | 24.371 | 24.335 | 24.277 | 24.203 | 24.126 | 23.742 | 23.372 | 23.138 | 22.98 | Primary | 813
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Falling Short | 6.253 | 6.039 | 5.8 | 5.532 | 5.228 | 4.893 | 4.552 | 2.825 | 1.066 | -0.474 | -1.785 | Primary | 814
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Falling Short | 6.767 | 6.764 | 6.758 | 6.751 | 6.74 | 6.728 | 6.716 | 6.662 | 6.625 | 6.605 | 6.594 | Primary | 815
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Falling Short | 11.522 | 11.24 | 10.874 | 10.425 | 9.876 | 9.236 | 8.613 | 5.903 | 3.886 | 2.556 | 1.615 | Primary | 816
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Falling Short | 21.932 | 21.938 | 21.929 | 21.896 | 21.834 | 21.737 | 21.603 | 20.529 | 18.97 | 17.861 | 17.548 | Primary | 817
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Falling Short | 11.276 | 11.174 | 11.033 | 10.854 | 10.62 | 10.337 | 10.06 | 8.865 | 7.971 | 7.438 | 7.139 | Primary | 818
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Falling Short | 12.048 | 11.918 | 11.752 | 11.538 | 11.264 | 10.921 | 10.52 | 7.9 | 4.606 | 2.21 | 1.206 | Primary | 819
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Falling Short | 0.692 | 0.603 | 0.497 | 0.373 | 0.225 | 0.054 | -0.121 | -1.014 | -1.911 | -2.621 | -3.122 | Primary | 820
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Falling Short | 6.989 | 1.304 | 1.083 | 0.824 | 0.517 | 0.166 | -0.178 | -1.722 | -2.907 | -3.715 | -4.322 | Primary | 821
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Falling Short | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 822
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Falling Short | 4.935 | 4.742 | 4.516 | 4.257 | 3.952 | 3.61 | 3.275 | 1.753 | 0.49 | -0.495 | -1.325 | Primary | 823
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Falling Short | 12.96 | 12.858 | 12.721 | 12.533 | 12.273 | 11.934 | 11.538 | 9 | 5.854 | 3.687 | 2.991 | Primary | 824
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Falling Short | 2.248 | 2.143 | 2.007 | 1.838 | 1.614 | 1.341 | 1.066 | -0.207 | -1.284 | -1.984 | -2.366 | Primary | 825
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Falling Short | 2.284 | 2.202 | 2.115 | 2.027 | 1.912 | 1.774 | 1.641 | 1.113 | 0.779 | 0.598 | 0.491 | Primary | 826
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Falling Short | 12.955 | 12.904 | 12.824 | 12.715 | 12.568 | 12.388 | 12.212 | 11.445 | 10.885 | 10.562 | 10.381 | Primary | 827
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Falling Short | 7.794 | 7.819 | 7.839 | 7.847 | 7.842 | 7.826 | 7.81 | 7.701 | 7.548 | 7.444 | 7.37 | Primary | 828
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Falling Short | 13.501 | 13.488 | 13.458 | 13.409 | 13.339 | 13.255 | 13.168 | 12.701 | 12.207 | 11.853 | 11.617 | Primary | 829
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Falling Short | 7 | 6.661 | 6.268 | 5.819 | 5.295 | 4.703 | 4.123 | 1.49 | -0.7 | -2.4 | -3.779 | Primary | 830
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Falling Short | 12.715 | 12.708 | 12.68 | 12.623 | 12.532 | 12.402 | 12.238 | 11.059 | 9.473 | 8.355 | 7.997 | Primary | 831
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Falling Short | 13.713 | 13.732 | 13.748 | 13.759 | 13.767 | 13.772 | 13.776 | 13.772 | 13.738 | 13.701 | 13.664 | Primary | 832
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Falling Short | 5.897 | 5.893 | 5.883 | 5.87 | 5.85 | 5.824 | 5.8 | 5.692 | 5.617 | 5.575 | 5.553 | Primary | 833
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Falling Short | 14.108 | 14.126 | 14.135 | 14.131 | 14.115 | 14.092 | 14.069 | 13.937 | 13.78 | 13.677 | 13.603 | Primary | 834
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Falling Short | -4.056 | -4.181 | -4.355 | -4.579 | -4.861 | -5.196 | -5.523 | -6.905 | -7.911 | -8.525 | -8.897 | Primary | 835
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Falling Short | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 836
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Falling Short | 8.994 | 8.068 | 7.738 | 7.346 | 6.868 | 6.314 | 5.779 | 3.54 | 2.016 | 1.061 | 0.353 | Primary | 837
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Falling Short | 8.933 | 8.687 | 8.381 | 8.019 | 13.56 | 13.014 | 12.49 | 10.365 | 8.982 | 8.21 | 7.747 | Primary | 838
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Falling Short | 3.912 | 3.942 | 3.956 | 3.951 | 3.927 | 3.889 | 3.847 | 3.584 | 3.284 | 3.086 | 2.976 | Primary | 839
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Falling Short | 2.287 | 2.018 | 1.686 | 1.292 | 0.819 | 0.277 | -0.244 | -2.409 | -3.864 | -4.788 | -5.496 | Primary | 840
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Falling Short | 14.401 | 14.299 | 14.169 | 14.008 | 13.802 | 13.555 | 13.318 | 12.345 | 11.711 | 11.362 | 11.156 | Primary | 841
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Falling Short | 5.388 | 5.138 | 4.803 | 4.384 | 3.861 | 3.246 | 2.641 | -0.086 | -2.321 | -3.857 | -4.882 | Primary | 842
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Falling Short | 5.202 | 4.325 | 4.169 | 3.984 | 3.738 | 3.435 | 3.129 | 1.71 | 0.554 | -0.17 | -0.533 | Primary | 843
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Falling Short | 15.077 | 15.009 | 14.919 | 14.808 | 14.665 | 14.495 | 14.33 | 13.663 | 13.248 | 13.018 | 12.87 | Primary | 844
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Falling Short | 4.138 | 4.024 | 3.865 | 3.66 | 3.389 | 3.06 | 2.735 | 1.268 | 0.066 | -0.669 | -1.023 | Primary | 845
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Falling Short | 7.739 | 7.545 | 7.321 | 7.059 | 6.754 | 6.41 | 6.051 | 4.126 | 2.009 | 0.29 | -0.951 | Primary | 846
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Falling Short | 8.919 | 8.744 | 8.507 | 8.212 | 7.832 | 7.379 | 6.941 | 5.045 | 3.42 | 2.329 | 1.637 | Primary | 847
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Falling Short | 6.756 | 6.496 | 6.184 | 5.82 | 5.39 | 4.897 | 4.421 | 2.385 | 0.997 | 0.141 | -0.493 | Primary | 848
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Falling Short | 2.667 | 2.276 | 1.864 | 1.437 | 0.899 | 0.261 | -0.35 | -2.807 | -4.276 | -5.046 | -5.506 | Primary | 849
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Falling Short | 9.815 | 9.602 | 9.361 | 9.092 | 8.746 | 8.333 | 7.939 | 6.346 | 5.34 | 4.791 | 4.45 | Primary | 850
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Falling Short | 10.746 | 10.504 | 10.226 | 9.914 | 9.51 | 9.019 | 8.525 | 6.224 | 4.288 | 3.099 | 2.604 | Primary | 851
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Falling Short | 13.325 | 13.331 | 13.321 | 13.283 | 13.217 | 13.123 | 13.006 | 12.165 | 11.019 | 10.219 | 9.949 | Primary | 852
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Falling Short | 8.817 | 8.759 | 8.682 | 8.582 | 8.45 | 8.291 | 8.137 | 7.483 | 7.016 | 6.749 | 6.591 | Primary | 853
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Falling Short | 3.494 | 3.482 | 3.45 | 3.393 | 3.307 | 3.193 | 3.061 | 2.219 | 1.163 | 0.415 | 0.12 | Primary | 854
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Falling Short | 12.918 | 12.816 | 12.677 | 12.5 | 12.271 | 11.998 | 11.735 | 10.676 | 10.01 | 9.649 | 9.428 | Primary | 855
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Falling Short | 17.6 | 17.539 | 17.449 | 17.329 | 17.171 | 16.981 | 16.798 | 16.053 | 15.599 | 15.369 | 15.253 | Primary | 856
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Falling Short | 15.294 | 15.222 | 15.132 | 15.024 | 14.899 | 14.76 | 14.62 | 13.913 | 13.138 | 12.479 | 11.889 | Primary | 857
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Falling Short | 4.058 | 3.918 | 3.747 | 3.531 | 3.262 | 2.935 | 2.558 | 0.147 | -2.837 | -5.045 | -6.079 | Primary | 858
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Falling Short | 10.027 | 10.052 | 10.065 | 10.059 | 10.037 | 10.001 | 9.958 | 9.651 | 9.234 | 8.937 | 8.788 | Primary | 859
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Falling Short | -1.284 | -1.367 | -1.461 | -1.573 | -1.704 | -1.854 | -2.015 | -2.932 | -3.976 | -4.825 | -5.399 | Primary | 860
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Falling Short | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary | 861
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Falling Short | 6.861 | 6.644 | 6.389 | 6.094 | 5.715 | 5.262 | 4.813 | 2.802 | 1.211 | 0.234 | -0.273 | Primary | 862
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Falling Short | 14.401 | 14.272 | 14.094 | 13.867 | 13.585 | 13.251 | 12.924 | 11.537 | 10.619 | 10.108 | 9.809 | Primary | 863
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Falling Short | 3.448 | 3.355 | 3.245 | 3.116 | 2.965 | 2.794 | 2.628 | 1.904 | 1.336 | 0.919 | 0.577 | Primary | 864
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Falling Short | 8.687 | 8.452 | 8.164 | 7.8 | 7.342 | 6.784 | 6.133 | 1.884 | -3.523 | -7.543 | -9.37 | Primary | 865
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Falling Short | 13.284 | 13.054 | 12.809 | 12.549 | 12.221 | 11.834 | 11.462 | 9.926 | 8.929 | 8.4 | 8.107 | Primary | 866
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Falling Short | 5.059 | 4.989 | 4.907 | 4.813 | 4.704 | 4.581 | 4.461 | 3.955 | 3.591 | 3.33 | 3.11 | Primary | 867
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Falling Short | 6.717 | 6.458 | 6.142 | 5.766 | 5.312 | 4.788 | 4.283 | 2.116 | 0.445 | -0.73 | -1.651 | Primary | 868
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Falling Short | 10.189 | 10.053 | 9.87 | 9.635 | 9.333 | 8.974 | 8.627 | 7.218 | 6.316 | 5.822 | 5.537 | Primary | 869
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Falling Short | 14.969 | 14.789 | 14.584 | 14.359 | 14.078 | 13.747 | 13.432 | 12.205 | 11.516 | 11.159 | 10.931 | Primary | 870
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Falling Short | 6.359 | 6.293 | 6.181 | 6.023 | 5.808 | 5.546 | 5.286 | 4.129 | 3.196 | 2.627 | 2.316 | Primary | 871
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Falling Short | 13.939 | 13.602 | 13.214 | 12.769 | 12.248 | 11.656 | 11.065 | 8.293 | 5.904 | 4.165 | 2.918 | Primary | 872
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Falling Short | 13.057 | 13.024 | 12.982 | 12.926 | 12.859 | 12.782 | 12.705 | 12.309 | 11.893 | 11.55 | 11.258 | Primary | 873
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Falling Short | 9.17 | 8.998 | 8.783 | 8.52 | 8.192 | 7.805 | 7.412 | 5.553 | 3.892 | 2.748 | 2.09 | Primary | 874
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Falling Short | 12.348 | 12.357 | 12.346 | 12.312 | 12.251 | 12.163 | 12.055 | 11.318 | 10.356 | 9.682 | 9.445 | Primary | 875
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Falling Short | 6.813 | 6.808 | 6.774 | 6.703 | 6.593 | 6.442 | 6.266 | 5.128 | 3.662 | 2.611 | 2.17 | Primary | 876
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Falling Short | 25.531 | 25.419 | 25.284 | 25.118 | 24.916 | 24.68 | 24.427 | 23.008 | 21.41 | 20.136 | 19.324 | Primary | 877
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Falling Short | 4.301 | 4.011 | 3.707 | 3.388 | 3.048 | 2.692 | 2.327 | 0.429 | -1.524 | -3.354 | -5.05 | Primary | 878
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Falling Short | 1.801 | 1.744 | 1.677 | 1.602 | 1.516 | 1.419 | 1.324 | 0.882 | 0.49 | 0.132 | -0.206 | Primary | 879
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Falling Short | 12.444 | 12.257 | 12.04 | 11.79 | 11.489 | 11.147 | 10.811 | 9.291 | 8.062 | 7.193 | 6.521 | Primary | 880
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Falling Short | 10.122 | 10.132 | 10.131 | 10.115 | 10.084 | 10.04 | 9.991 | 9.687 | 9.329 | 9.088 | 8.973 | Primary | 881
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Falling Short | 10.208 | 10.16 | 10.083 | 9.97 | 9.821 | 9.645 | 9.468 | 8.627 | 7.937 | 7.516 | 7.229 | Primary | 882
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Falling Short | 0.638 | 0.567 | 0.486 | 0.39 | 0.279 | 0.152 | 0.018 | -0.753 | -1.639 | -2.369 | -2.878 | Primary | 883
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Falling Short | 9.336 | 9.33 | 9.29 | 9.2 | 9.05 | 8.833 | 8.551 | 6.397 | 3.365 | 1.226 | 0.589 | Primary | 884
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Falling Short | 16.424 | 16.405 | 16.381 | 16.347 | 16.299 | 16.233 | 16.165 | 15.811 | 15.459 | 15.228 | 15.12 | Primary | 885
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Falling Short | 8.926 | 7.882 | 7.562 | 7.186 | 6.742 | 6.237 | 5.744 | 3.544 | 1.797 | 0.553 | -0.414 | Primary | 886
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Falling Short | 12.213 | 12.153 | 12.066 | 11.95 | 11.797 | 11.609 | 11.427 | 10.701 | 10.26 | 10.018 | 9.862 | Primary | 887
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Falling Short | 17.975 | 17.987 | 17.956 | 17.866 | 17.702 | 17.456 | 17.131 | 14.665 | 11.215 | 8.774 | 8.064 | Primary | 888
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Falling Short | 10.185 | 10.052 | 9.861 | 9.615 | 9.29 | 8.893 | 8.506 | 6.808 | 5.513 | 4.744 | 4.356 | Primary | 889
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Falling Short | 4.267 | 4.22 | 4.164 | 4.099 | 4.021 | 3.932 | 3.845 | 3.45 | 3.125 | 2.868 | 2.654 | Primary | 890
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Falling Short | 9.555 | 9.418 | 9.259 | 9.078 | 8.847 | 8.57 | 8.301 | 7.149 | 6.322 | 5.839 | 5.551 | Primary | 891
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 14.989 | 14.799 | 14.579 | 14.322 | 14.025 | 13.696 | 13.358 | 11.591 | 9.76 | 8.185 | 6.856 | Primary | 892
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Falling Short | 13.358 | 13.164 | 12.939 | 12.674 | 12.368 | 12.032 | 11.682 | 9.797 | 7.75 | 5.974 | 4.489 | Primary | 893
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Falling Short | 13.311 | 13.321 | 13.32 | 13.303 | 13.268 | 13.219 | 13.164 | 12.815 | 12.368 | 12.058 | 11.917 | Primary | 894
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Falling Short | 8.059 | 8.082 | 8.094 | 8.091 | 8.076 | 8.051 | 8.023 | 7.878 | 7.741 | 7.641 | 7.552 | Primary | 895
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Falling Short | 17.534 | 17.481 | 17.403 | 17.301 | 17.172 | 17.016 | 16.865 | 16.204 | 15.681 | 15.352 | 15.167 | Primary | 896
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Falling Short | 5.55 | 5.418 | 5.278 | 5.125 | 4.96 | 4.783 | 4.593 | 3.505 | 2.231 | 0.994 | -0.111 | Primary | 897
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Falling Short | 2.337 | 2.117 | 1.872 | 1.603 | 1.262 | 0.858 | 0.469 | -1.117 | -2.136 | -2.695 | -3.035 | Primary | 898
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Falling Short | 12.846 | 12.672 | 12.471 | 12.247 | 11.964 | 11.63 | 11.308 | 10.011 | 9.103 | 8.551 | 8.187 | Primary | 899
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Falling Short | 10.054 | 9.825 | 9.549 | 9.225 | 8.809 | 8.305 | 7.799 | 5.384 | 3.277 | 1.937 | 1.313 | Primary | 900
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Falling Short | 11.546 | 11.549 | 11.533 | 11.492 | 11.42 | 11.316 | 11.188 | 10.275 | 9.055 | 8.202 | 7.923 | Primary | 901
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Falling Short | 16.055 | 15.964 | 15.838 | 15.677 | 15.47 | 15.222 | 14.985 | 14.034 | 13.455 | 13.152 | 12.977 | Primary | 902
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Falling Short | 12.885 | 12.829 | 12.742 | 12.62 | 12.455 | 12.253 | 12.057 | 11.232 | 10.655 | 10.343 | 10.19 | Primary | 903
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Falling Short | 9.389 | 9.289 | 9.142 | 8.945 | 8.676 | 8.345 | 8.008 | 6.394 | 4.947 | 4.029 | 3.639 | Primary | 904
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Falling Short | 11.496 | 9.809 | 9.732 | 9.623 | 9.476 | 9.296 | 9.123 | 8.422 | 7.989 | 7.76 | 7.616 | Primary | 905
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Falling Short | 5.211 | 5.156 | 5.091 | 5.014 | 4.919 | 4.807 | 4.701 | 4.245 | 3.914 | 3.7 | 3.555 | Primary | 906
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Falling Short | 14.307 | 14.097 | 13.83 | 13.505 | 13.099 | 12.619 | 12.157 | 10.245 | 9.002 | 8.321 | 7.932 | Primary | 907
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Falling Short | 3.111 | 2.932 | 2.682 | 2.361 | 1.943 | 1.443 | 0.96 | -1.02 | -2.306 | -3.02 | -3.442 | Primary | 908
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Falling Short | 14.847 | 14.728 | 14.572 | 14.38 | 14.131 | 13.829 | 13.537 | 12.308 | 11.443 | 10.941 | 10.676 | Primary | 909
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Falling Short | 7.072 | 6.876 | 6.623 | 6.312 | 5.912 | 5.437 | 4.98 | 3.09 | 1.82 | 1.095 | 0.638 | Primary | 910
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Falling Short | 19.203 | 19.227 | 19.223 | 19.183 | 19.105 | 18.998 | 18.883 | 18.229 | 17.536 | 17.085 | 16.872 | Primary | 911
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Falling Short | 12.521 | 12.418 | 12.294 | 12.145 | 11.96 | 11.742 | 11.525 | 10.548 | 9.778 | 9.301 | 9.035 | Primary | 912
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Falling Short | 4.489 | 4.272 | 4.009 | 3.695 | 3.316 | 2.878 | 2.443 | 0.431 | -1.314 | -2.615 | -3.562 | Primary | 913
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Falling Short | 8.788 | 8.138 | 7.386 | 6.529 | 5.527 | 4.391 | 3.28 | -1.66 | -5.373 | -7.892 | -9.773 | Primary | 914
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Falling Short | 4.672 | 4.47 | 4.235 | 3.966 | 3.627 | 3.228 | 2.839 | 1.2 | 0.117 | -0.496 | -0.876 | Primary | 915
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Falling Short | 12.968 | 12.703 | 12.383 | 12.01 | 11.564 | 11.054 | 10.563 | 8.502 | 7.067 | 6.116 | 5.371 | Primary | 916
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Falling Short | 20.836 | 17.726 | 17.742 | 17.753 | 17.762 | 17.77 | 17.777 | 17.794 | 17.784 | 17.774 | 17.764 | Primary | 917
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Falling Short | 3.212 | 2.998 | 2.751 | 2.457 | 2.108 | 1.702 | 1.242 | -1.621 | -5.175 | -7.984 | -9.608 | Primary | 918
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Falling Short | 13.802 | 13.78 | 13.744 | 13.693 | 13.622 | 13.535 | 13.448 | 13.029 | 12.657 | 12.407 | 12.215 | Primary | 919
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Falling Short | 14.201 | 14.236 | 14.264 | 14.287 | 14.301 | 14.311 | 14.318 | 14.324 | 14.297 | 14.269 | 14.242 | Primary | 920
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Falling Short | 15.614 | 15.638 | 15.654 | 15.661 | 15.659 | 15.65 | 15.641 | 15.579 | 15.488 | 15.424 | 15.382 | Primary | 921
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Falling Short | 9.612 | 9.325 | 8.956 | 8.509 | 7.96 | 7.316 | 6.693 | 4.05 | 2.142 | 0.913 | 0.076 | Primary | 922
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Falling Short | 14.644 | 14.552 | 14.449 | 14.33 | 14.194 | 14.046 | 13.892 | 13.069 | 12.193 | 11.441 | 10.814 | Primary | 923
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Falling Short | 5.93 | 5.908 | 5.863 | 5.791 | 5.69 | 5.569 | 5.446 | 4.842 | 4.274 | 3.905 | 3.654 | Primary | 924
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Falling Short | 14 | 13.915 | 13.798 | 13.645 | 13.444 | 13.201 | 12.964 | 11.931 | 11.125 | 10.635 | 10.369 | Primary | 925
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Falling Short | 17.518 | 13.968 | 13.948 | 13.918 | 13.874 | 13.816 | 13.759 | 13.522 | 13.359 | 13.266 | 13.228 | Primary | 926
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Falling Short | 10.894 | 10.754 | 10.586 | 10.39 | 10.153 | 9.878 | 9.606 | 8.368 | 7.347 | 6.632 | 6.134 | Primary | 927
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Falling Short | 2.679 | 2.569 | 2.428 | 2.254 | 2.038 | 1.78 | 1.507 | 0.05 | -1.416 | -2.42 | -2.893 | Primary | 928
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Falling Short | 11.071 | 10.933 | 10.752 | 10.534 | 10.254 | 9.919 | 9.597 | 8.292 | 7.365 | 6.782 | 6.393 | Primary | 929
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Falling Short | 12.598 | 12.516 | 12.4 | 12.248 | 12.05 | 11.809 | 11.574 | 10.567 | 9.839 | 9.42 | 9.207 | Primary | 930
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Falling Short | 5.37 | 5.136 | 4.869 | 4.558 | 4.197 | 3.784 | 3.332 | 0.655 | -2.466 | -4.97 | -6.576 | Primary | 931
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Falling Short | 16.498 | 16.376 | 16.234 | 16.071 | 15.881 | 15.668 | 15.457 | 14.486 | 13.664 | 13.032 | 12.538 | Primary | 932
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Falling Short | 11.63 | 9.892 | 9.665 | 9.403 | 9.097 | 8.747 | 8.367 | 6.163 | 3.673 | 1.756 | 0.577 | Primary | 933
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Falling Short | 4.695 | 4.609 | 4.508 | 4.392 | 4.255 | 4.1 | 3.95 | 3.306 | 2.828 | 2.492 | 2.224 | Primary | 934
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Falling Short | 14.816 | 14.69 | 14.517 | 14.295 | 14.011 | 13.671 | 13.342 | 11.981 | 11.068 | 10.574 | 10.337 | Primary | 935
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Falling Short | 0.026 | -0.101 | -0.251 | -0.428 | -0.644 | -0.893 | -1.14 | -2.293 | -3.298 | -4.01 | -4.483 | Primary | 936
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Falling Short | 9.181 | 8.955 | 8.68 | 8.352 | 7.955 | 7.496 | 7.047 | 5.032 | 3.372 | 2.166 | 1.273 | Primary | 937
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Falling Short | 8.423 | 8.303 | 8.132 | 7.905 | 7.605 | 7.239 | 6.882 | 5.331 | 4.157 | 3.466 | 3.118 | Primary | 938
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Falling Short | 5.441 | 5.168 | 4.836 | 4.435 | 3.95 | 3.392 | 2.848 | 0.397 | -1.63 | -3.081 | -4.162 | Primary | 939
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Falling Short | 16.062 | 15.94 | 15.77 | 15.548 | 15.257 | 14.903 | 14.555 | 12.996 | 11.716 | 10.924 | 10.522 | Primary | 940
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Falling Short | 8.136 | 8.165 | 8.175 | 8.165 | 8.131 | 8.079 | 8.017 | 7.592 | 7.029 | 6.632 | 6.457 | Primary | 941
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Falling Short | 16.444 | 17.281 | 17.087 | 8.651 | 8.381 | 8.07 | 7.771 | 6.503 | 5.638 | 5.1 | 4.695 | Primary | 942
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Falling Short | 10.912 | 10.592 | 10.203 | 9.742 | 9.192 | 8.56 | 7.941 | 5.169 | 3.03 | 1.613 | 0.611 | Primary | 943
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Falling Short | 8.716 | 8.729 | 8.732 | 8.719 | 8.69 | 8.65 | 8.607 | 8.351 | 8.055 | 7.857 | 7.754 | Primary | 944
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Falling Short | 10.76 | 10.53 | 10.234 | 9.874 | 9.43 | 8.91 | 8.41 | 6.349 | 5.066 | 4.372 | 3.915 | Primary | 945
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Falling Short | 4.844 | 4.397 | 3.882 | 3.283 | 2.584 | 1.792 | 0.985 | -3.09 | -7.102 | -10.24 | -12.47 | Primary | 946
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Falling Short | 12.932 | 12.964 | 12.995 | 13.019 | 13.04 | 13.059 | 13.077 | 13.129 | 13.139 | 13.139 | 13.134 | Primary | 947
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Falling Short | 13.642 | 13.683 | 13.713 | 13.727 | 13.725 | 13.705 | 13.671 | 13.306 | 12.709 | 12.28 | 12.152 | Primary | 948
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Falling Short | 2.662 | 2.702 | 2.737 | 2.763 | 2.783 | 2.795 | 2.804 | 2.799 | 2.73 | 2.672 | 2.644 | Primary | 949
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Falling Short | 6.371 | 6.3 | 6.213 | 6.109 | 5.973 | 5.808 | 5.646 | 4.952 | 4.451 | 4.158 | 3.994 | Primary | 950
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Falling Short | 1.863 | 1.733 | 1.587 | 1.426 | 1.237 | 1.023 | 0.811 | -0.169 | -0.986 | -1.584 | -2.026 | Primary | 951
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Falling Short | 12.705 | 12.573 | 12.391 | 12.159 | 11.864 | 11.512 | 11.157 | 9.452 | 8.079 | 7.268 | 6.875 | Primary | 952
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Falling Short | 12.55 | 10.555 | 10.553 | 10.535 | 10.502 | 10.456 | 10.403 | 10.051 | 9.594 | 9.287 | 9.166 | Primary | 953
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Falling Short | 9.312 | 9.131 | 15.924 | 15.691 | 15.392 | 15.035 | 14.689 | 13.279 | 12.381 | 11.89 | 11.604 | Primary | 954
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Falling Short | 11.335 | 11.204 | 11.059 | 10.895 | 10.71 | 10.503 | 10.28 | 8.991 | 7.514 | 6.276 | 5.369 | Primary | 955
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Falling Short | 3.285 | 1.823 | 1.565 | 1.313 | 0.996 | 0.623 | 0.257 | -1.338 | -2.508 | -3.281 | -3.847 | Primary | 956
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Falling Short | 12.806 | 12.738 | 12.665 | 12.582 | 12.491 | 12.394 | 12.294 | 11.767 | 11.204 | 10.651 | 10.1 | Primary | 957
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Falling Short | 8.427 | 8.378 | 15.291 | 15.166 | 14.992 | 14.776 | 14.562 | 13.588 | 12.794 | 12.312 | 12.053 | Primary | 958
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Falling Short | 5.381 | 4.397 | 4.099 | 3.806 | 3.442 | 3.012 | 2.581 | 0.514 | -1.362 | -2.686 | -3.501 | Primary | 959
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Falling Short | 10.198 | 10.019 | 9.774 | 9.469 | 9.079 | 8.614 | 8.17 | 6.384 | 5.212 | 4.546 | 4.125 | Primary | 960
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Falling Short | 12.664 | 12.538 | 10.297 | 10.101 | 9.853 | 9.545 | 9.183 | 6.78 | 3.681 | 1.331 | 0.236 | Primary | 961
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Falling Short | 9.382 | 9.139 | 8.837 | 8.477 | 8.039 | 7.527 | 7.022 | 4.735 | 2.917 | 1.694 | 0.892 | Primary | 962
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Falling Short | 7.802 | 6.015 | 5.835 | 5.62 | 5.342 | 5.008 | 4.681 | 3.261 | 2.217 | 1.6 | 1.269 | Primary | 963
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Falling Short | 8.408 | 7.685 | 7.71 | 7.708 | 7.68 | 7.63 | 7.561 | 6.948 | 6.008 | 5.345 | 5.124 | Primary | 964
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Falling Short | 18.849 | 18.833 | 18.801 | 18.745 | 18.661 | 18.544 | 18.397 | 17.323 | 15.849 | 14.813 | 14.498 | Primary | 965
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Falling Short | 8.564 | 8.524 | 8.448 | 8.338 | 8.182 | 7.988 | 7.799 | 7.037 | 6.552 | 6.287 | 6.123 | Primary | 966
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Falling Short | 10.561 | 10.433 | 10.261 | 10.042 | 9.764 | 9.433 | 9.101 | 7.557 | 6.37 | 5.668 | 5.284 | Primary | 967
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Falling Short | 12.423 | 12.331 | 12.2 | 12.027 | 11.802 | 11.534 | 11.277 | 10.22 | 9.52 | 9.147 | 8.925 | Primary | 968
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Falling Short | 12.242 | 12.253 | 12.247 | 12.223 | 12.179 | 12.118 | 12.049 | 11.626 | 11.079 | 10.683 | 10.484 | Primary | 969
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Falling Short | 8.249 | 8.311 | 8.368 | 8.418 | 8.456 | 8.486 | 8.511 | 8.572 | 8.549 | 8.518 | 8.493 | Primary | 970
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Falling Short | 8.171 | 6.374 | 6.334 | 6.274 | 6.182 | 6.062 | 5.93 | 5.175 | 4.342 | 3.76 | 3.471 | Primary | 971
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Falling Short | 10.227 | 9.005 | 9.035 | 9.05 | 9.052 | 9.048 | 9.041 | 8.97 | 8.851 | 8.768 | 8.704 | Primary | 972
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Falling Short | 1.696 | 1.57 | 1.423 | 1.255 | 1.055 | 0.827 | 0.604 | -0.396 | -1.208 | -1.801 | -2.263 | Primary | 973
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Falling Short | 3.354 | 3.346 | 3.334 | 3.318 | 3.295 | 3.266 | 3.236 | 3.085 | 2.931 | 2.812 | 2.712 | Primary | 974
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Falling Short | 13.738 | 13.655 | 13.55 | 13.417 | 13.251 | 13.051 | 12.827 | 11.449 | 9.777 | 8.502 | 7.825 | Primary | 975
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Falling Short | 24.478 | 24.447 | 24.413 | 24.371 | 24.324 | 24.275 | 24.223 | 23.924 | 23.556 | 23.178 | 22.79 | Primary | 976
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Falling Short | 14.896 | 14.91 | 14.913 | 14.905 | 14.884 | 14.853 | 14.822 | 14.689 | 14.586 | 14.516 | 14.459 | Primary | 977
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Falling Short | -1.147 | -1.37 | -1.612 | -1.879 | -2.173 | -2.49 | -2.816 | -4.548 | -6.416 | -8.155 | -9.713 | Primary | 978
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Falling Short | 3.528 | 3.287 | 3.008 | 2.672 | 2.271 | 1.803 | 1.279 | -1.965 | -5.939 | -9.041 | -10.818 | Primary | 979
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Falling Short | 11.021 | 10.952 | 10.841 | 10.688 | 10.482 | 10.232 | 9.99 | 9.02 | 8.414 | 8.104 | 7.938 | Primary | 980
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Falling Short | 11.604 | 11.655 | 11.698 | 11.727 | 11.744 | 11.746 | 11.737 | 11.547 | 11.182 | 10.911 | 10.835 | Primary | 981
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Falling Short | 8.54 | 8.298 | 7.994 | 7.626 | 7.174 | 6.643 | 6.112 | 3.606 | 1.417 | -0.102 | -1.038 | Primary | 982
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Falling Short | 17.061 | 16.395 | 16.339 | 16.273 | 16.197 | 16.114 | 16.031 | 15.635 | 15.284 | 15.006 | 14.745 | Primary | 983
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Falling Short | 5.075 | 4.905 | 4.715 | 4.507 | 4.248 | 3.943 | 3.652 | 2.514 | 1.881 | 1.561 | 1.363 | Primary | 984
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Falling Short | 8.607 | 8.479 | 8.293 | 8.048 | 7.729 | 7.349 | 6.982 | 5.488 | 4.588 | 4.128 | 3.856 | Primary | 985
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Falling Short | -1.166 | -1.266 | -1.391 | -1.544 | -1.734 | -1.957 | -2.173 | -3.079 | -3.711 | -4.089 | -4.345 | Primary | 986
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Falling Short | 15.314 | 15.25 | 15.173 | 15.071 | 14.946 | 14.797 | 14.63 | 13.593 | 12.32 | 11.353 | 10.827 | Primary | 987
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Falling Short | 16.183 | 15.914 | 15.68 | 15.485 | 15.237 | 14.94 | 14.648 | 13.355 | 12.369 | 11.793 | 11.535 | Primary | 988
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Falling Short | 10.622 | 10.498 | 10.31 | 10.064 | 9.743 | 9.355 | 8.98 | 7.381 | 6.209 | 5.493 | 5.064 | Primary | 989
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Falling Short | 24.216 | 24.238 | 24.258 | 24.276 | 24.289 | 24.299 | 24.307 | 24.327 | 24.316 | 24.303 | 24.293 | Primary | 990
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Falling Short | 8.422 | 8.437 | 8.449 | 8.455 | 8.453 | 8.447 | 8.442 | 8.389 | 8.297 | 8.239 | 8.198 | Primary | 991
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Falling Short | 11.224 | 11.112 | 10.946 | 10.728 | 10.444 | 10.105 | 9.78 | 8.483 | 7.682 | 7.252 | 6.993 | Primary | 992
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Falling Short | -0.876 | -0.962 | -1.055 | -1.154 | -1.26 | -1.371 | -1.485 | -2.095 | -2.747 | -3.413 | -4.085 | Primary | 993
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Falling Short | 9.152 | 9.029 | 8.891 | 8.737 | 8.563 | 8.373 | 8.179 | 7.173 | 6.133 | 5.216 | 4.426 | Primary | 994
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Falling Short | 13.403 | 13.269 | 13.09 | 12.867 | 12.585 | 12.25 | 11.927 | 10.608 | 9.785 | 9.332 | 9.049 | Primary | 995
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Falling Short | 11.573 | 11.402 | 11.203 | 10.973 | 10.701 | 10.393 | 10.086 | 8.657 | 7.408 | 6.49 | 5.8 | Primary | 996
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Falling Short | 8.223 | 7.922 | 7.562 | 7.139 | 6.639 | 6.066 | 5.504 | 2.954 | 1.007 | -0.261 | -1.157 | Primary | 997
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Falling Short | 13.311 | 13.027 | 12.721 | 12.387 | 12.022 | 11.625 | 11.208 | 8.911 | 6.358 | 4.125 | 2.363 | Primary | 998
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Falling Short | 7.583 | 7.565 | 7.514 | 7.424 | 7.29 | 7.115 | 6.919 | 5.744 | 4.396 | 3.487 | 3.131 | Primary | 999
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Falling Short | 13.978 | 13.888 | 13.757 | 13.587 | 13.365 | 13.099 | 12.843 | 11.798 | 11.085 | 10.673 | 10.425 | Primary | 1000
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Falling Short | 7.518 | 7.315 | 7.084 | 6.825 | 6.497 | 6.107 | 5.731 | 4.174 | 3.157 | 2.588 | 2.236 | Primary | 1001
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Falling Short | 7.857 | 7.683 | 7.489 | 7.265 | 7.01 | 6.73 | 6.44 | 4.848 | 3.084 | 1.576 | 0.37 | Primary | 1002
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - Leading the Way | 13.078 | 12.825 | 12.573 | 12.478 | 12.459 | 12.435 | 12.323 | 10.605 | 9.165 | 8.108 | 8.431 | Primary | 1003
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - Leading the Way | 12.589 | 10.944 | 10.846 | 10.69 | 10.58 | 10.422 | 10.132 | 6.993 | 4.614 | 3.177 | 3.422 | Primary | 1004
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - Leading the Way | 11.596 | 11.303 | 10.912 | 10.46 | 10.005 | 9.528 | 8.881 | 3.54 | -0.723 | -3.96 | -4.287 | Primary | 1005
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - Leading the Way | 5.925 | 4.523 | 4.527 | 4.495 | 4.472 | 4.426 | 4.317 | 1.88 | -0.002 | -1.304 | -0.85 | Primary | 1006
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 5.378 | 5.065 | 4.655 | 4.265 | 3.987 | 3.698 | 3.242 | -0.272 | -2.9 | -4.751 | -4.593 | Primary | 1007
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - Leading the Way | 5.349 | 5.342 | 5.31 | 5.272 | 5.269 | 5.261 | 5.208 | 4.425 | 3.802 | 3.346 | 3.499 | Primary | 1008
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - Leading the Way | 10.083 | 9.571 | 8.882 | 8.117 | 7.588 | 7.039 | 6.258 | -0.064 | -4.882 | -8.298 | -8.413 | Primary | 1009
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - Leading the Way | 17.138 | 17.162 | 17.161 | 17.147 | 17.165 | 17.179 | 17.15 | 15.744 | 14.571 | 13.647 | 13.997 | Primary | 1010
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - Leading the Way | 1.405 | 1.211 | 0.925 | 0.584 | 0.289 | -0.023 | -0.497 | -4.922 | -8.494 | -11.257 | -11.314 | Primary | 1011
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - Leading the Way | 2.981 | 2.451 | 2.562 | 2.651 | 2.761 | 2.863 | 2.933 | 2.227 | 1.675 | 1.286 | 1.802 | Primary | 1012
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - Leading the Way | 12.166 | 11.942 | 11.6 | 11.192 | 10.924 | 10.64 | 10.217 | 6.529 | 3.709 | 1.667 | 1.653 | Primary | 1013
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - Leading the Way | 2.629 | 2.333 | 1.933 | 1.545 | 1.247 | 0.903 | 0.415 | -4.377 | -7.754 | -9.91 | -9.582 | Primary | 1014
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - Leading the Way | 3.091 | 3.086 | 3.071 | 3.049 | 3.032 | 3.012 | 2.979 | 2.609 | 2.305 | 2.078 | 2.061 | Primary | 1015
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - Leading the Way | 15.838 | 15.649 | 15.35 | 14.995 | 14.802 | 14.599 | 14.249 | 10.657 | 7.913 | 5.952 | 6.269 | Primary | 1016
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - Leading the Way | 12.949 | 12.484 | 12.45 | 12.403 | 12.39 | 12.374 | 12.325 | 11.468 | 10.737 | 10.16 | 10.216 | Primary | 1017
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - Leading the Way | 10.607 | 10.603 | 10.552 | 10.468 | 10.429 | 10.373 | 10.255 | 8.004 | 6.297 | 5.152 | 5.616 | Primary | 1018
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - Leading the Way | 15.641 | 15.305 | 14.814 | 14.243 | 13.815 | 13.353 | 12.702 | 7.969 | 4.518 | 2.301 | 2.279 | Primary | 1019
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - Leading the Way | 8.449 | 8.471 | 8.466 | 8.438 | 8.423 | 8.396 | 8.306 | 6.869 | 5.734 | 4.968 | 5.234 | Primary | 1020
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - Leading the Way | 6.698 | 6.574 | 6.385 | 6.15 | 6.002 | 5.843 | 5.574 | 1.914 | -1.253 | -3.853 | -3.947 | Primary | 1021
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - Leading the Way | 21.815 | 21.779 | 21.682 | 21.544 | 21.455 | 21.357 | 21.177 | 19.689 | 18.58 | 17.814 | 17.982 | Primary | 1022
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - Leading the Way | 3.811 | 3.681 | 3.513 | 3.324 | 3.207 | 3.085 | 2.895 | 0.902 | -0.839 | -2.282 | -2.544 | Primary | 1023
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - Leading the Way | 11.559 | 11.075 | 10.391 | 9.603 | 9.045 | 8.445 | 7.572 | 0.376 | -5.045 | -8.75 | -8.834 | Primary | 1024
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - Leading the Way | 9.565 | 9.207 | 8.703 | 8.168 | 7.786 | 7.379 | 6.743 | 1.474 | -2.44 | -5.151 | -4.896 | Primary | 1025
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - Leading the Way | 14.942 | 14.698 | 14.357 | 14.014 | 13.761 | 13.496 | 13.105 | 10.361 | 8.396 | 7.097 | 7.218 | Primary | 1026
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - Leading the Way | 2.552 | 2.49 | 2.31 | 2.045 | 1.924 | 1.757 | 1.415 | -2.834 | -6.056 | -8.123 | -7.601 | Primary | 1027
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - Leading the Way | 5.915 | 5.709 | 5.412 | 5.059 | 4.781 | 4.477 | 4.061 | 1 | -1.276 | -2.776 | -2.928 | Primary | 1028
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 15.137 | 15.111 | 15.063 | 15.004 | 14.965 | 14.917 | 14.825 | 13.342 | 12.132 | 11.235 | 11.395 | Primary | 1029
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - Leading the Way | 4.302 | 1.225 | 1.146 | 1.016 | 0.92 | 0.775 | 0.472 | -4.127 | -7.727 | -10.152 | -9.551 | Primary | 1030
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - Leading the Way | 8.297 | 8.183 | 7.971 | 7.682 | 7.469 | 7.205 | 6.79 | 2.485 | -0.859 | -3.08 | -2.983 | Primary | 1031
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - Leading the Way | 11.774 | 11.485 | 11.029 | 10.476 | 10.127 | 9.759 | 9.126 | 3.442 | -0.926 | -4.088 | -3.794 | Primary | 1032
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - Leading the Way | 6.166 | 5.734 | 5.071 | 4.273 | 3.684 | 3.043 | 2.056 | -6.156 | -12.363 | -16.653 | -16.534 | Primary | 1033
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - Leading the Way | 6.844 | 6.825 | 6.803 | 6.777 | 6.755 | 6.733 | 6.706 | 6.346 | 6.03 | 5.757 | 5.726 | Primary | 1034
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - Leading the Way | 4.341 | 4.31 | 4.264 | 4.209 | 4.16 | 4.104 | 4.029 | 3.306 | 2.751 | 2.342 | 2.305 | Primary | 1035
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - Leading the Way | 13.79 | 13.471 | 13.001 | 12.451 | 12.12 | 11.769 | 11.22 | 6.452 | 2.912 | 0.445 | 0.575 | Primary | 1036
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 13.961 | 13.874 | 13.785 | 13.689 | 13.591 | 13.493 | 13.393 | 12.233 | 11.048 | 9.88 | 9.379 | Primary | 1037
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - Leading the Way | 5.542 | 5.463 | 5.353 | 5.227 | 5.135 | 5.039 | 4.905 | 3.929 | 3.242 | 2.784 | 2.788 | Primary | 1038
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - Leading the Way | 10.62 | 10.325 | 9.863 | 9.322 | 8.98 | 8.618 | 8.026 | 2.478 | -1.608 | -4.46 | -4.052 | Primary | 1039
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - Leading the Way | 11.544 | 11.281 | 10.861 | 10.365 | 9.986 | 9.576 | 8.934 | 3.65 | -0.228 | -2.864 | -2.619 | Primary | 1040
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - Leading the Way | 9.31 | 9.331 | 9.302 | 9.24 | 9.247 | 9.238 | 9.148 | 7.204 | 5.661 | 4.588 | 4.973 | Primary | 1041
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - Leading the Way | 10.361 | 10.352 | 10.291 | 10.2 | 10.144 | 10.076 | 9.947 | 8.37 | 7.322 | 6.643 | 6.926 | Primary | 1042
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - Leading the Way | 17.455 | 17.284 | 17.038 | 16.749 | 16.521 | 16.268 | 15.923 | 13.596 | 12.001 | 11.082 | 11.087 | Primary | 1043
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - Leading the Way | 7.912 | 22.43 | 22.155 | 21.841 | 21.609 | 21.364 | 20.954 | 17.024 | 13.999 | 11.786 | 12.05 | Primary | 1044
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - Leading the Way | 10.743 | 10.335 | 9.726 | 8.994 | 8.436 | 7.863 | 6.997 | 0.086 | -5.446 | -9.676 | -9.893 | Primary | 1045
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - Leading the Way | 3.864 | 3.754 | 3.605 | 3.461 | 3.37 | 3.275 | 3.134 | 2.086 | 1.338 | 0.85 | 0.919 | Primary | 1046
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - Leading the Way | 6.235 | 5.585 | 4.762 | 3.953 | 3.304 | 2.618 | 1.643 | -5.333 | -10.488 | -13.907 | -13.748 | Primary | 1047
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - Leading the Way | 4.644 | 4.256 | 3.709 | 3.064 | 2.42 | 1.736 | 0.772 | -7.604 | -14.114 | -19.208 | -19.699 | Primary | 1048
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - Leading the Way | 6.009 | 5.472 | 4.689 | 3.755 | 3.043 | 2.299 | 1.196 | -7.693 | -14.693 | -19.928 | -20.235 | Primary | 1049
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - Leading the Way | 4.315 | 4.373 | 4.422 | 4.461 | 4.497 | 4.526 | 4.543 | 4.311 | 4.144 | 4.067 | 4.227 | Primary | 1050
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - Leading the Way | 7.938 | 7.467 | 6.741 | 5.846 | 5.162 | 4.387 | 3.25 | -5.514 | -11.923 | -15.953 | -15.969 | Primary | 1051
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - Leading the Way | 13.029 | 13.107 | 13.171 | 13.22 | 13.263 | 13.296 | 13.315 | 12.462 | 11.782 | 11.312 | 11.65 | Primary | 1052
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - Leading the Way | 10.29 | 10.417 | 10.535 | 10.647 | 10.752 | 10.854 | 10.948 | 11.104 | 11.22 | 11.326 | 11.637 | Primary | 1053
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - Leading the Way | 11.059 | 11.144 | 11.198 | 11.263 | 11.352 | 11.428 | 11.442 | 9.558 | 8.028 | 6.897 | 7.607 | Primary | 1054
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - Leading the Way | 11.739 | 11.791 | 11.821 | 11.841 | 11.881 | 11.914 | 11.918 | 11.198 | 10.651 | 10.264 | 10.574 | Primary | 1055
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - Leading the Way | 10.932 | 10.636 | 10.178 | 9.637 | 9.247 | 8.804 | 8.142 | 3.132 | -0.385 | -2.431 | -2.234 | Primary | 1056
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - Leading the Way | 4.289 | 4.219 | 4.113 | 3.992 | 3.871 | 3.745 | 3.592 | 2.937 | 2.584 | 2.404 | 2.326 | Primary | 1057
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - Leading the Way | 5.268 | 5.253 | 5.213 | 5.159 | 5.116 | 5.067 | 4.994 | 4.357 | 3.791 | 3.303 | 3.105 | Primary | 1058
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - Leading the Way | 13.735 | 13.279 | 12.675 | 12.08 | 11.637 | 11.17 | 10.439 | 4.516 | 0.169 | -2.805 | -2.474 | Primary | 1059
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - Leading the Way | 0.005 | 0.004 | -0.009 | -0.031 | -0.049 | -0.072 | -0.11 | -0.543 | -0.896 | -1.165 | -1.19 | Primary | 1060
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - Leading the Way | 3.335 | 3.137 | 2.873 | 2.584 | 2.362 | 2.129 | 1.826 | -0.417 | -1.99 | -3.079 | -3.123 | Primary | 1061
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - Leading the Way | 9.657 | 9.422 | 9.05 | 8.6 | 8.312 | 7.987 | 7.499 | 3.221 | 0.147 | -1.754 | -1.526 | Primary | 1062
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - Leading the Way | 9.196 | 9.067 | 8.889 | 8.745 | 8.658 | 8.559 | 8.359 | 5.663 | 3.652 | 2.206 | 2.627 | Primary | 1063
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - Leading the Way | 5.41 | 5.114 | 4.705 | 4.246 | 3.921 | 3.574 | 3.072 | -1.565 | -5.264 | -8.048 | -8.249 | Primary | 1064
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - Leading the Way | 4.797 | 4.819 | 4.834 | 4.843 | 4.851 | 4.855 | 4.846 | 4.578 | 4.377 | 4.253 | 4.332 | Primary | 1065
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - Leading the Way | 21.98 | 21.798 | 21.534 | 21.257 | 21.098 | 20.929 | 20.627 | 17.539 | 15.179 | 13.502 | 13.841 | Primary | 1066
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - Leading the Way | 7.939 | 7.981 | 7.997 | 8.013 | 8.064 | 8.107 | 8.108 | 6.847 | 5.844 | 5.096 | 5.528 | Primary | 1067
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - Leading the Way | 13.506 | 13.177 | 12.757 | 12.381 | 12.108 | 11.821 | 11.353 | 7.532 | 4.747 | 2.842 | 3.167 | Primary | 1068
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - Leading the Way | 7.277 | 7.244 | 7.125 | 6.95 | 6.834 | 6.7 | 6.434 | 2.999 | 0.426 | -1.427 | -0.985 | Primary | 1069
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - Leading the Way | 4.774 | 4.107 | 3.172 | 2.182 | 1.541 | 0.862 | -0.202 | -8.804 | -15.114 | -19.349 | -18.867 | Primary | 1070
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - Leading the Way | 0.957 | 0.919 | 0.871 | 0.815 | 0.761 | 0.704 | 0.632 | -0.119 | -0.765 | -1.3 | -1.406 | Primary | 1071
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - Leading the Way | 3.188 | 3.067 | 2.891 | 2.672 | 2.477 | 2.251 | 1.939 | -1.162 | -3.706 | -5.588 | -5.877 | Primary | 1072
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - Leading the Way | 12.98 | 12.927 | 12.805 | 12.638 | 12.508 | 12.367 | 12.128 | 10.008 | 8.44 | 7.369 | 7.628 | Primary | 1073
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - Leading the Way | 14.826 | 14.624 | 15.286 | 14.865 | 14.597 | 14.315 | 13.836 | 9.443 | 6.154 | 3.805 | 4.091 | Primary | 1074
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - Leading the Way | 22.304 | 22.264 | 22.118 | 21.863 | 21.583 | 21.198 | 20.624 | 14.475 | 9.952 | 7.359 | 7.759 | Primary | 1075
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - Leading the Way | 9.832 | 9.536 | 9.121 | 8.636 | 8.256 | 7.854 | 7.281 | 2.377 | -1.522 | -4.472 | -4.752 | Primary | 1076
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - Leading the Way | 2.437 | 2.194 | 1.869 | 1.498 | 1.255 | 0.996 | 0.626 | -2.492 | -4.79 | -6.44 | -6.53 | Primary | 1077
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - Leading the Way | 8.173 | 7.795 | 7.161 | 6.381 | 5.969 | 5.538 | 4.744 | -2.86 | -8.812 | -13.136 | -12.631 | Primary | 1078
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - Leading the Way | 6.094 | 3.8 | 3.778 | 3.735 | 3.702 | 3.657 | 3.559 | 2.125 | 0.998 | 0.197 | 0.36 | Primary | 1079
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - Leading the Way | 7.489 | 7.022 | 6.329 | 5.538 | 4.99 | 4.413 | 3.528 | -3.397 | -8.323 | -11.632 | -11.256 | Primary | 1080
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - Leading the Way | 3.919 | 3.655 | 17.944 | 17.458 | 17.074 | 16.66 | 15.99 | 10.114 | 5.691 | 2.624 | 2.989 | Primary | 1081
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - Leading the Way | -0.173 | -0.309 | -0.504 | -0.735 | -0.92 | -1.111 | -1.39 | -3.804 | -5.743 | -7.27 | -7.394 | Primary | 1082
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - Leading the Way | 2.851 | 2.854 | 2.838 | 2.807 | 2.795 | 2.777 | 2.732 | 1.849 | 1.189 | 0.755 | 0.938 | Primary | 1083
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - Leading the Way | 10.457 | 10.171 | 9.707 | 9.15 | 8.768 | 8.366 | 7.733 | 2.74 | -0.983 | -3.561 | -3.241 | Primary | 1084
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - Leading the Way | 8.563 | 8.204 | 7.657 | 7.018 | 6.637 | 6.225 | 5.562 | -0.465 | -4.884 | -7.838 | -7.487 | Primary | 1085
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - Leading the Way | 12.481 | 12.368 | 12.178 | 11.948 | 11.783 | 11.598 | 11.327 | 9.191 | 7.675 | 6.723 | 6.77 | Primary | 1086
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - Leading the Way | 3.812 | 2.868 | 2.86 | 2.797 | 2.774 | 2.716 | 2.536 | -0.187 | -2.342 | -3.768 | -3.319 | Primary | 1087
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - Leading the Way | 15.278 | 15.184 | 15.052 | 14.884 | 14.723 | 14.534 | 14.287 | 11.663 | 9.54 | 8.023 | 7.847 | Primary | 1088
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - Leading the Way | 4.098 | 3.996 | 3.85 | 3.682 | 3.562 | 3.436 | 3.249 | 1.631 | 0.341 | -0.628 | -0.658 | Primary | 1089
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - Leading the Way | 2.461 | 2.396 | 2.291 | 2.166 | 2.084 | 1.998 | 1.85 | 0.435 | -0.637 | -1.401 | -1.272 | Primary | 1090
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - Leading the Way | 14.978 | 14.625 | 14.094 | 13.463 | 13.015 | 12.524 | 11.786 | 5.332 | 0.424 | -3.032 | -3.091 | Primary | 1091
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - Leading the Way | 1.969 | 1.805 | 1.504 | 1.121 | 0.83 | 0.512 | -0.05 | -6.092 | -10.69 | -14.08 | -13.64 | Primary | 1092
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - Leading the Way | 14.835 | 14.755 | 14.604 | 14.41 | 14.349 | 14.276 | 14.095 | 11.52 | 9.496 | 8.09 | 8.463 | Primary | 1093
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - Leading the Way | 4.719 | 4.617 | 4.477 | 4.317 | 4.183 | 4.042 | 3.85 | 2.294 | 1.081 | 0.168 | 0.095 | Primary | 1094
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - Leading the Way | 6.931 | 6.478 | 5.823 | 5.069 | 4.501 | 3.898 | 3.077 | -3.151 | -7.663 | -10.777 | -10.855 | Primary | 1095
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - Leading the Way | 12.641 | 12.298 | 11.804 | 11.246 | 10.865 | 10.466 | 9.897 | 5.406 | 2.055 | -0.341 | -0.389 | Primary | 1096
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - Leading the Way | 12.887 | 11.212 | 11.079 | 10.863 | 10.677 | 10.411 | 9.993 | 5.899 | 2.984 | 1.528 | 1.88 | Primary | 1097
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - Leading the Way | 2.953 | 2.689 | 2.387 | 2.161 | 1.976 | 1.785 | 1.533 | 0.092 | -0.831 | -1.353 | -1.267 | Primary | 1098
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - Leading the Way | 7.988 | 7.267 | 6.3 | 5.235 | 4.501 | 3.739 | 2.67 | -4.954 | -10.57 | -14.343 | -14.522 | Primary | 1099
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - Leading the Way | 8.538 | 8.536 | 8.527 | 8.512 | 8.499 | 8.482 | 8.458 | 8.269 | 8.085 | 7.908 | 7.775 | Primary | 1100
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - Leading the Way | 1.978 | 1.755 | 1.407 | 0.945 | 0.436 | -0.195 | -1.043 | -7.119 | -11.344 | -13.452 | -13.649 | Primary | 1101
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - Leading the Way | 11.798 | 11.422 | 10.928 | 10.453 | 10.151 | 9.827 | 9.279 | 4.034 | -0.054 | -2.988 | -2.702 | Primary | 1102
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - Leading the Way | 9.322 | 8.926 | 8.316 | 7.575 | 7.087 | 6.554 | 5.738 | -0.778 | -5.561 | -8.7 | -8.558 | Primary | 1103
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - Leading the Way | 0.877 | 0.762 | 0.594 | 0.381 | 0.171 | -0.079 | -0.404 | -2.719 | -4.376 | -5.298 | -5.511 | Primary | 1104
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - Leading the Way | 7.431 | 7.084 | 6.555 | 5.932 | 5.494 | 5.038 | 4.321 | -2.032 | -6.989 | -10.691 | -10.547 | Primary | 1105
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - Leading the Way | 0.906 | 0.866 | 0.76 | 0.617 | 0.565 | 0.498 | 0.335 | -2.292 | -4.331 | -5.736 | -5.257 | Primary | 1106
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - Leading the Way | 1.488 | 1.487 | 1.487 | 1.486 | 1.485 | 1.484 | 1.482 | 1.465 | 1.449 | 1.434 | 1.427 | Primary | 1107
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 10.495 | 10.523 | 10.506 | 10.459 | 10.475 | 10.484 | 10.432 | 8.623 | 7.196 | 6.128 | 6.595 | Primary | 1108
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - Leading the Way | 7.128 | 7.09 | 7.02 | 6.935 | 6.89 | 6.84 | 6.751 | 5.603 | 4.753 | 4.149 | 4.285 | Primary | 1109
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 8.505 | 8.423 | 8.301 | 8.157 | 8.031 | 7.901 | 7.728 | 6.619 | 5.83 | 5.287 | 5.254 | Primary | 1110
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - Leading the Way | 3.92 | 3.714 | 3.42 | 3.089 | 2.852 | 2.588 | 2.195 | -0.864 | -3.168 | -4.684 | -4.754 | Primary | 1111
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - Leading the Way | 14.573 | 14.266 | 13.847 | 14.369 | 13.941 | 13.5 | 12.909 | 8.743 | 5.585 | 3.356 | 3.228 | Primary | 1112
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - Leading the Way | 10.105 | 9.024 | 8.613 | 8.115 | 7.814 | 7.497 | 6.982 | 2.322 | -1.2 | -3.735 | -3.545 | Primary | 1113
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - Leading the Way | 3.254 | 3.063 | 2.801 | 2.491 | 2.189 | 1.849 | 1.392 | -2.134 | -4.799 | -6.623 | -6.931 | Primary | 1114
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - Leading the Way | 10.759 | 10.075 | 9.318 | 8.81 | 8.5 | 8.172 | 7.619 | 2.614 | -1.257 | -4.003 | -3.647 | Primary | 1115
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - Leading the Way | 10.774 | 10.718 | 10.639 | 10.544 | 10.489 | 10.43 | 10.331 | 8.865 | 7.502 | 6.302 | 6.093 | Primary | 1116
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - Leading the Way | -2.973 | -3.665 | -4.651 | -5.784 | -6.631 | -7.515 | -8.791 | -18.659 | -26.208 | -31.638 | -31.863 | Primary | 1117
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - Leading the Way | 7.079 | 6.423 | 5.559 | 4.711 | 4.153 | 3.574 | 2.727 | -3.235 | -7.42 | -10.011 | -9.558 | Primary | 1118
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - Leading the Way | 5.265 | 5.27 | 5.179 | 5.02 | 5.063 | 5.089 | 4.944 | 1.677 | -1.049 | -3.131 | -2.607 | Primary | 1119
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - Leading the Way | 17.266 | 14.222 | 14.027 | 13.806 | 13.636 | 13.461 | 13.232 | 10.881 | 8.891 | 7.232 | 6.99 | Primary | 1120
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - Leading the Way | 13.888 | 13.847 | 13.779 | 13.686 | 13.593 | 13.479 | 13.329 | 11.706 | 10.377 | 9.424 | 9.285 | Primary | 1121
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - Leading the Way | 9.605 | 9.388 | 9.108 | 8.764 | 8.403 | 7.976 | 7.45 | 3.214 | -0.172 | -2.49 | -3.25 | Primary | 1122
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - Leading the Way | 12.758 | 12.736 | 12.658 | 12.545 | 12.525 | 12.499 | 12.397 | 10.096 | 8.219 | 6.785 | 7.168 | Primary | 1123
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - Leading the Way | 11.525 | 11.567 | 11.571 | 11.55 | 11.573 | 11.59 | 11.558 | 10.654 | 9.967 | 9.518 | 9.84 | Primary | 1124
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - Leading the Way | 4.17 | 3.988 | 3.763 | 3.49 | 3.184 | 2.822 | 2.389 | -0.944 | -3.618 | -5.438 | -6.214 | Primary | 1125
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - Leading the Way | 16.338 | 16.265 | 16.147 | 15.998 | 15.926 | 15.84 | 15.677 | 13.737 | 12.156 | 11.028 | 11.072 | Primary | 1126
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - Leading the Way | 10.815 | 10.523 | 10.062 | 9.514 | 9.22 | 8.906 | 8.377 | 3.299 | -0.523 | -3.157 | -2.744 | Primary | 1127
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - Leading the Way | 10.327 | 10.21 | 9.985 | 9.694 | 9.584 | 9.452 | 9.161 | 5.33 | 2.331 | 0.269 | 0.753 | Primary | 1128
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - Leading the Way | 7.106 | 6.752 | 6.184 | 5.491 | 5.022 | 4.503 | 3.704 | -2.757 | -7.343 | -10.252 | -9.817 | Primary | 1129
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - Leading the Way | 4.536 | 4.159 | 3.62 | 3.009 | 2.542 | 2.028 | 1.3 | -4.581 | -8.992 | -11.909 | -11.909 | Primary | 1130
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - Leading the Way | 11.73 | 11.716 | 11.655 | 11.562 | 11.448 | 11.287 | 11.053 | 9.269 | 8.138 | 7.717 | 7.846 | Primary | 1131
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - Leading the Way | 15.422 | 15.104 | 14.606 | 14 | 13.677 | 13.34 | 12.768 | 7.69 | 3.858 | 1.162 | 1.468 | Primary | 1132
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - Leading the Way | 9.264 | 8.792 | 8.089 | 7.235 | 6.56 | 5.801 | 4.718 | -3.595 | -9.592 | -13.401 | -13.53 | Primary | 1133
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - Leading the Way | 3.295 | 3.179 | 3.016 | 3.328 | 3.182 | 3.029 | 2.815 | 1.16 | -0.093 | -1.013 | -1.109 | Primary | 1134
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - Leading the Way | 8.04 | 7.822 | 7.457 | 7.025 | 6.695 | 6.349 | 5.753 | 0.279 | -3.964 | -7.079 | -6.608 | Primary | 1135
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - Leading the Way | 4.144 | 3.944 | 3.642 | 3.297 | 3.094 | 2.883 | 2.543 | -0.186 | -2.219 | -3.632 | -3.526 | Primary | 1136
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 12.3 | 12.284 | 12.241 | 12.179 | 12.15 | 12.113 | 12.037 | 10.855 | 9.851 | 9.05 | 9.052 | Primary | 1137
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - Leading the Way | 25.328 | 25.285 | 25.219 | 25.136 | 25.086 | 25.032 | 24.944 | 23.568 | 22.404 | 21.472 | 21.507 | Primary | 1138
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - Leading the Way | 14.657 | 14.514 | 14.307 | 14.056 | 13.826 | 13.572 | 13.239 | 11.127 | 9.667 | 8.794 | 8.706 | Primary | 1139
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - Leading the Way | 12.697 | 12.748 | 12.776 | 12.787 | 12.814 | 12.837 | 12.83 | 11.699 | 10.799 | 10.117 | 10.455 | Primary | 1140
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - Leading the Way | 19.833 | 19.813 | 19.782 | 19.745 | 19.721 | 19.696 | 19.66 | 18.923 | 18.243 | 17.641 | 17.589 | Primary | 1141
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - Leading the Way | 6.817 | 6.553 | 6.139 | 5.645 | 5.349 | 5.037 | 4.55 | 0.502 | -2.391 | -4.275 | -3.938 | Primary | 1142
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - Leading the Way | 22.491 | 22.482 | 22.396 | 22.26 | 22.223 | 22.168 | 22.003 | 19.233 | 17.082 | 15.546 | 16.03 | Primary | 1143
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - Leading the Way | 14.575 | 14.501 | 14.367 | 14.208 | 14.182 | 14.151 | 14.016 | 11.361 | 9.203 | 7.604 | 8.048 | Primary | 1144
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - Leading the Way | 4.735 | 4.649 | 4.513 | 4.352 | 4.258 | 4.155 | 3.985 | 2.53 | 1.469 | 0.755 | 0.845 | Primary | 1145
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - Leading the Way | 4.522 | 4.502 | 4.475 | 4.444 | 4.415 | 4.38 | 4.338 | 4.032 | 3.785 | 3.609 | 3.519 | Primary | 1146
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - Leading the Way | 15.691 | 15.609 | 15.471 | 15.292 | 15.167 | 15.018 | 14.789 | 11.883 | 9.484 | 7.701 | 7.702 | Primary | 1147
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 9.661 | 9.523 | 9.306 | 9.045 | 8.845 | 8.633 | 8.298 | 5.618 | 3.673 | 2.358 | 2.553 | Primary | 1148
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - Leading the Way | 11.537 | 11.442 | 11.291 | 11.109 | 10.996 | 10.879 | 10.669 | 8.661 | 7.131 | 6.044 | 6.229 | Primary | 1149
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - Leading the Way | 2.327 | 2.18 | 1.985 | 1.769 | 1.571 | 1.365 | 1.078 | -1.014 | -2.661 | -3.951 | -4.179 | Primary | 1150
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - Leading the Way | 3.473 | 3.261 | 2.962 | 2.605 | 2.398 | 2.16 | 1.779 | -2.986 | -6.882 | -9.836 | -9.899 | Primary | 1151
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - Leading the Way | 18.929 | 18.909 | 18.869 | 18.813 | 18.768 | 18.709 | 18.619 | 17.815 | 17.217 | 16.869 | 16.867 | Primary | 1152
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - Leading the Way | 4.845 | 4.763 | 4.639 | 4.494 | 4.395 | 4.292 | 4.114 | 2.526 | 1.315 | 0.437 | 0.541 | Primary | 1153
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - Leading the Way | 14.798 | 14.783 | 14.747 | 14.712 | 14.696 | 14.669 | 14.593 | 13.373 | 12.4 | 11.703 | 11.868 | Primary | 1154
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - Leading the Way | 12.646 | 12.738 | 12.812 | 12.872 | 12.939 | 12.994 | 13.026 | 12.681 | 12.419 | 12.289 | 12.568 | Primary | 1155
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - Leading the Way | 2.222 | 1.913 | 1.471 | 0.949 | 0.532 | 0.087 | -0.513 | -4.39 | -7.086 | -8.761 | -8.863 | Primary | 1156
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 5.917 | 5.885 | 5.824 | 5.746 | 5.704 | 5.655 | 5.566 | 4.371 | 3.389 | 2.66 | 2.728 | Primary | 1157
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - Leading the Way | 5.275 | 5.229 | 5.149 | 5.044 | 4.968 | 4.874 | 4.726 | 3.318 | 2.239 | 1.554 | 1.56 | Primary | 1158
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - Leading the Way | 5.25 | 4.92 | 4.449 | 3.899 | 3.477 | 3.025 | 2.372 | -2.797 | -6.72 | -9.502 | -9.642 | Primary | 1159
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - Leading the Way | 15.341 | 15.259 | 15.136 | 14.984 | 14.899 | 14.804 | 14.645 | 12.595 | 10.903 | 9.632 | 9.697 | Primary | 1160
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - Leading the Way | 8.194 | 7.634 | 6.894 | 6.17 | 5.592 | 4.989 | 4.074 | -2.878 | -7.948 | -11.522 | -11.294 | Primary | 1161
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - Leading the Way | 4.891 | 4.807 | 4.658 | 4.488 | 4.389 | 4.262 | 3.993 | 0.196 | -2.819 | -4.975 | -4.54 | Primary | 1162
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - Leading the Way | 10.393 | 10.084 | 9.578 | 8.951 | 8.56 | 8.153 | 7.441 | 0.584 | -4.907 | -9.04 | -8.757 | Primary | 1163
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - Leading the Way | 0.257 | 0.171 | 0.057 | -0.078 | -0.168 | -0.268 | -0.422 | -2.204 | -3.665 | -4.779 | -4.834 | Primary | 1164
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - Leading the Way | 13.443 | 13.138 | 12.676 | 12.15 | 11.778 | 11.38 | 10.759 | 5.789 | 2.123 | -0.374 | -0.162 | Primary | 1165
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - Leading the Way | 18.437 | 18.429 | 18.405 | 18.367 | 18.345 | 18.314 | 18.259 | 17.22 | 16.41 | 15.818 | 15.972 | Primary | 1166
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - Leading the Way | 12.619 | 12.391 | 12.083 | 11.735 | 11.566 | 11.387 | 11.089 | 7.841 | 5.138 | 3.038 | 2.856 | Primary | 1167
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - Leading the Way | 7.167 | 7.047 | 6.866 | 6.64 | 6.463 | 6.266 | 5.945 | 2.747 | 0.086 | -1.943 | -2.04 | Primary | 1168
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - Leading the Way | 8.24 | 8.092 | 7.84 | 7.5 | 7.262 | 6.969 | 6.467 | 1.264 | -2.948 | -5.914 | -5.993 | Primary | 1169
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - Leading the Way | 16.349 | 16.336 | 16.32 | 16.303 | 16.284 | 16.263 | 16.24 | 16.085 | 15.908 | 15.716 | 15.54 | Primary | 1170
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - Leading the Way | 16.966 | 16.875 | 16.721 | 16.531 | 16.38 | 16.216 | 15.962 | 13.595 | 11.864 | 10.63 | 10.792 | Primary | 1171
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - Leading the Way | 18.994 | 18.95 | 18.882 | 18.801 | 18.746 | 18.689 | 18.591 | 17.472 | 16.543 | 15.811 | 15.849 | Primary | 1172
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - Leading the Way | 9.137 | 8.606 | 7.96 | 7.421 | 7.113 | 6.79 | 6.261 | 1.379 | -2.317 | -4.89 | -4.512 | Primary | 1173
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - Leading the Way | 10.46 | 10.023 | 9.41 | 8.766 | 8.342 | 7.896 | 7.191 | 1.37 | -2.802 | -5.634 | -5.286 | Primary | 1174
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - Leading the Way | -6.478 | -6.363 | -6.275 | -6.206 | -6.137 | -6.085 | -6.068 | -6.568 | -6.912 | -7.051 | -6.684 | Primary | 1175
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - Leading the Way | 10.156 | 9.488 | 8.683 | 8.006 | 7.545 | 7.066 | 6.287 | -0.489 | -5.681 | -9.432 | -9.074 | Primary | 1176
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - Leading the Way | 11.42 | 11.295 | 11.1 | 10.847 | 10.669 | 10.457 | 10.123 | 6.17 | 3.023 | 0.768 | 0.805 | Primary | 1177
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - Leading the Way | 5.23 | 4.925 | 4.494 | 3.996 | 3.63 | 3.253 | 2.718 | -1.678 | -5.07 | -7.607 | -7.707 | Primary | 1178
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - Leading the Way | 24.507 | 24.478 | 24.379 | 24.233 | 24.205 | 24.168 | 24.025 | 20.879 | 18.343 | 16.461 | 17.019 | Primary | 1179
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - Leading the Way | 6.495 | 6.3 | 6.03 | 5.721 | 5.489 | 5.237 | 4.892 | 1.915 | -0.462 | -2.211 | -2.496 | Primary | 1180
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - Leading the Way | 6.769 | 6.76 | 6.743 | 6.723 | 6.711 | 6.699 | 6.677 | 6.447 | 6.288 | 6.186 | 6.218 | Primary | 1181
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - Leading the Way | 11.676 | 11.098 | 10.236 | 9.219 | 8.602 | 7.954 | 6.948 | -1.516 | -7.99 | -12.589 | -12.54 | Primary | 1182
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - Leading the Way | 21.981 | 21.991 | 21.96 | 21.879 | 21.756 | 21.57 | 21.31 | 19.322 | 18.019 | 17.601 | 17.67 | Primary | 1183
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - Leading the Way | 11.277 | 11.027 | 10.637 | 10.183 | 9.912 | 9.62 | 9.135 | 4.486 | 0.986 | -1.438 | -1.063 | Primary | 1184
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - Leading the Way | 12.095 | 11.941 | 11.695 | 11.353 | 10.962 | 10.464 | 9.768 | 4.003 | -0.294 | -2.768 | -2.959 | Primary | 1185
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - Leading the Way | 0.762 | 0.67 | 0.534 | 0.368 | 0.221 | 0.055 | -0.176 | -2.215 | -3.776 | -4.902 | -5.016 | Primary | 1186
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - Leading the Way | 7.086 | 1.348 | 0.999 | 0.592 | 0.286 | -0.039 | -0.493 | -3.817 | -6.276 | -7.943 | -8.008 | Primary | 1187
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 1188
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - Leading the Way | 5.072 | 4.812 | 4.446 | 4.025 | 3.734 | 3.429 | 2.994 | -0.61 | -3.392 | -5.461 | -5.67 | Primary | 1189
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - Leading the Way | 12.913 | 12.693 | 12.351 | 11.922 | 11.5 | 10.967 | 10.217 | 4.148 | -0.098 | -2.281 | -2.161 | Primary | 1190
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - Leading the Way | 2.328 | 2.094 | 1.731 | 1.334 | 1.096 | 0.828 | 0.391 | -3.494 | -6.297 | -8.042 | -7.643 | Primary | 1191
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - Leading the Way | 2.274 | 2.087 | 1.846 | 1.639 | 1.513 | 1.382 | 1.18 | -0.349 | -1.454 | -2.164 | -2.032 | Primary | 1192
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - Leading the Way | 12.99 | 12.843 | 12.586 | 12.266 | 12.11 | 11.94 | 11.613 | 8.223 | 5.733 | 4.064 | 4.463 | Primary | 1193
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - Leading the Way | 7.908 | 7.95 | 7.975 | 8.002 | 8.038 | 8.068 | 8.073 | 6.703 | 5.626 | 4.815 | 5.279 | Primary | 1194
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - Leading the Way | 13.583 | 13.499 | 13.347 | 13.154 | 13.096 | 13.028 | 12.85 | 10.07 | 7.877 | 6.317 | 6.698 | Primary | 1195
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - Leading the Way | 7.128 | 6.739 | 6.194 | 5.566 | 5.04 | 4.486 | 3.735 | -1.667 | -5.638 | -8.5 | -8.926 | Primary | 1196
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - Leading the Way | 12.781 | 12.733 | 12.612 | 12.426 | 12.281 | 12.074 | 11.742 | 8.631 | 6.404 | 5.263 | 5.439 | Primary | 1197
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - Leading the Way | 13.777 | 13.82 | 13.857 | 13.889 | 13.923 | 13.955 | 13.98 | 13.825 | 13.7 | 13.61 | 13.748 | Primary | 1198
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - Leading the Way | 5.913 | 5.896 | 5.864 | 5.827 | 5.809 | 5.788 | 5.748 | 5.403 | 5.175 | 5.029 | 5.062 | Primary | 1199
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - Leading the Way | 14.203 | 14.23 | 14.233 | 14.22 | 14.227 | 14.229 | 14.207 | 12.926 | 11.923 | 11.183 | 11.536 | Primary | 1200
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - Leading the Way | -4.029 | -4.318 | -4.775 | -5.333 | -5.659 | -6.005 | -6.567 | -11.351 | -14.857 | -17.176 | -16.826 | Primary | 1201
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - Leading the Way | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 1202
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - Leading the Way | 8.957 | 7.842 | 7.183 | 6.416 | 5.894 | 5.351 | 4.506 | -2.694 | -8.244 | -12.296 | -12.121 | Primary | 1203
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - Leading the Way | 8.937 | 8.338 | 7.483 | 6.562 | 12.011 | 11.434 | 10.519 | 3.11 | -2.241 | -5.84 | -5.453 | Primary | 1204
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - Leading the Way | 4.048 | 4.123 | 4.17 | 4.189 | 4.209 | 4.22 | 4.163 | 2.283 | 0.697 | -0.542 | -0.143 | Primary | 1205
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - Leading the Way | 2.296 | 1.979 | 1.527 | 0.992 | 0.475 | -0.06 | -0.83 | -6.9 | -11.653 | -15.374 | -15.561 | Primary | 1206
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - Leading the Way | 14.388 | 14.197 | 13.905 | 13.572 | 13.337 | 13.091 | 12.679 | 8.839 | 5.857 | 3.665 | 3.898 | Primary | 1207
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - Leading the Way | 5.6 | 5.073 | 4.273 | 3.323 | 2.72 | 2.075 | 1.111 | -6.78 | -12.621 | -16.611 | -16.573 | Primary | 1208
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - Leading the Way | 5.187 | 4.19 | 3.819 | 3.425 | 3.173 | 2.885 | 2.378 | -2.239 | -5.707 | -8.048 | -7.684 | Primary | 1209
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - Leading the Way | 15.096 | 14.932 | 14.679 | 14.393 | 14.238 | 14.073 | 13.786 | 11.119 | 9.095 | 7.649 | 7.817 | Primary | 1210
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - Leading the Way | 4.171 | 3.871 | 3.405 | 2.858 | 2.516 | 2.144 | 1.545 | -3.777 | -7.655 | -10.235 | -9.94 | Primary | 1211
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - Leading the Way | 7.892 | 7.625 | 7.258 | 6.824 | 6.521 | 6.181 | 5.697 | 0.993 | -2.757 | -5.431 | -5.625 | Primary | 1212
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - Leading the Way | 8.919 | 8.449 | 7.777 | 7.016 | 6.529 | 6.017 | 5.258 | -0.602 | -4.742 | -7.377 | -7.052 | Primary | 1213
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - Leading the Way | 6.852 | 6.53 | 6.065 | 5.525 | 5.072 | 4.601 | 3.963 | -0.061 | -2.923 | -4.785 | -4.853 | Primary | 1214
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - Leading the Way | 2.334 | 1.61 | 0.703 | -0.099 | -0.715 | -1.359 | -2.405 | -10.975 | -17.299 | -21.681 | -21.004 | Primary | 1215
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - Leading the Way | 9.699 | 9.173 | 8.457 | 7.739 | 7.338 | 6.919 | 6.215 | 0.023 | -4.582 | -7.74 | -7.287 | Primary | 1216
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - Leading the Way | 10.623 | 10.113 | 9.423 | 8.731 | 8.212 | 7.637 | 6.774 | 0.134 | -4.618 | -7.597 | -7.357 | Primary | 1217
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - Leading the Way | 13.411 | 13.399 | 13.334 | 13.219 | 13.123 | 12.987 | 12.765 | 10.02 | 8.022 | 6.892 | 7.234 | Primary | 1218
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - Leading the Way | 8.819 | 8.697 | 8.503 | 8.276 | 8.118 | 7.951 | 7.669 | 4.876 | 2.816 | 1.355 | 1.572 | Primary | 1219
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - Leading the Way | 3.584 | 3.513 | 3.373 | 3.186 | 3.069 | 2.915 | 2.663 | 0.212 | -1.568 | -2.556 | -2.354 | Primary | 1220
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - Leading the Way | 12.908 | 12.684 | 12.327 | 11.903 | 11.641 | 11.365 | 10.91 | 6.83 | 3.785 | 1.645 | 1.934 | Primary | 1221
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - Leading the Way | 17.6 | 17.499 | 17.315 | 17.077 | 16.896 | 16.704 | 16.392 | 13.921 | 12.096 | 10.808 | 10.931 | Primary | 1222
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - Leading the Way | 15.454 | 15.34 | 15.165 | 14.952 | 14.858 | 14.758 | 14.568 | 12.085 | 9.992 | 8.397 | 8.479 | Primary | 1223
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - Leading the Way | 4.15 | 3.963 | 3.681 | 3.308 | 2.955 | 2.511 | 1.893 | -3.53 | -7.594 | -10.027 | -10.222 | Primary | 1224
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - Leading the Way | 10.148 | 10.183 | 10.186 | 10.163 | 10.169 | 10.159 | 10.104 | 8.331 | 6.948 | 5.99 | 6.409 | Primary | 1225
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - Leading the Way | -1.198 | -1.299 | -1.451 | -1.637 | -1.758 | -1.902 | -2.129 | -4.528 | -6.412 | -7.703 | -7.7 | Primary | 1226
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - Leading the Way | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary | 1227
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - Leading the Way | 6.782 | 6.269 | 5.579 | 4.867 | 4.415 | 3.924 | 3.181 | -2.839 | -7.122 | -9.928 | -9.739 | Primary | 1228
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - Leading the Way | 14.34 | 14.016 | 13.53 | 12.943 | 12.622 | 12.283 | 11.71 | 6.66 | 2.853 | 0.148 | 0.356 | Primary | 1229
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - Leading the Way | 3.463 | 3.319 | 3.117 | 2.889 | 2.728 | 2.56 | 2.32 | 0.255 | -1.327 | -2.525 | -2.598 | Primary | 1230
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - Leading the Way | 8.802 | 8.447 | 7.931 | 7.257 | 6.609 | 5.798 | 4.713 | -4.502 | -11.372 | -15.371 | -15.871 | Primary | 1231
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - Leading the Way | 13.065 | 12.57 | 11.945 | 11.364 | 10.968 | 10.553 | 9.924 | 4.534 | 0.627 | -2.093 | -1.85 | Primary | 1232
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - Leading the Way | 5.066 | 4.976 | 4.848 | 4.7 | 4.588 | 4.474 | 4.298 | 2.87 | 1.743 | 0.894 | 0.863 | Primary | 1233
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - Leading the Way | 6.741 | 6.302 | 5.674 | 4.948 | 4.451 | 3.934 | 3.169 | -3.822 | -9.288 | -13.441 | -13.475 | Primary | 1234
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - Leading the Way | 10.171 | 9.894 | 9.444 | 8.902 | 8.56 | 8.201 | 7.587 | 1.967 | -2.309 | -5.327 | -4.859 | Primary | 1235
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - Leading the Way | 14.854 | 14.519 | 14.076 | 13.64 | 13.32 | 12.99 | 12.483 | 8.608 | 5.67 | 3.575 | 3.759 | Primary | 1236
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - Leading the Way | 6.448 | 6.244 | 5.889 | 5.445 | 5.205 | 4.942 | 4.481 | -0.331 | -3.937 | -6.401 | -5.925 | Primary | 1237
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - Leading the Way | 14.02 | 13.636 | 13.12 | 12.534 | 11.983 | 11.391 | 10.602 | 4.662 | 0.141 | -3.15 | -3.618 | Primary | 1238
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - Leading the Way | 13.131 | 13.08 | 12.996 | 12.888 | 12.845 | 12.797 | 12.699 | 11.112 | 9.813 | 8.831 | 8.978 | Primary | 1239
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - Leading the Way | 9.277 | 8.933 | 8.435 | 7.874 | 7.49 | 7.069 | 6.464 | 1.878 | -1.456 | -3.575 | -3.598 | Primary | 1240
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - Leading the Way | 12.448 | 12.455 | 12.41 | 12.32 | 12.246 | 12.136 | 11.951 | 9.875 | 8.383 | 7.57 | 7.815 | Primary | 1241
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - Leading the Way | 6.949 | 6.868 | 6.694 | 6.451 | 6.307 | 6.114 | 5.779 | 2.005 | -0.776 | -2.429 | -2.046 | Primary | 1242
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - Leading the Way | 25.646 | 25.534 | 25.35 | 25.11 | 24.91 | 24.67 | 24.335 | 21.53 | 19.431 | 18.115 | 18.002 | Primary | 1243
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - Leading the Way | 4.553 | 4.352 | 4.095 | 3.796 | 3.578 | 3.344 | 2.982 | -0.842 | -4.264 | -7.135 | -7.757 | Primary | 1244
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - Leading the Way | 1.872 | 1.834 | 1.773 | 1.699 | 1.641 | 1.579 | 1.496 | 0.935 | 0.518 | 0.209 | 0.136 | Primary | 1245
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - Leading the Way | 12.504 | 12.206 | 11.797 | 11.341 | 11.033 | 10.706 | 10.229 | 5.837 | 2.448 | -0.049 | -0.077 | Primary | 1246
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - Leading the Way | 10.199 | 10.198 | 10.157 | 10.089 | 10.072 | 10.044 | 9.951 | 8.193 | 6.838 | 5.891 | 6.182 | Primary | 1247
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - Leading the Way | 10.31 | 10.221 | 10.034 | 9.776 | 9.651 | 9.514 | 9.16 | 3.673 | -0.951 | -4.579 | -4.059 | Primary | 1248
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - Leading the Way | 0.733 | 0.665 | 0.566 | 0.442 | 0.342 | 0.224 | 0.062 | -1.635 | -3.01 | -4.002 | -4.103 | Primary | 1249
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - Leading the Way | 9.425 | 9.406 | 9.305 | 9.11 | 8.836 | 8.447 | 7.897 | 2.736 | -0.929 | -2.73 | -2.457 | Primary | 1250
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - Leading the Way | 16.453 | 16.409 | 16.334 | 16.257 | 16.211 | 16.155 | 16.049 | 14.727 | 13.753 | 13.109 | 13.289 | Primary | 1251
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - Leading the Way | 8.979 | 7.819 | 7.27 | 6.633 | 6.157 | 5.658 | 4.932 | -1.541 | -6.625 | -10.461 | -10.626 | Primary | 1252
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - Leading the Way | 12.242 | 12.14 | 11.951 | 11.717 | 11.567 | 11.406 | 11.108 | 8.508 | 6.573 | 5.236 | 5.533 | Primary | 1253
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - Leading the Way | 18.115 | 18.143 | 18.064 | 17.87 | 17.585 | 17.162 | 16.554 | 11.739 | 8.567 | 7.418 | 7.683 | Primary | 1254
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - Leading the Way | 10.218 | 9.854 | 9.272 | 8.576 | 8.201 | 7.793 | 7.075 | 0.413 | -4.526 | -7.843 | -7.275 | Primary | 1255
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - Leading the Way | 4.306 | 4.248 | 4.16 | 4.056 | 3.985 | 3.91 | 3.796 | 2.884 | 2.195 | 1.695 | 1.664 | Primary | 1256
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - Leading the Way | 9.479 | 9.147 | 8.682 | 8.204 | 7.952 | 7.683 | 7.201 | 2.398 | -1.119 | -3.458 | -2.894 | Primary | 1257
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 15.296 | 15.139 | 14.888 | 14.573 | 14.367 | 14.133 | 13.775 | 9.685 | 6.319 | 3.761 | 3.654 | Primary | 1258
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - Leading the Way | 13.704 | 13.564 | 13.335 | 13.036 | 12.832 | 12.601 | 12.241 | 7.213 | 2.925 | -0.475 | -0.579 | Primary | 1259
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - Leading the Way | 13.404 | 13.405 | 13.372 | 13.318 | 13.291 | 13.249 | 13.161 | 11.479 | 10.244 | 9.456 | 9.831 | Primary | 1260
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - Leading the Way | 8.174 | 8.204 | 8.192 | 8.149 | 8.181 | 8.208 | 8.166 | 6.734 | 5.545 | 4.653 | 5.011 | Primary | 1261
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - Leading the Way | 17.586 | 17.456 | 17.25 | 17.004 | 16.851 | 16.687 | 16.438 | 14.473 | 13.055 | 12.151 | 12.271 | Primary | 1262
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - Leading the Way | 5.824 | 5.82 | 5.8 | 5.763 | 5.717 | 5.652 | 5.563 | 4.673 | 3.879 | 3.255 | 2.987 | Primary | 1263
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - Leading the Way | 2.195 | 1.709 | 1.056 | 0.413 | 0.03 | -0.372 | -1.042 | -6.968 | -11.356 | -14.359 | -13.864 | Primary | 1264
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - Leading the Way | 12.746 | 12.386 | 11.9 | 11.408 | 11.073 | 10.725 | 10.168 | 5.486 | 1.985 | -0.443 | -0.112 | Primary | 1265
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - Leading the Way | 10.023 | 9.507 | 8.772 | 7.98 | 7.479 | 6.922 | 6.043 | -1.236 | -6.46 | -9.636 | -9.093 | Primary | 1266
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - Leading the Way | 11.648 | 11.659 | 11.619 | 11.531 | 11.437 | 11.295 | 11.081 | 8.847 | 7.289 | 6.534 | 6.801 | Primary | 1267
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - Leading the Way | 16.046 | 15.833 | 15.494 | 15.085 | 14.845 | 14.593 | 14.176 | 10.782 | 8.341 | 6.725 | 6.986 | Primary | 1268
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - Leading the Way | 12.903 | 12.797 | 12.601 | 12.349 | 12.152 | 11.941 | 11.574 | 7.808 | 5.019 | 3.05 | 3.479 | Primary | 1269
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - Leading the Way | 9.423 | 9.162 | 8.739 | 8.229 | 7.894 | 7.516 | 6.921 | 1.762 | -1.951 | -4.285 | -3.93 | Primary | 1270
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - Leading the Way | 11.545 | 9.796 | 9.588 | 9.319 | 9.171 | 9.014 | 8.71 | 5.629 | 3.201 | 1.414 | 1.687 | Primary | 1271
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - Leading the Way | 5.212 | 5.125 | 5.001 | 4.866 | 4.757 | 4.642 | 4.48 | 3.249 | 2.347 | 1.705 | 1.698 | Primary | 1272
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - Leading the Way | 14.304 | 13.869 | 13.23 | 12.507 | 12.011 | 11.489 | 10.7 | 4.565 | 0.14 | -2.916 | -2.833 | Primary | 1273
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - Leading the Way | 3.151 | 2.817 | 2.267 | 1.607 | 1.141 | 0.649 | -0.179 | -7.521 | -13.09 | -17.045 | -16.465 | Primary | 1274
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - Leading the Way | 14.857 | 14.582 | 14.17 | 13.712 | 13.41 | 13.086 | 12.583 | 8.64 | 5.768 | 3.838 | 4 | Primary | 1275
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - Leading the Way | 7.105 | 6.638 | 5.952 | 5.187 | 4.727 | 4.241 | 3.469 | -3.63 | -8.977 | -12.788 | -12.432 | Primary | 1276
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - Leading the Way | 19.374 | 19.411 | 19.365 | 19.25 | 19.211 | 19.147 | 18.928 | 14.896 | 11.616 | 9.178 | 9.793 | Primary | 1277
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - Leading the Way | 12.578 | 12.435 | 12.221 | 11.98 | 11.784 | 11.57 | 11.266 | 8.873 | 7.18 | 6.133 | 6.346 | Primary | 1278
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - Leading the Way | 4.588 | 4.268 | 3.792 | 3.228 | 2.831 | 2.404 | 1.772 | -3.682 | -7.762 | -10.657 | -10.697 | Primary | 1279
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - Leading the Way | 8.803 | 8.085 | 7.127 | 6.051 | 5.007 | 3.912 | 2.45 | -7.001 | -14.063 | -19.133 | -19.964 | Primary | 1280
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - Leading the Way | 4.588 | 4.251 | 3.772 | 3.271 | 2.907 | 2.523 | 1.876 | -4.119 | -8.822 | -12.3 | -12.004 | Primary | 1281
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - Leading the Way | 12.965 | 12.476 | 11.799 | 11.033 | 10.538 | 10.027 | 9.277 | 3.595 | -0.695 | -3.77 | -3.909 | Primary | 1282
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - Leading the Way | 20.883 | 17.791 | 17.822 | 17.85 | 17.876 | 17.901 | 17.925 | 17.692 | 17.489 | 17.327 | 17.466 | Primary | 1283
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - Leading the Way | 3.483 | 3.244 | 2.902 | 2.477 | 2.086 | 1.603 | 0.968 | -4.462 | -8.626 | -11.172 | -11.635 | Primary | 1284
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - Leading the Way | 13.88 | 13.762 | 13.562 | 13.325 | 13.269 | 13.206 | 13.003 | 9.775 | 7.132 | 5.144 | 5.492 | Primary | 1285
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - Leading the Way | 14.305 | 14.363 | 14.402 | 14.433 | 14.487 | 14.537 | 14.566 | 14.265 | 14.026 | 13.869 | 14.1 | Primary | 1286
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - Leading the Way | 15.69 | 15.723 | 15.735 | 15.731 | 15.752 | 15.768 | 15.757 | 14.909 | 14.241 | 13.744 | 13.993 | Primary | 1287
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - Leading the Way | 9.648 | 9.097 | 8.285 | 7.337 | 6.702 | 6.035 | 5.052 | -2.199 | -7.546 | -11.194 | -11.181 | Primary | 1288
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - Leading the Way | 14.757 | 14.647 | 14.481 | 14.276 | 14.18 | 14.071 | 13.864 | 10.879 | 8.359 | 6.392 | 6.431 | Primary | 1289
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - Leading the Way | 6.036 | 5.948 | 5.776 | 5.551 | 5.471 | 5.38 | 5.152 | 1.272 | -1.834 | -4.132 | -3.598 | Primary | 1290
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - Leading the Way | 14.014 | 13.832 | 13.542 | 13.199 | 12.956 | 12.695 | 12.303 | 8.876 | 6.418 | 4.789 | 5.041 | Primary | 1291
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - Leading the Way | 17.538 | 13.977 | 13.926 | 13.867 | 13.827 | 13.781 | 13.703 | 13.171 | 12.836 | 12.67 | 12.788 | Primary | 1292
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - Leading the Way | 10.957 | 10.7 | 10.339 | 9.941 | 9.681 | 9.403 | 8.992 | 5.702 | 3.232 | 1.532 | 1.483 | Primary | 1293
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - Leading the Way | 2.701 | 2.494 | 2.191 | 1.827 | 1.546 | 1.224 | 0.773 | -2.666 | -5.178 | -6.689 | -6.753 | Primary | 1294
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - Leading the Way | 11.155 | 10.787 | 10.26 | 9.696 | 9.369 | 9.025 | 8.489 | 4.419 | 1.47 | -0.496 | -0.321 | Primary | 1295
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - Leading the Way | 12.612 | 12.401 | 12.064 | 11.665 | 11.433 | 11.184 | 10.767 | 7.044 | 4.319 | 2.489 | 2.781 | Primary | 1296
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - Leading the Way | 5.593 | 5.406 | 5.125 | 4.753 | 4.406 | 3.987 | 3.376 | -2.553 | -7.303 | -10.581 | -10.907 | Primary | 1297
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - Leading the Way | 16.529 | 16.386 | 16.182 | 15.941 | 15.747 | 15.542 | 15.248 | 12.918 | 11.085 | 9.715 | 9.561 | Primary | 1298
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - Leading the Way | 11.713 | 9.916 | 9.556 | 9.105 | 8.771 | 8.379 | 7.759 | 1.67 | -3.2 | -6.561 | -6.699 | Primary | 1299
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - Leading the Way | 4.704 | 4.585 | 4.42 | 4.23 | 4.083 | 3.93 | 3.722 | 2.203 | 1.091 | 0.288 | 0.206 | Primary | 1300
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - Leading the Way | 14.814 | 14.532 | 14.098 | 13.583 | 13.231 | 12.861 | 12.317 | 8.243 | 5.374 | 3.547 | 3.79 | Primary | 1301
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - Leading the Way | 0.032 | -0.15 | -0.408 | -0.705 | -0.952 | -1.217 | -1.6 | -4.96 | -7.514 | -9.353 | -9.368 | Primary | 1302
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - Leading the Way | 9.327 | 8.98 | 8.473 | 7.886 | 7.459 | 7.007 | 6.344 | 0.545 | -3.99 | -7.35 | -7.427 | Primary | 1303
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - Leading the Way | 8.442 | 8.14 | 7.657 | 7.078 | 6.714 | 6.321 | 5.686 | -0.113 | -4.327 | -7.174 | -6.754 | Primary | 1304
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - Leading the Way | 5.55 | 5.096 | 4.443 | 3.685 | 3.154 | 2.593 | 1.782 | -5.981 | -12.057 | -16.667 | -16.777 | Primary | 1305
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - Leading the Way | 16.065 | 15.766 | 15.309 | 14.772 | 14.402 | 14 | 13.403 | 8.402 | 4.901 | 2.65 | 2.935 | Primary | 1306
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - Leading the Way | 8.272 | 8.302 | 8.281 | 8.22 | 8.209 | 8.176 | 8.072 | 5.968 | 4.355 | 3.309 | 3.768 | Primary | 1307
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - Leading the Way | 16.418 | 17.201 | 16.902 | 8.36 | 8.064 | 7.757 | 7.294 | 3.369 | 0.239 | -2.216 | -2.315 | Primary | 1308
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - Leading the Way | 10.992 | 10.541 | 9.897 | 9.142 | 8.543 | 7.912 | 7.021 | 0.507 | -4.345 | -7.702 | -7.878 | Primary | 1309
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - Leading the Way | 8.804 | 8.805 | 8.766 | 8.698 | 8.687 | 8.667 | 8.584 | 6.707 | 5.218 | 4.132 | 4.462 | Primary | 1310
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - Leading the Way | 10.821 | 10.374 | 9.711 | 8.944 | 8.462 | 7.958 | 7.171 | 0.847 | -3.69 | -6.775 | -6.434 | Primary | 1311
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - Leading the Way | 5.074 | 4.531 | 3.78 | 2.89 | 2.141 | 1.32 | 0.222 | -8.885 | -15.951 | -21.104 | -21.974 | Primary | 1312
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - Leading the Way | 13.01 | 13.077 | 13.139 | 13.196 | 13.249 | 13.3 | 13.348 | 13.287 | 13.232 | 13.196 | 13.386 | Primary | 1313
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - Leading the Way | 13.755 | 13.835 | 13.894 | 13.927 | 13.938 | 13.921 | 13.874 | 12.995 | 12.421 | 12.215 | 12.469 | Primary | 1314
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - Leading the Way | 2.768 | 2.849 | 2.918 | 2.979 | 3.038 | 3.092 | 3.134 | 2.888 | 2.707 | 2.61 | 2.88 | Primary | 1315
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - Leading the Way | 6.36 | 6.206 | 5.981 | 5.745 | 5.602 | 5.448 | 5.195 | 2.822 | 1.147 | 0.099 | 0.452 | Primary | 1316
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - Leading the Way | 1.873 | 1.717 | 1.509 | 1.282 | 1.087 | 0.879 | 0.595 | -1.408 | -2.89 | -3.906 | -4.03 | Primary | 1317
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - Leading the Way | 12.653 | 12.387 | 11.991 | 11.518 | 11.151 | 10.75 | 10.184 | 5.559 | 2.219 | 0.101 | 0.379 | Primary | 1318
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - Leading the Way | 12.617 | 10.626 | 10.616 | 10.589 | 10.557 | 10.511 | 10.427 | 8.698 | 7.353 | 6.421 | 6.719 | Primary | 1319
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - Leading the Way | 9.207 | 8.84 | 15.338 | 14.837 | 14.5 | 14.143 | 13.573 | 8.832 | 5.358 | 2.957 | 3.248 | Primary | 1320
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - Leading the Way | 11.486 | 11.365 | 11.186 | 10.959 | 10.816 | 10.644 | 10.359 | 7.071 | 4.337 | 2.332 | 2.214 | Primary | 1321
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - Leading the Way | 3.164 | 1.514 | 0.965 | 0.529 | 0.231 | -0.089 | -0.653 | -6.273 | -10.722 | -14.006 | -13.65 | Primary | 1322
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - Leading the Way | 12.955 | 12.93 | 12.881 | 12.815 | 12.793 | 12.766 | 12.703 | 11.595 | 10.619 | 9.808 | 9.782 | Primary | 1323
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - Leading the Way | 8.531 | 8.369 | 15.07 | 14.696 | 14.515 | 14.314 | 13.926 | 9.606 | 6.386 | 4.227 | 4.783 | Primary | 1324
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - Leading the Way | 5.203 | 3.983 | 3.351 | 2.833 | 2.424 | 1.975 | 1.327 | -4.333 | -8.661 | -11.708 | -11.721 | Primary | 1325
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - Leading the Way | 10.195 | 9.73 | 9.025 | 8.202 | 7.741 | 7.259 | 6.461 | -0.263 | -5.271 | -8.724 | -8.335 | Primary | 1326
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - Leading the Way | 12.809 | 12.655 | 10.324 | 9.99 | 9.658 | 9.227 | 8.644 | 4.073 | 0.766 | -0.96 | -1.227 | Primary | 1327
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - Leading the Way | 9.472 | 9.057 | 8.456 | 7.761 | 7.282 | 6.766 | 6.019 | 0.517 | -3.438 | -6.056 | -6.119 | Primary | 1328
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - Leading the Way | 7.805 | 5.838 | 5.361 | 4.846 | 4.528 | 4.187 | 3.613 | -1.728 | -5.811 | -8.668 | -8.319 | Primary | 1329
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - Leading the Way | 8.554 | 7.862 | 7.903 | 7.903 | 7.877 | 7.816 | 7.71 | 5.437 | 3.74 | 2.728 | 3.188 | Primary | 1330
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - Leading the Way | 18.874 | 18.834 | 18.751 | 18.622 | 18.467 | 18.257 | 17.975 | 15.527 | 13.825 | 13.028 | 13.109 | Primary | 1331
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - Leading the Way | 8.644 | 8.525 | 8.288 | 7.986 | 7.837 | 7.676 | 7.347 | 4.01 | 1.429 | -0.428 | -0.076 | Primary | 1332
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - Leading the Way | 10.536 | 10.344 | 10.054 | 9.709 | 9.387 | 9.038 | 8.524 | 4.374 | 1.273 | -0.906 | -0.814 | Primary | 1333
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - Leading the Way | 12.44 | 12.194 | 11.805 | 11.336 | 11.072 | 10.795 | 10.328 | 5.455 | 1.798 | -0.784 | -0.332 | Primary | 1334
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - Leading the Way | 12.364 | 12.337 | 12.259 | 12.149 | 12.111 | 12.056 | 11.931 | 9.999 | 8.498 | 7.512 | 7.825 | Primary | 1335
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - Leading the Way | 8.409 | 8.531 | 8.639 | 8.753 | 8.865 | 8.968 | 9.051 | 8.701 | 8.431 | 8.25 | 8.692 | Primary | 1336
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - Leading the Way | 8.261 | 6.391 | 6.202 | 5.968 | 5.898 | 5.801 | 5.54 | 2.033 | -0.711 | -2.556 | -2.09 | Primary | 1337
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - Leading the Way | 10.385 | 9.206 | 9.269 | 9.316 | 9.369 | 9.417 | 9.445 | 8.58 | 7.909 | 7.415 | 7.814 | Primary | 1338
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - Leading the Way | 1.705 | 1.522 | 1.268 | 0.978 | 0.764 | 0.539 | 0.216 | -2.568 | -4.698 | -6.303 | -6.431 | Primary | 1339
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - Leading the Way | 3.43 | 3.39 | 3.326 | 3.258 | 3.248 | 3.236 | 3.189 | 2.269 | 1.503 | 0.928 | 1.041 | Primary | 1340
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - Leading the Way | 13.861 | 13.765 | 13.604 | 13.389 | 13.2 | 12.963 | 12.637 | 9.802 | 7.686 | 6.447 | 6.388 | Primary | 1341
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - Leading the Way | 24.617 | 24.645 | 24.669 | 24.685 | 24.697 | 24.707 | 24.715 | 24.103 | 23.504 | 22.95 | 22.979 | Primary | 1342
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - Leading the Way | 14.971 | 14.995 | 14.988 | 14.961 | 14.968 | 14.971 | 14.93 | 13.981 | 13.203 | 12.615 | 12.855 | Primary | 1343
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - Leading the Way | -0.825 | -0.936 | -1.1 | -1.302 | -1.464 | -1.647 | -1.902 | -4.41 | -6.517 | -8.146 | -8.472 | Primary | 1344
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - Leading the Way | 3.728 | 3.46 | 3.073 | 2.575 | 2.122 | 1.567 | 0.809 | -6.654 | -12.521 | -16.457 | -16.884 | Primary | 1345
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - Leading the Way | 11.093 | 10.912 | 10.595 | 10.204 | 9.976 | 9.734 | 9.315 | 5.454 | 2.565 | 0.569 | 0.962 | Primary | 1346
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - Leading the Way | 11.73 | 11.834 | 11.92 | 11.988 | 12.038 | 12.067 | 12.073 | 11.723 | 11.542 | 11.574 | 11.835 | Primary | 1347
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - Leading the Way | 8.617 | 8.216 | 7.611 | 6.893 | 6.392 | 5.845 | 5.006 | -2.257 | -7.753 | -11.514 | -11.336 | Primary | 1348
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - Leading the Way | 17.103 | 16.427 | 16.343 | 16.242 | 16.187 | 16.129 | 16.018 | 14.358 | 12.903 | 11.685 | 11.685 | Primary | 1349
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - Leading the Way | 4.951 | 4.652 | 4.254 | 3.865 | 3.571 | 3.268 | 2.788 | -0.932 | -3.789 | -5.854 | -5.691 | Primary | 1350
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - Leading the Way | 8.605 | 8.377 | 7.97 | 7.447 | 7.093 | 6.72 | 6.068 | 0.075 | -4.59 | -8.043 | -7.741 | Primary | 1351
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - Leading the Way | -1.167 | -1.371 | -1.67 | -2.012 | -2.227 | -2.452 | -2.824 | -6.498 | -9.352 | -11.451 | -11.259 | Primary | 1352
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - Leading the Way | 15.39 | 15.328 | 15.225 | 15.081 | 14.935 | 14.756 | 14.503 | 11.599 | 9.281 | 7.673 | 7.675 | Primary | 1353
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - Leading the Way | 15.823 | 15.266 | 14.664 | 14.266 | 13.949 | 13.608 | 13.094 | 8.819 | 5.638 | 3.468 | 3.632 | Primary | 1354
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - Leading the Way | 10.786 | 10.417 | 9.845 | 9.173 | 8.783 | 8.367 | 7.721 | 2.514 | -1.238 | -3.698 | -3.448 | Primary | 1355
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - Leading the Way | 24.274 | 24.316 | 24.353 | 24.392 | 24.431 | 24.467 | 24.495 | 24.297 | 24.136 | 24.017 | 24.184 | Primary | 1356
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - Leading the Way | 8.485 | 8.507 | 8.523 | 8.543 | 8.562 | 8.579 | 8.586 | 7.543 | 6.68 | 5.998 | 6.3 | Primary | 1357
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - Leading the Way | 11.275 | 10.974 | 10.493 | 9.913 | 9.585 | 9.241 | 8.68 | 3.999 | 0.542 | -1.847 | -1.591 | Primary | 1358
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - Leading the Way | -0.701 | -0.725 | -0.768 | -0.825 | -0.846 | -0.872 | -0.928 | -1.664 | -2.341 | -2.91 | -3.024 | Primary | 1359
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - Leading the Way | 9.307 | 9.199 | 9.044 | 8.856 | 8.731 | 8.592 | 8.388 | 6.059 | 4.067 | 2.478 | 2.293 | Primary | 1360
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - Leading the Way | 13.427 | 13.133 | 12.676 | 12.141 | 11.826 | 11.494 | 10.927 | 5.963 | 2.16 | -0.599 | -0.413 | Primary | 1361
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - Leading the Way | 11.6 | 11.35 | 11.001 | 10.602 | 10.32 | 10.022 | 9.578 | 5.802 | 2.887 | 0.852 | 0.874 | Primary | 1362
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - Leading the Way | 8.368 | 8.035 | 7.544 | 6.957 | 6.443 | 5.893 | 5.138 | -0.276 | -4.311 | -7.118 | -7.33 | Primary | 1363
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - Leading the Way | 13.55 | 13.327 | 13.044 | 12.713 | 12.408 | 12.065 | 11.615 | 7.461 | 3.964 | 1.282 | 0.627 | Primary | 1364
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - Leading the Way | 7.698 | 7.656 | 7.524 | 7.316 | 7.166 | 6.971 | 6.585 | 1.858 | -1.868 | -4.413 | -3.954 | Primary | 1365
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - Leading the Way | 14.056 | 13.801 | 13.403 | 12.934 | 12.672 | 12.395 | 11.941 | 8.036 | 5.124 | 3.113 | 3.323 | Primary | 1366
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - Leading the Way | 7.429 | 7.03 | 6.486 | 5.944 | 5.579 | 5.193 | 4.552 | -1.37 | -5.905 | -9.193 | -8.837 | Primary | 1367
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - Leading the Way | 8.092 | 7.922 | 7.687 | 7.403 | 7.198 | 6.967 | 6.645 | 2.508 | -0.983 | -3.747 | -3.993 | Primary | 1368
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NG FES - System Transformation | 12.919 | 12.626 | 12.418 | 12.358 | 12.3 | 12.235 | 12.163 | 11.724 | 10.841 | 9.474 | 7.38 | Primary | 1369
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NG FES - System Transformation | 12.526 | 10.88 | 10.814 | 10.714 | 10.603 | 10.458 | 10.273 | 8.895 | 6.763 | 4.868 | 2.544 | Primary | 1370
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NG FES - System Transformation | 11.443 | 11.174 | 10.839 | 10.442 | 9.958 | 9.449 | 8.917 | 6.243 | 3.149 | -0.322 | -4.708 | Primary | 1371
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NG FES - System Transformation | 5.854 | 4.434 | 4.434 | 4.408 | 4.365 | 4.303 | 4.209 | 3.546 | 1.559 | -0.063 | -1.817 | Primary | 1372
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 5.271 | 4.944 | 4.592 | 4.27 | 3.953 | 3.63 | 3.298 | 1.778 | 0.063 | -2.023 | -5.111 | Primary | 1373
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NG FES - System Transformation | 5.317 | 5.304 | 5.283 | 5.261 | 5.236 | 5.205 | 5.171 | 4.971 | 4.64 | 4.224 | 3.622 | Primary | 1374
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NG FES - System Transformation | 9.889 | 9.42 | 8.858 | 8.247 | 7.639 | 7.01 | 6.354 | 3.177 | -0.121 | -4.136 | -9.653 | Primary | 1375
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NG FES - System Transformation | 17.073 | 17.084 | 17.081 | 17.069 | 17.058 | 17.041 | 17.011 | 16.828 | 15.741 | 14.616 | 13.172 | Primary | 1376
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NG FES - System Transformation | 1.322 | 1.119 | 0.86 | 0.558 | 0.233 | -0.11 | -0.471 | -2.279 | -5.075 | -8.114 | -12.105 | Primary | 1377
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NG FES - System Transformation | 2.868 | 2.298 | 2.375 | 2.433 | 2.481 | 2.516 | 2.534 | 2.504 | 1.71 | 0.911 | -0.062 | Primary | 1378
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NG FES - System Transformation | 12.037 | 11.828 | 11.546 | 11.219 | 10.895 | 10.557 | 10.197 | 8.474 | 6.332 | 3.953 | 0.72 | Primary | 1379
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NG FES - System Transformation | 2.436 | 2.127 | 1.8 | 1.495 | 1.157 | 0.782 | 0.354 | -1.934 | -5.114 | -7.856 | -10.974 | Primary | 1380
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NG FES - System Transformation | 3.064 | 3.048 | 3.026 | 2.998 | 2.966 | 2.93 | 2.889 | 2.648 | 2.278 | 1.941 | 1.591 | Primary | 1381
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NG FES - System Transformation | 15.736 | 15.563 | 15.328 | 15.064 | 14.823 | 14.574 | 14.309 | 13.058 | 11.166 | 8.899 | 5.61 | Primary | 1382
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NG FES - System Transformation | 12.878 | 12.387 | 12.339 | 12.28 | 12.226 | 12.165 | 12.096 | 11.695 | 10.917 | 10.004 | 8.841 | Primary | 1383
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NG FES - System Transformation | 10.508 | 10.502 | 10.469 | 10.412 | 10.346 | 10.264 | 10.158 | 9.515 | 7.87 | 6.37 | 4.639 | Primary | 1384
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NG FES - System Transformation | 15.476 | 15.17 | 14.773 | 14.324 | 13.851 | 13.354 | 12.831 | 10.215 | 7.723 | 5.019 | 1.43 | Primary | 1385
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NG FES - System Transformation | 8.41 | 8.421 | 8.415 | 8.394 | 8.367 | 8.328 | 8.275 | 7.858 | 6.809 | 5.791 | 4.502 | Primary | 1386
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NG FES - System Transformation | 6.55 | 6.411 | 6.237 | 6.031 | 5.818 | 5.592 | 5.346 | 3.992 | 1.364 | -1.661 | -5.607 | Primary | 1387
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NG FES - System Transformation | 21.762 | 21.707 | 21.61 | 21.483 | 21.359 | 21.229 | 21.091 | 20.428 | 19.611 | 18.616 | 17.147 | Primary | 1388
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NG FES - System Transformation | 3.724 | 3.576 | 3.409 | 3.233 | 3.069 | 2.898 | 2.716 | 1.726 | 0.18 | -1.638 | -4.03 | Primary | 1389
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NG FES - System Transformation | 11.325 | 10.874 | 10.314 | 9.686 | 9.042 | 8.363 | 7.634 | 3.868 | -0.175 | -4.711 | -10.734 | Primary | 1390
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NG FES - System Transformation | 9.445 | 9.075 | 8.644 | 8.21 | 7.786 | 7.344 | 6.88 | 4.638 | 1.852 | -1.215 | -5.536 | Primary | 1391
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NG FES - System Transformation | 14.761 | 14.522 | 14.239 | 13.959 | 13.655 | 13.342 | 13.021 | 11.55 | 10.3 | 8.727 | 6.46 | Primary | 1392
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NG FES - System Transformation | 2.384 | 2.339 | 2.225 | 2.059 | 1.884 | 1.67 | 1.409 | -0.268 | -2.905 | -5.644 | -9.272 | Primary | 1393
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NG FES - System Transformation | 5.806 | 5.589 | 5.315 | 5.001 | 4.68 | 4.338 | 3.972 | 2.067 | -0.006 | -2.034 | -4.468 | Primary | 1394
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 15.106 | 15.081 | 15.05 | 15.012 | 14.969 | 14.917 | 14.853 | 14.461 | 13.465 | 12.448 | 11.166 | Primary | 1395
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NG FES - System Transformation | 4.166 | 1.08 | 1.034 | 0.953 | 0.835 | 0.674 | 0.462 | -1.091 | -4.423 | -7.472 | -11.093 | Primary | 1396
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NG FES - System Transformation | 8.152 | 8.04 | 7.872 | 7.656 | 7.415 | 7.134 | 6.805 | 4.761 | 1.728 | -1.107 | -4.498 | Primary | 1397
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NG FES - System Transformation | 11.657 | 11.372 | 10.995 | 10.561 | 10.15 | 9.723 | 9.277 | 7.08 | 4.251 | 0.669 | -4.691 | Primary | 1398
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NG FES - System Transformation | 6.001 | 5.554 | 4.97 | 4.305 | 3.652 | 2.962 | 2.225 | -1.573 | -6.436 | -11.474 | -18.24 | Primary | 1399
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NG FES - System Transformation | 6.832 | 6.812 | 6.789 | 6.762 | 6.735 | 6.709 | 6.679 | 6.535 | 6.226 | 5.912 | 5.544 | Primary | 1400
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NG FES - System Transformation | 4.307 | 4.267 | 4.218 | 4.162 | 4.1 | 4.032 | 3.957 | 3.548 | 2.943 | 2.407 | 1.819 | Primary | 1401
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NG FES - System Transformation | 13.647 | 13.359 | 12.991 | 12.577 | 12.181 | 11.77 | 11.334 | 9.222 | 6.796 | 3.893 | -0.272 | Primary | 1402
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 13.864 | 13.732 | 13.596 | 13.45 | 13.297 | 13.141 | 12.975 | 12.094 | 10.51 | 8.913 | 7.244 | Primary | 1403
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NG FES - System Transformation | 5.517 | 5.439 | 5.342 | 5.234 | 5.128 | 5.02 | 4.907 | 4.376 | 3.838 | 3.268 | 2.515 | Primary | 1404
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NG FES - System Transformation | 10.473 | 10.181 | 9.799 | 9.372 | 8.963 | 8.535 | 8.078 | 5.864 | 2.945 | -0.328 | -4.944 | Primary | 1405
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NG FES - System Transformation | 11.456 | 11.171 | 10.796 | 10.375 | 9.96 | 9.52 | 9.052 | 6.711 | 3.705 | 0.701 | -3.372 | Primary | 1406
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NG FES - System Transformation | 9.209 | 9.221 | 9.207 | 9.173 | 9.138 | 9.087 | 9.012 | 8.455 | 7.15 | 5.699 | 3.737 | Primary | 1407
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NG FES - System Transformation | 10.282 | 10.25 | 10.181 | 10.088 | 9.99 | 9.88 | 9.75 | 9.077 | 7.958 | 7.021 | 5.923 | Primary | 1408
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NG FES - System Transformation | 17.389 | 17.222 | 17.015 | 16.78 | 16.534 | 16.272 | 15.991 | 14.546 | 13.226 | 11.973 | 10.455 | Primary | 1409
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NG FES - System Transformation | 7.845 | 22.353 | 22.113 | 21.85 | 21.589 | 21.316 | 21.03 | 19.626 | 17.38 | 14.924 | 11.516 | Primary | 1410
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NG FES - System Transformation | 10.63 | 10.19 | 9.62 | 8.971 | 8.341 | 7.699 | 7.042 | 3.964 | -0.055 | -4.728 | -11.289 | Primary | 1411
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NG FES - System Transformation | 3.804 | 3.697 | 3.576 | 3.464 | 3.352 | 3.237 | 3.117 | 2.591 | 2.095 | 1.482 | 0.587 | Primary | 1412
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NG FES - System Transformation | 6.074 | 5.439 | 4.761 | 4.117 | 3.439 | 2.729 | 1.994 | -1.617 | -4.933 | -8.804 | -14.174 | Primary | 1413
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NG FES - System Transformation | 4.504 | 4.083 | 3.551 | 2.932 | 2.237 | 1.501 | 0.721 | -3.195 | -8.873 | -14.33 | -20.968 | Primary | 1414
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NG FES - System Transformation | 5.829 | 5.265 | 4.544 | 3.725 | 2.921 | 2.093 | 1.233 | -2.937 | -8.298 | -14.253 | -22.334 | Primary | 1415
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NG FES - System Transformation | 4.271 | 4.311 | 4.342 | 4.364 | 4.379 | 4.386 | 4.384 | 4.28 | 3.935 | 3.662 | 3.399 | Primary | 1416
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NG FES - System Transformation | 7.758 | 7.33 | 6.745 | 6.052 | 5.339 | 4.563 | 3.716 | -0.91 | -6.058 | -10.95 | -17.216 | Primary | 1417
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NG FES - System Transformation | 12.973 | 13.032 | 13.079 | 13.112 | 13.134 | 13.144 | 13.139 | 13.012 | 12.125 | 11.42 | 10.737 | Primary | 1418
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NG FES - System Transformation | 10.222 | 10.314 | 10.396 | 10.468 | 10.532 | 10.588 | 10.635 | 10.783 | 10.605 | 10.439 | 10.277 | Primary | 1419
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NG FES - System Transformation | 10.905 | 10.939 | 10.967 | 11.004 | 11.027 | 11.033 | 11.011 | 10.754 | 9.048 | 7.41 | 5.456 | Primary | 1420
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NG FES - System Transformation | 11.678 | 11.71 | 11.729 | 11.74 | 11.744 | 11.74 | 11.724 | 11.6 | 11.012 | 10.482 | 9.883 | Primary | 1421
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NG FES - System Transformation | 10.802 | 10.53 | 10.171 | 9.765 | 9.348 | 8.894 | 8.395 | 5.701 | 3.002 | 0.385 | -3.041 | Primary | 1422
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NG FES - System Transformation | 4.251 | 4.157 | 4.035 | 3.898 | 3.753 | 3.603 | 3.449 | 2.757 | 2.247 | 1.9 | 1.621 | Primary | 1423
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NG FES - System Transformation | 5.128 | 5.051 | 4.953 | 4.841 | 4.714 | 4.577 | 4.427 | 3.603 | 2.581 | 1.518 | 0.401 | Primary | 1424
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NG FES - System Transformation | 13.595 | 13.12 | 12.599 | 12.108 | 11.624 | 11.122 | 10.597 | 8.077 | 4.954 | 1.571 | -3.162 | Primary | 1425
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NG FES - System Transformation | -0.039 | -0.059 | -0.088 | -0.126 | -0.17 | -0.22 | -0.277 | -0.612 | -1.11 | -1.567 | -2.031 | Primary | 1426
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NG FES - System Transformation | 3.256 | 3.057 | 2.825 | 2.575 | 2.32 | 2.056 | 1.78 | 0.497 | -0.84 | -2.208 | -3.886 | Primary | 1427
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NG FES - System Transformation | 9.467 | 9.305 | 9.064 | 8.764 | 8.424 | 8.052 | 7.643 | 5.468 | 3.385 | 0.996 | -2.234 | Primary | 1428
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NG FES - System Transformation | 9.075 | 8.914 | 8.751 | 8.622 | 8.491 | 8.348 | 8.182 | 7.334 | 5.532 | 3.757 | 1.476 | Primary | 1429
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NG FES - System Transformation | 5.259 | 4.953 | 4.592 | 4.203 | 3.819 | 3.418 | 2.987 | 0.802 | -2.254 | -5.512 | -9.706 | Primary | 1430
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NG FES - System Transformation | 4.778 | 4.793 | 4.803 | 4.808 | 4.809 | 4.805 | 4.796 | 4.695 | 4.451 | 4.242 | 4.003 | Primary | 1431
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NG FES - System Transformation | 21.888 | 21.697 | 21.477 | 21.26 | 21.061 | 20.853 | 20.633 | 19.576 | 17.908 | 15.904 | 13.009 | Primary | 1432
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NG FES - System Transformation | 7.843 | 7.857 | 7.863 | 7.87 | 7.876 | 7.872 | 7.85 | 7.664 | 6.604 | 5.548 | 4.228 | Primary | 1433
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NG FES - System Transformation | 13.373 | 13.017 | 12.65 | 12.331 | 12.014 | 11.685 | 11.341 | 9.732 | 7.72 | 5.455 | 2.237 | Primary | 1434
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NG FES - System Transformation | 7.189 | 7.13 | 7.014 | 6.857 | 6.697 | 6.517 | 6.307 | 5.164 | 2.845 | 0.681 | -2.079 | Primary | 1435
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NG FES - System Transformation | 4.53 | 3.859 | 3.076 | 2.293 | 1.56 | 0.8 | 0.001 | -3.796 | -8.111 | -13.113 | -20.361 | Primary | 1436
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NG FES - System Transformation | 0.94 | 0.897 | 0.848 | 0.794 | 0.736 | 0.674 | 0.606 | 0.24 | -0.42 | -1.026 | -1.686 | Primary | 1437
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NG FES - System Transformation | 3.083 | 2.934 | 2.752 | 2.538 | 2.303 | 2.041 | 1.745 | 0.016 | -2.57 | -4.842 | -7.201 | Primary | 1438
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NG FES - System Transformation | 12.929 | 12.859 | 12.742 | 12.59 | 12.434 | 12.267 | 12.089 | 11.235 | 9.979 | 8.667 | 6.898 | Primary | 1439
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NG FES - System Transformation | 14.736 | 14.547 | 15.274 | 14.947 | 14.63 | 14.301 | 13.953 | 12.275 | 10.011 | 7.39 | 3.569 | Primary | 1440
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NG FES - System Transformation | 22.244 | 22.213 | 22.118 | 21.95 | 21.729 | 21.432 | 21.045 | 18.193 | 13.49 | 10.19 | 7.002 | Primary | 1441
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NG FES - System Transformation | 9.687 | 9.38 | 9.001 | 8.575 | 8.135 | 7.675 | 7.19 | 4.757 | 1.559 | -1.89 | -6.33 | Primary | 1442
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NG FES - System Transformation | 2.34 | 2.118 | 1.867 | 1.59 | 1.31 | 1.018 | 0.707 | -0.833 | -2.452 | -4.31 | -6.847 | Primary | 1443
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NG FES - System Transformation | 7.943 | 7.603 | 7.111 | 6.534 | 6.004 | 5.459 | 4.889 | 2.149 | -1.488 | -6.402 | -14.016 | Primary | 1444
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NG FES - System Transformation | 6.058 | 3.758 | 3.739 | 3.706 | 3.662 | 3.607 | 3.538 | 3.065 | 2.042 | 1.077 | -0.114 | Primary | 1445
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NG FES - System Transformation | 7.315 | 6.85 | 6.262 | 5.618 | 4.988 | 4.339 | 3.656 | 0.469 | -3.047 | -6.948 | -12.483 | Primary | 1446
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NG FES - System Transformation | 3.826 | 3.549 | 17.887 | 17.48 | 17.065 | 16.627 | 16.161 | 13.792 | 10.451 | 6.952 | 2.196 | Primary | 1447
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NG FES - System Transformation | -0.217 | -0.369 | -0.56 | -0.775 | -0.985 | -1.201 | -1.426 | -2.502 | -4.118 | -5.815 | -8.027 | Primary | 1448
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NG FES - System Transformation | 2.818 | 2.819 | 2.809 | 2.788 | 2.765 | 2.736 | 2.696 | 2.433 | 1.789 | 1.199 | 0.508 | Primary | 1449
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NG FES - System Transformation | 10.303 | 10.026 | 9.64 | 9.191 | 8.738 | 8.27 | 7.788 | 5.551 | 3.014 | -0.149 | -4.781 | Primary | 1450
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NG FES - System Transformation | 8.375 | 8.062 | 7.649 | 7.186 | 6.735 | 6.259 | 5.745 | 3.161 | 0.147 | -3.351 | -8.354 | Primary | 1451
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NG FES - System Transformation | 12.365 | 12.237 | 12.062 | 11.857 | 11.64 | 11.406 | 11.152 | 9.83 | 8.413 | 6.997 | 5.257 | Primary | 1452
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NG FES - System Transformation | 3.706 | 2.727 | 2.712 | 2.661 | 2.598 | 2.505 | 2.377 | 1.402 | -0.628 | -2.573 | -5.039 | Primary | 1453
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NG FES - System Transformation | 15.204 | 15.102 | 14.978 | 14.828 | 14.658 | 14.464 | 14.237 | 12.846 | 10.584 | 8.657 | 6.677 | Primary | 1454
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NG FES - System Transformation | 4.047 | 3.948 | 3.822 | 3.681 | 3.539 | 3.393 | 3.24 | 2.506 | 1.546 | 0.435 | -1.071 | Primary | 1455
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NG FES - System Transformation | 2.427 | 2.359 | 2.268 | 2.165 | 2.066 | 1.963 | 1.855 | 1.338 | 0.557 | -0.332 | -1.589 | Primary | 1456
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NG FES - System Transformation | 14.826 | 14.465 | 14.008 | 13.491 | 12.988 | 12.452 | 11.871 | 8.817 | 4.892 | 0.868 | -4.416 | Primary | 1457
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NG FES - System Transformation | 1.841 | 1.669 | 1.411 | 1.092 | 0.746 | 0.373 | -0.036 | -2.167 | -5.734 | -9.457 | -14.48 | Primary | 1458
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NG FES - System Transformation | 14.738 | 14.677 | 14.58 | 14.463 | 14.361 | 14.247 | 14.116 | 13.358 | 11.968 | 10.181 | 7.566 | Primary | 1459
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NG FES - System Transformation | 4.68 | 4.579 | 4.456 | 4.317 | 4.169 | 4.015 | 3.855 | 3.089 | 2.105 | 1.079 | -0.214 | Primary | 1460
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NG FES - System Transformation | 6.73 | 6.282 | 5.713 | 5.077 | 4.432 | 3.761 | 3.05 | -0.296 | -4.036 | -7.794 | -12.564 | Primary | 1461
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NG FES - System Transformation | 12.457 | 12.134 | 11.725 | 11.276 | 10.824 | 10.36 | 9.873 | 7.638 | 5.193 | 2.416 | -1.378 | Primary | 1462
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NG FES - System Transformation | 12.789 | 11.128 | 11.05 | 10.921 | 10.754 | 10.528 | 10.234 | 8.055 | 5.063 | 2.866 | 0.645 | Primary | 1463
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NG FES - System Transformation | 2.855 | 2.566 | 2.296 | 2.093 | 1.886 | 1.673 | 1.454 | 0.509 | -0.23 | -0.969 | -1.897 | Primary | 1464
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NG FES - System Transformation | 7.713 | 7.07 | 6.307 | 5.48 | 4.636 | 3.766 | 2.867 | -1.439 | -4.795 | -9.363 | -15.91 | Primary | 1465
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NG FES - System Transformation | 8.467 | 8.43 | 8.383 | 8.33 | 8.271 | 8.207 | 8.139 | 7.733 | 7.242 | 6.737 | 6.216 | Primary | 1466
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NG FES - System Transformation | 1.973 | 1.772 | 1.495 | 1.146 | 0.736 | 0.244 | -0.335 | -4.167 | -8.57 | -11.338 | -13.749 | Primary | 1467
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NG FES - System Transformation | 11.648 | 11.267 | 10.865 | 10.506 | 10.163 | 9.8 | 9.414 | 7.457 | 4.622 | 1.314 | -3.425 | Primary | 1468
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NG FES - System Transformation | 9.156 | 8.776 | 8.273 | 7.693 | 7.139 | 6.553 | 5.926 | 2.723 | -0.825 | -4.693 | -10.057 | Primary | 1469
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NG FES - System Transformation | 0.814 | 0.694 | 0.539 | 0.353 | 0.143 | -0.097 | -0.371 | -2.051 | -3.915 | -5.29 | -6.572 | Primary | 1470
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NG FES - System Transformation | 7.28 | 6.919 | 6.45 | 5.922 | 5.408 | 4.878 | 4.325 | 1.725 | -1.903 | -6.063 | -11.881 | Primary | 1471
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NG FES - System Transformation | 0.797 | 0.75 | 0.666 | 0.563 | 0.466 | 0.356 | 0.222 | -0.555 | -2.319 | -4.178 | -6.602 | Primary | 1472
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NG FES - System Transformation | 1.484 | 1.482 | 1.48 | 1.478 | 1.475 | 1.471 | 1.467 | 1.446 | 1.415 | 1.386 | 1.356 | Primary | 1473
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 10.356 | 10.376 | 10.371 | 10.342 | 10.301 | 10.251 | 10.182 | 9.791 | 8.524 | 7.114 | 5.269 | Primary | 1474
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NG FES - System Transformation | 7.076 | 7.041 | 6.989 | 6.926 | 6.861 | 6.79 | 6.71 | 6.31 | 5.61 | 4.893 | 3.957 | Primary | 1475
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 8.477 | 8.387 | 8.27 | 8.135 | 7.993 | 7.847 | 7.697 | 7.033 | 6.399 | 5.834 | 5.205 | Primary | 1476
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NG FES - System Transformation | 3.815 | 3.611 | 3.364 | 3.1 | 2.83 | 2.541 | 2.229 | 0.555 | -1.266 | -3.174 | -5.693 | Primary | 1477
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NG FES - System Transformation | 14.431 | 14.164 | 13.821 | 14.417 | 13.95 | 13.467 | 12.975 | 10.651 | 8.656 | 6.158 | 2.823 | Primary | 1478
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NG FES - System Transformation | 9.969 | 8.906 | 8.577 | 8.194 | 7.826 | 7.445 | 7.041 | 5.127 | 2.718 | -0.164 | -4.353 | Primary | 1479
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NG FES - System Transformation | 3.206 | 3.005 | 2.762 | 2.486 | 2.186 | 1.857 | 1.497 | -0.534 | -3.109 | -5.261 | -7.637 | Primary | 1480
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NG FES - System Transformation | 10.487 | 9.744 | 9.108 | 8.715 | 8.349 | 7.97 | 7.572 | 5.672 | 3.124 | -0.024 | -4.661 | Primary | 1481
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NG FES - System Transformation | 10.662 | 10.567 | 10.457 | 10.337 | 10.217 | 10.09 | 9.952 | 9.156 | 7.685 | 6.003 | 3.937 | Primary | 1482
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NG FES - System Transformation | -3.21 | -3.912 | -4.787 | -5.751 | -6.703 | -7.685 | -8.706 | -13.568 | -19.216 | -25.447 | -33.88 | Primary | 1483
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NG FES - System Transformation | 6.788 | 6.16 | 5.471 | 4.822 | 4.166 | 3.495 | 2.807 | -0.287 | -2.662 | -6.081 | -11.205 | Primary | 1484
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NG FES - System Transformation | 5.102 | 5.1 | 5.051 | 4.972 | 4.923 | 4.857 | 4.764 | 4.043 | 2.294 | -0.261 | -4.326 | Primary | 1485
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NG FES - System Transformation | 17.193 | 14.136 | 13.947 | 13.74 | 13.536 | 13.325 | 13.102 | 12.011 | 10.15 | 8.226 | 5.924 | Primary | 1486
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NG FES - System Transformation | 13.796 | 13.736 | 13.658 | 13.56 | 13.44 | 13.301 | 13.141 | 12.135 | 10.568 | 9.208 | 7.841 | Primary | 1487
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NG FES - System Transformation | 9.497 | 9.248 | 8.96 | 8.627 | 8.253 | 7.831 | 7.353 | 4.404 | 0.515 | -2.517 | -5.3 | Primary | 1488
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NG FES - System Transformation | 12.656 | 12.642 | 12.596 | 12.528 | 12.464 | 12.391 | 12.299 | 11.811 | 10.323 | 8.62 | 6.289 | Primary | 1489
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NG FES - System Transformation | 11.471 | 11.503 | 11.512 | 11.503 | 11.49 | 11.466 | 11.432 | 11.214 | 10.683 | 10.113 | 9.382 | Primary | 1490
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NG FES - System Transformation | 4.047 | 3.819 | 3.561 | 3.269 | 2.939 | 2.566 | 2.145 | -0.506 | -3.953 | -6.651 | -9.086 | Primary | 1491
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NG FES - System Transformation | 16.261 | 16.184 | 16.084 | 15.97 | 15.865 | 15.747 | 15.613 | 14.776 | 13.447 | 11.929 | 9.905 | Primary | 1492
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NG FES - System Transformation | 10.654 | 10.404 | 10.059 | 9.667 | 9.302 | 8.924 | 8.52 | 6.585 | 4.042 | 0.917 | -3.678 | Primary | 1493
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NG FES - System Transformation | 10.204 | 10.109 | 9.959 | 9.777 | 9.618 | 9.441 | 9.236 | 8.035 | 5.91 | 3.324 | -0.402 | Primary | 1494
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NG FES - System Transformation | 6.934 | 6.58 | 6.106 | 5.556 | 5.021 | 4.453 | 3.841 | 0.73 | -2.836 | -6.608 | -11.778 | Primary | 1495
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NG FES - System Transformation | 4.369 | 3.985 | 3.519 | 3.016 | 2.506 | 1.961 | 1.374 | -1.719 | -5.414 | -9.098 | -13.68 | Primary | 1496
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NG FES - System Transformation | 11.687 | 11.661 | 11.609 | 11.535 | 11.43 | 11.291 | 11.116 | 9.893 | 8.528 | 7.811 | 7.37 | Primary | 1497
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NG FES - System Transformation | 15.275 | 14.996 | 14.613 | 14.171 | 13.77 | 13.362 | 12.935 | 10.935 | 8.66 | 5.527 | 0.65 | Primary | 1498
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NG FES - System Transformation | 9.117 | 8.663 | 8.072 | 7.388 | 6.693 | 5.938 | 5.112 | 0.627 | -4.489 | -9.085 | -14.736 | Primary | 1499
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NG FES - System Transformation | 3.249 | 3.124 | 2.969 | 3.298 | 3.128 | 2.953 | 2.769 | 1.874 | 0.794 | -0.301 | -1.696 | Primary | 1500
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NG FES - System Transformation | 7.927 | 7.679 | 7.342 | 6.96 | 6.574 | 6.174 | 5.755 | 3.779 | 0.653 | -2.889 | -7.884 | Primary | 1501
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NG FES - System Transformation | 4.012 | 3.839 | 3.608 | 3.351 | 3.097 | 2.837 | 2.568 | 1.318 | 0.139 | -1.507 | -4.047 | Primary | 1502
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 12.206 | 12.163 | 12.104 | 12.029 | 11.951 | 11.862 | 11.761 | 11.163 | 10.068 | 8.894 | 7.469 | Primary | 1503
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NG FES - System Transformation | 25.283 | 25.241 | 25.187 | 25.121 | 25.055 | 24.983 | 24.901 | 24.466 | 23.439 | 22.366 | 21.039 | Primary | 1504
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NG FES - System Transformation | 14.505 | 14.37 | 14.196 | 13.985 | 13.724 | 13.446 | 13.153 | 11.656 | 10.468 | 9.276 | 7.902 | Primary | 1505
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NG FES - System Transformation | 12.633 | 12.667 | 12.686 | 12.689 | 12.686 | 12.675 | 12.65 | 12.475 | 11.517 | 10.624 | 9.58 | Primary | 1506
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NG FES - System Transformation | 19.789 | 19.758 | 19.72 | 19.676 | 19.63 | 19.582 | 19.527 | 19.234 | 18.502 | 17.74 | 16.86 | Primary | 1507
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NG FES - System Transformation | 6.594 | 6.38 | 6.08 | 5.724 | 5.345 | 4.95 | 4.539 | 2.606 | 0.906 | -1.502 | -5.079 | Primary | 1508
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NG FES - System Transformation | 22.359 | 22.331 | 22.259 | 22.153 | 22.053 | 21.935 | 21.79 | 20.945 | 19.052 | 17.023 | 14.319 | Primary | 1509
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NG FES - System Transformation | 14.489 | 14.42 | 14.331 | 14.237 | 14.171 | 14.098 | 14.008 | 13.481 | 11.974 | 10.057 | 7.26 | Primary | 1510
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NG FES - System Transformation | 4.696 | 4.612 | 4.501 | 4.377 | 4.263 | 4.143 | 4.016 | 3.387 | 2.665 | 1.817 | 0.565 | Primary | 1511
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NG FES - System Transformation | 4.496 | 4.464 | 4.427 | 4.387 | 4.343 | 4.296 | 4.243 | 3.93 | 3.574 | 3.255 | 2.947 | Primary | 1512
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NG FES - System Transformation | 15.577 | 15.484 | 15.358 | 15.205 | 15.042 | 14.859 | 14.646 | 13.382 | 11.06 | 8.8 | 6.137 | Primary | 1513
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 9.615 | 9.472 | 9.279 | 9.055 | 8.833 | 8.602 | 8.36 | 7.214 | 5.774 | 4.22 | 2.06 | Primary | 1514
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NG FES - System Transformation | 11.493 | 11.401 | 11.278 | 11.135 | 11 | 10.861 | 10.715 | 10.011 | 8.973 | 7.706 | 5.845 | Primary | 1515
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NG FES - System Transformation | 2.276 | 2.111 | 1.917 | 1.707 | 1.482 | 1.249 | 1.01 | -0.152 | -1.535 | -3.007 | -4.894 | Primary | 1516
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NG FES - System Transformation | 3.33 | 3.138 | 2.911 | 2.655 | 2.403 | 2.127 | 1.81 | -0.057 | -3.319 | -6.79 | -11.232 | Primary | 1517
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NG FES - System Transformation | 18.899 | 18.875 | 18.84 | 18.796 | 18.746 | 18.684 | 18.611 | 18.122 | 17.495 | 16.977 | 16.416 | Primary | 1518
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NG FES - System Transformation | 4.817 | 4.734 | 4.627 | 4.509 | 4.394 | 4.277 | 4.154 | 3.565 | 2.725 | 1.731 | 0.277 | Primary | 1519
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NG FES - System Transformation | 14.757 | 14.729 | 14.7 | 14.673 | 14.644 | 14.606 | 14.555 | 14.196 | 13.363 | 12.515 | 11.393 | Primary | 1520
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NG FES - System Transformation | 12.581 | 12.649 | 12.703 | 12.744 | 12.778 | 12.8 | 12.809 | 12.721 | 12.291 | 11.883 | 11.398 | Primary | 1521
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NG FES - System Transformation | 2.121 | 1.821 | 1.435 | 0.993 | 0.54 | 0.067 | -0.428 | -2.82 | -4.92 | -7.009 | -9.665 | Primary | 1522
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 5.867 | 5.833 | 5.783 | 5.723 | 5.663 | 5.596 | 5.519 | 5.071 | 4.254 | 3.338 | 2.139 | Primary | 1523
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NG FES - System Transformation | 5.22 | 5.171 | 5.103 | 5.021 | 4.931 | 4.826 | 4.704 | 3.935 | 2.92 | 1.96 | 0.807 | Primary | 1524
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NG FES - System Transformation | 5.142 | 4.812 | 4.397 | 3.933 | 3.47 | 2.985 | 2.474 | -0.087 | -3.198 | -6.421 | -10.657 | Primary | 1525
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NG FES - System Transformation | 15.278 | 15.192 | 15.084 | 14.963 | 14.851 | 14.731 | 14.595 | 13.84 | 12.386 | 10.792 | 8.751 | Primary | 1526
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NG FES - System Transformation | 8.024 | 7.428 | 6.771 | 6.147 | 5.509 | 4.851 | 4.169 | 1.023 | -2.615 | -6.566 | -12.083 | Primary | 1527
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NG FES - System Transformation | 4.771 | 4.684 | 4.577 | 4.464 | 4.333 | 4.177 | 3.988 | 2.791 | 0.304 | -2.293 | -5.679 | Primary | 1528
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NG FES - System Transformation | 10.252 | 9.943 | 9.516 | 9.017 | 8.548 | 8.064 | 7.561 | 5.11 | 1.411 | -3.152 | -9.874 | Primary | 1529
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NG FES - System Transformation | 0.19 | 0.104 | 0.004 | -0.112 | -0.232 | -0.361 | -0.505 | -1.337 | -2.628 | -4.041 | -5.807 | Primary | 1530
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NG FES - System Transformation | 13.326 | 13.031 | 12.648 | 12.229 | 11.81 | 11.374 | 10.913 | 8.693 | 6.091 | 3.241 | -0.784 | Primary | 1531
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NG FES - System Transformation | 18.398 | 18.389 | 18.372 | 18.346 | 18.312 | 18.273 | 18.224 | 17.936 | 17.17 | 16.467 | 15.651 | Primary | 1532
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NG FES - System Transformation | 12.448 | 12.263 | 12.046 | 11.811 | 11.571 | 11.32 | 11.051 | 9.618 | 7.903 | 5.421 | 1.802 | Primary | 1533
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NG FES - System Transformation | 7.097 | 6.969 | 6.808 | 6.618 | 6.415 | 6.195 | 5.959 | 4.611 | 2.572 | 0.245 | -2.88 | Primary | 1534
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NG FES - System Transformation | 8.124 | 7.969 | 7.758 | 7.498 | 7.232 | 6.925 | 6.569 | 4.218 | 0.602 | -3.044 | -7.744 | Primary | 1535
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NG FES - System Transformation | 16.293 | 16.249 | 16.201 | 16.148 | 16.093 | 16.034 | 15.971 | 15.602 | 15.146 | 14.674 | 14.201 | Primary | 1536
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NG FES - System Transformation | 16.915 | 16.821 | 16.684 | 16.518 | 16.343 | 16.157 | 15.957 | 14.987 | 13.563 | 12.172 | 10.374 | Primary | 1537
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NG FES - System Transformation | 18.977 | 18.934 | 18.878 | 18.814 | 18.75 | 18.685 | 18.615 | 18.285 | 17.678 | 17.039 | 16.225 | Primary | 1538
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NG FES - System Transformation | 8.901 | 8.36 | 7.843 | 7.446 | 7.071 | 6.684 | 6.274 | 4.363 | 1.949 | -1.071 | -5.492 | Primary | 1539
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NG FES - System Transformation | 10.295 | 9.858 | 9.347 | 8.835 | 8.342 | 7.831 | 7.294 | 4.758 | 1.834 | -1.443 | -6.142 | Primary | 1540
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NG FES - System Transformation | -6.559 | -6.478 | -6.418 | -6.376 | -6.35 | -6.339 | -6.345 | -6.539 | -7.097 | -7.539 | -7.98 | Primary | 1541
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NG FES - System Transformation | 9.932 | 9.231 | 8.553 | 8.018 | 7.498 | 6.963 | 6.407 | 3.809 | 0.324 | -3.818 | -9.838 | Primary | 1542
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NG FES - System Transformation | 11.324 | 11.204 | 11.048 | 10.857 | 10.66 | 10.435 | 10.171 | 8.538 | 5.679 | 2.972 | -0.285 | Primary | 1543
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NG FES - System Transformation | 5.127 | 4.826 | 4.45 | 4.03 | 3.617 | 3.194 | 2.758 | 0.734 | -1.804 | -4.62 | -8.402 | Primary | 1544
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NG FES - System Transformation | 24.4 | 24.373 | 24.309 | 24.219 | 24.143 | 24.055 | 23.945 | 23.293 | 21.266 | 19.002 | 15.931 | Primary | 1545
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NG FES - System Transformation | 6.314 | 6.089 | 5.818 | 5.515 | 5.198 | 4.86 | 4.495 | 2.545 | 0.152 | -2.362 | -5.335 | Primary | 1546
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NG FES - System Transformation | 6.763 | 6.753 | 6.739 | 6.723 | 6.708 | 6.692 | 6.674 | 6.584 | 6.455 | 6.324 | 6.142 | Primary | 1547
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NG FES - System Transformation | 11.402 | 10.898 | 10.228 | 9.464 | 8.728 | 7.968 | 7.169 | 3.336 | -0.877 | -6.148 | -13.869 | Primary | 1548
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NG FES - System Transformation | 21.959 | 21.969 | 21.952 | 21.904 | 21.819 | 21.69 | 21.516 | 20.085 | 18.401 | 17.56 | 17.1 | Primary | 1549
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NG FES - System Transformation | 11.151 | 10.907 | 10.591 | 10.243 | 9.917 | 9.574 | 9.206 | 7.39 | 4.934 | 2.103 | -1.93 | Primary | 1550
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NG FES - System Transformation | 12.056 | 11.922 | 11.735 | 11.485 | 11.165 | 10.771 | 10.298 | 6.998 | 2.675 | -0.502 | -3.646 | Primary | 1551
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NG FES - System Transformation | 0.704 | 0.595 | 0.454 | 0.293 | 0.123 | -0.06 | -0.264 | -1.378 | -2.975 | -4.371 | -5.941 | Primary | 1552
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NG FES - System Transformation | 6.933 | 1.206 | 0.913 | 0.578 | 0.219 | -0.155 | -0.541 | -2.426 | -4.16 | -6.191 | -8.914 | Primary | 1553
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NG FES - System Transformation | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 1554
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NG FES - System Transformation | 4.926 | 4.667 | 4.344 | 3.986 | 3.626 | 3.254 | 2.861 | 0.953 | -1.298 | -3.813 | -7.124 | Primary | 1555
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NG FES - System Transformation | 12.854 | 12.655 | 12.4 | 12.097 | 11.747 | 11.318 | 10.802 | 7.352 | 3.138 | 0.238 | -2.568 | Primary | 1556
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NG FES - System Transformation | 2.142 | 1.914 | 1.627 | 1.329 | 1.026 | 0.7 | 0.343 | -1.492 | -3.541 | -5.893 | -9.157 | Primary | 1557
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NG FES - System Transformation | 2.165 | 1.978 | 1.785 | 1.626 | 1.466 | 1.3 | 1.129 | 0.362 | -0.34 | -1.291 | -2.716 | Primary | 1558
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NG FES - System Transformation | 12.894 | 12.75 | 12.545 | 12.309 | 12.1 | 11.878 | 11.637 | 10.39 | 8.636 | 6.541 | 3.467 | Primary | 1559
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NG FES - System Transformation | 7.82 | 7.834 | 7.843 | 7.852 | 7.853 | 7.844 | 7.817 | 7.638 | 6.371 | 5.276 | 4.106 | Primary | 1560
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NG FES - System Transformation | 13.481 | 13.424 | 13.335 | 13.222 | 13.121 | 13.008 | 12.874 | 12.073 | 10.616 | 8.709 | 5.928 | Primary | 1561
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NG FES - System Transformation | 6.96 | 6.52 | 5.978 | 5.374 | 4.759 | 4.121 | 3.452 | 0.177 | -3.512 | -7.064 | -11.371 | Primary | 1562
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NG FES - System Transformation | 12.721 | 12.687 | 12.612 | 12.502 | 12.372 | 12.199 | 11.977 | 10.313 | 8.162 | 6.515 | 4.712 | Primary | 1563
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NG FES - System Transformation | 13.744 | 13.773 | 13.796 | 13.814 | 13.829 | 13.841 | 13.847 | 13.84 | 13.602 | 13.382 | 13.142 | Primary | 1564
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NG FES - System Transformation | 5.891 | 5.872 | 5.846 | 5.816 | 5.787 | 5.754 | 5.719 | 5.538 | 5.367 | 5.169 | 4.876 | Primary | 1565
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NG FES - System Transformation | 14.141 | 14.16 | 14.164 | 14.154 | 14.137 | 14.114 | 14.076 | 13.866 | 12.838 | 11.902 | 10.855 | Primary | 1566
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NG FES - System Transformation | -4.167 | -4.428 | -4.786 | -5.202 | -5.593 | -5.999 | -6.425 | -8.488 | -10.708 | -13.563 | -17.823 | Primary | 1567
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NG FES - System Transformation | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 1568
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NG FES - System Transformation | 8.804 | 7.695 | 7.136 | 6.513 | 5.914 | 5.297 | 4.659 | 1.641 | -2.164 | -6.767 | -13.357 | Primary | 1569
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NG FES - System Transformation | 8.659 | 8.11 | 7.439 | 6.746 | 12.081 | 11.399 | 10.684 | 7.365 | 4.004 | -0.215 | -6.579 | Primary | 1570
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NG FES - System Transformation | 3.972 | 4.026 | 4.058 | 4.067 | 4.056 | 4.03 | 3.988 | 3.64 | 2.178 | 0.668 | -1.247 | Primary | 1571
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NG FES - System Transformation | 2.215 | 1.885 | 1.457 | 0.956 | 0.404 | -0.165 | -0.746 | -3.42 | -7.006 | -10.913 | -16.092 | Primary | 1572
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NG FES - System Transformation | 14.309 | 14.113 | 13.864 | 13.593 | 13.324 | 13.045 | 12.753 | 11.358 | 9.221 | 6.802 | 3.377 | Primary | 1573
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NG FES - System Transformation | 5.315 | 4.865 | 4.247 | 3.528 | 2.809 | 2.056 | 1.253 | -2.673 | -6.748 | -11.498 | -18.163 | Primary | 1574
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NG FES - System Transformation | 5.022 | 3.999 | 3.684 | 3.371 | 3.059 | 2.719 | 2.347 | 0.348 | -2.182 | -5.075 | -9.185 | Primary | 1575
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NG FES - System Transformation | 15.006 | 14.849 | 14.647 | 14.431 | 14.233 | 14.028 | 13.81 | 12.778 | 11.464 | 9.799 | 7.28 | Primary | 1576
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NG FES - System Transformation | 4.028 | 3.756 | 3.391 | 2.981 | 2.585 | 2.165 | 1.712 | -0.59 | -3.396 | -6.425 | -10.688 | Primary | 1577
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NG FES - System Transformation | 7.72 | 7.479 | 7.189 | 6.855 | 6.499 | 6.113 | 5.688 | 3.279 | 0.187 | -3.167 | -7.359 | Primary | 1578
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NG FES - System Transformation | 8.699 | 8.311 | 7.815 | 7.254 | 6.679 | 6.081 | 5.454 | 2.464 | 0.071 | -3.19 | -8.018 | Primary | 1579
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NG FES - System Transformation | 6.656 | 6.357 | 5.964 | 5.512 | 5.006 | 4.486 | 3.959 | 1.529 | -0.345 | -2.547 | -5.494 | Primary | 1580
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NG FES - System Transformation | 2.088 | 1.293 | 0.483 | -0.21 | -0.9 | -1.614 | -2.351 | -5.837 | -10.351 | -15.456 | -22.686 | Primary | 1581
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NG FES - System Transformation | 9.476 | 8.962 | 8.393 | 7.859 | 7.37 | 6.867 | 6.34 | 3.86 | 1.002 | -2.719 | -8.372 | Primary | 1582
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NG FES - System Transformation | 10.433 | 9.922 | 9.352 | 8.808 | 8.255 | 7.663 | 7.025 | 3.726 | 0.13 | -3.407 | -8.117 | Primary | 1583
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NG FES - System Transformation | 13.35 | 13.343 | 13.305 | 13.233 | 13.144 | 13.024 | 12.863 | 11.685 | 9.614 | 8.045 | 6.447 | Primary | 1584
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NG FES - System Transformation | 8.763 | 8.637 | 8.471 | 8.283 | 8.099 | 7.906 | 7.697 | 6.663 | 5.052 | 3.389 | 1.134 | Primary | 1585
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NG FES - System Transformation | 3.499 | 3.455 | 3.374 | 3.262 | 3.133 | 2.978 | 2.79 | 1.557 | 0.075 | -1.318 | -3.035 | Primary | 1586
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NG FES - System Transformation | 12.811 | 12.586 | 12.286 | 11.948 | 11.636 | 11.313 | 10.973 | 9.376 | 7.263 | 4.791 | 1.202 | Primary | 1587
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NG FES - System Transformation | 17.56 | 17.449 | 17.28 | 17.072 | 16.865 | 16.649 | 16.423 | 15.347 | 14.036 | 12.601 | 10.537 | Primary | 1588
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NG FES - System Transformation | 15.292 | 15.22 | 15.117 | 14.989 | 14.836 | 14.673 | 14.501 | 13.551 | 12.369 | 10.421 | 7.535 | Primary | 1589
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NG FES - System Transformation | 4.048 | 3.892 | 3.688 | 3.428 | 3.114 | 2.735 | 2.283 | -0.759 | -4.696 | -7.788 | -10.997 | Primary | 1590
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NG FES - System Transformation | 10.064 | 10.088 | 10.094 | 10.081 | 10.057 | 10.018 | 9.956 | 9.505 | 8.103 | 6.819 | 5.357 | Primary | 1591
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NG FES - System Transformation | -1.273 | -1.378 | -1.508 | -1.657 | -1.803 | -1.967 | -2.155 | -3.308 | -5.053 | -6.784 | -8.906 | Primary | 1592
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NG FES - System Transformation | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary | 1593
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NG FES - System Transformation | 6.545 | 6.064 | 5.532 | 5.01 | 4.485 | 3.93 | 3.336 | 0.382 | -2.487 | -5.811 | -10.542 | Primary | 1594
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NG FES - System Transformation | 14.224 | 13.925 | 13.546 | 13.114 | 12.726 | 12.325 | 11.901 | 9.813 | 7.52 | 4.459 | -0.297 | Primary | 1595
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NG FES - System Transformation | 3.407 | 3.258 | 3.078 | 2.88 | 2.69 | 2.496 | 2.291 | 1.315 | 0.041 | -1.323 | -3.127 | Primary | 1596
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NG FES - System Transformation | 8.678 | 8.383 | 8.009 | 7.539 | 6.986 | 6.317 | 5.516 | 0.11 | -6.805 | -11.94 | -16.956 | Primary | 1597
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NG FES - System Transformation | 12.909 | 12.397 | 11.873 | 11.411 | 10.968 | 10.51 | 10.026 | 7.754 | 4.942 | 1.906 | -2.313 | Primary | 1598
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NG FES - System Transformation | 5.036 | 4.938 | 4.816 | 4.683 | 4.554 | 4.423 | 4.288 | 3.644 | 2.802 | 1.836 | 0.489 | Primary | 1599
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NG FES - System Transformation | 6.562 | 6.119 | 5.572 | 4.967 | 4.387 | 3.789 | 3.162 | 0.202 | -3.958 | -8.589 | -14.864 | Primary | 1600
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NG FES - System Transformation | 10.061 | 9.779 | 9.398 | 8.965 | 8.564 | 8.15 | 7.715 | 5.636 | 2.668 | -0.841 | -5.941 | Primary | 1601
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NG FES - System Transformation | 14.746 | 14.398 | 14.016 | 13.654 | 13.296 | 12.932 | 12.56 | 10.911 | 8.989 | 6.637 | 3.205 | Primary | 1602
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NG FES - System Transformation | 6.299 | 6.116 | 5.847 | 5.525 | 5.22 | 4.895 | 4.539 | 2.738 | 0.157 | -2.813 | -7.015 | Primary | 1603
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NG FES - System Transformation | 13.881 | 13.479 | 12.999 | 12.461 | 11.868 | 11.242 | 10.582 | 7.249 | 3.306 | -0.469 | -4.956 | Primary | 1604
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NG FES - System Transformation | 13.057 | 13.009 | 12.948 | 12.872 | 12.796 | 12.714 | 12.622 | 12.103 | 11.084 | 9.837 | 8.165 | Primary | 1605
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NG FES - System Transformation | 9.093 | 8.79 | 8.406 | 7.985 | 7.548 | 7.084 | 6.582 | 4.046 | 1.568 | -1.079 | -4.601 | Primary | 1606
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NG FES - System Transformation | 12.38 | 12.382 | 12.352 | 12.29 | 12.21 | 12.101 | 11.958 | 10.937 | 9.362 | 8.158 | 6.903 | Primary | 1607
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NG FES - System Transformation | 6.818 | 6.772 | 6.673 | 6.529 | 6.36 | 6.152 | 5.896 | 4.186 | 1.838 | -0.405 | -3.177 | Primary | 1608
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NG FES - System Transformation | 25.577 | 25.46 | 25.301 | 25.103 | 24.881 | 24.628 | 24.342 | 22.651 | 20.606 | 18.967 | 17.342 | Primary | 1609
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NG FES - System Transformation | 4.402 | 4.146 | 3.86 | 3.55 | 3.248 | 2.928 | 2.589 | 0.619 | -2.566 | -6.16 | -10.762 | Primary | 1610
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NG FES - System Transformation | 1.829 | 1.772 | 1.698 | 1.614 | 1.526 | 1.434 | 1.337 | 0.863 | 0.365 | -0.114 | -0.625 | Primary | 1611
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NG FES - System Transformation | 12.344 | 12.058 | 11.721 | 11.361 | 10.997 | 10.618 | 10.213 | 8.237 | 5.677 | 2.819 | -0.981 | Primary | 1612
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NG FES - System Transformation | 10.136 | 10.129 | 10.1 | 10.056 | 10.014 | 9.96 | 9.886 | 9.385 | 8.186 | 6.991 | 5.446 | Primary | 1613
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NG FES - System Transformation | 10.203 | 10.128 | 10.001 | 9.833 | 9.666 | 9.483 | 9.276 | 8.059 | 4.837 | 0.901 | -4.758 | Primary | 1614
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NG FES - System Transformation | 0.671 | 0.599 | 0.508 | 0.401 | 0.285 | 0.154 | 0.004 | -0.892 | -2.305 | -3.598 | -5.027 | Primary | 1615
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NG FES - System Transformation | 9.377 | 9.369 | 9.308 | 9.185 | 8.99 | 8.714 | 8.345 | 5.489 | 1.277 | -1.292 | -3.321 | Primary | 1616
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NG FES - System Transformation | 16.392 | 16.336 | 16.27 | 16.209 | 16.143 | 16.067 | 15.977 | 15.455 | 14.55 | 13.712 | 12.683 | Primary | 1617
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NG FES - System Transformation | 8.838 | 7.676 | 7.193 | 6.654 | 6.118 | 5.563 | 4.978 | 2.129 | -1.859 | -6.129 | -11.751 | Primary | 1618
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NG FES - System Transformation | 12.164 | 12.042 | 11.867 | 11.664 | 11.467 | 11.26 | 11.043 | 9.994 | 8.61 | 6.915 | 4.423 | Primary | 1619
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NG FES - System Transformation | 18.04 | 18.051 | 17.992 | 17.853 | 17.633 | 17.314 | 16.892 | 13.583 | 9.546 | 7.377 | 5.958 | Primary | 1620
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NG FES - System Transformation | 10.021 | 9.679 | 9.221 | 8.707 | 8.238 | 7.746 | 7.218 | 4.538 | 1.221 | -2.811 | -8.807 | Primary | 1621
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NG FES - System Transformation | 4.267 | 4.202 | 4.119 | 4.025 | 3.933 | 3.836 | 3.734 | 3.231 | 2.641 | 1.993 | 1.129 | Primary | 1622
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NG FES - System Transformation | 9.326 | 8.989 | 8.616 | 8.26 | 7.943 | 7.611 | 7.254 | 5.461 | 3.05 | 0.102 | -4.201 | Primary | 1623
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 15.059 | 14.883 | 14.655 | 14.381 | 14.08 | 13.754 | 13.393 | 11.367 | 8.344 | 4.992 | 0.831 | Primary | 1624
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NG FES - System Transformation | 13.482 | 13.307 | 13.078 | 12.799 | 12.505 | 12.182 | 11.815 | 9.704 | 5.559 | 1.312 | -3.755 | Primary | 1625
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NG FES - System Transformation | 13.326 | 13.325 | 13.304 | 13.266 | 13.218 | 13.155 | 13.072 | 12.537 | 11.278 | 10.187 | 8.978 | Primary | 1626
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NG FES - System Transformation | 8.09 | 8.107 | 8.099 | 8.072 | 8.057 | 8.034 | 7.998 | 7.726 | 6.822 | 5.614 | 3.814 | Primary | 1627
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NG FES - System Transformation | 17.502 | 17.395 | 17.241 | 17.061 | 16.877 | 16.686 | 16.482 | 15.513 | 14.604 | 13.448 | 11.766 | Primary | 1628
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NG FES - System Transformation | 5.688 | 5.614 | 5.526 | 5.42 | 5.297 | 5.157 | 4.998 | 3.972 | 2.531 | 1.203 | -0.108 | Primary | 1629
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NG FES - System Transformation | 1.996 | 1.501 | 0.964 | 0.468 | 0.008 | -0.468 | -0.966 | -3.332 | -6.216 | -9.795 | -15.089 | Primary | 1630
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NG FES - System Transformation | 12.606 | 12.247 | 11.845 | 11.457 | 11.071 | 10.673 | 10.262 | 8.342 | 6.067 | 3.222 | -0.927 | Primary | 1631
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NG FES - System Transformation | 9.786 | 9.297 | 8.722 | 8.138 | 7.568 | 6.959 | 6.301 | 2.824 | -0.919 | -5.035 | -10.738 | Primary | 1632
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NG FES - System Transformation | 11.583 | 11.588 | 11.561 | 11.502 | 11.413 | 11.29 | 11.126 | 9.917 | 8.09 | 6.827 | 5.683 | Primary | 1633
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NG FES - System Transformation | 15.96 | 15.753 | 15.472 | 15.153 | 14.862 | 14.563 | 14.25 | 12.782 | 11.209 | 9.243 | 6.265 | Primary | 1634
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NG FES - System Transformation | 12.847 | 12.725 | 12.541 | 12.316 | 12.09 | 11.852 | 11.593 | 10.306 | 7.974 | 5.685 | 2.679 | Primary | 1635
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NG FES - System Transformation | 9.284 | 9.033 | 8.693 | 8.304 | 7.924 | 7.513 | 7.058 | 4.662 | 1.699 | -1.241 | -5.14 | Primary | 1636
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NG FES - System Transformation | 11.458 | 9.705 | 9.532 | 9.323 | 9.127 | 8.921 | 8.702 | 7.646 | 6.051 | 4.018 | 0.953 | Primary | 1637
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NG FES - System Transformation | 5.178 | 5.087 | 4.975 | 4.856 | 4.735 | 4.608 | 4.476 | 3.86 | 3.126 | 2.402 | 1.474 | Primary | 1638
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NG FES - System Transformation | 14.137 | 13.732 | 13.211 | 12.641 | 12.077 | 11.495 | 10.885 | 8.026 | 5.05 | 1.72 | -3.107 | Primary | 1639
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NG FES - System Transformation | 2.987 | 2.642 | 2.165 | 1.615 | 1.069 | 0.502 | -0.095 | -2.93 | -6.951 | -11.548 | -18.081 | Primary | 1640
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NG FES - System Transformation | 14.726 | 14.466 | 14.132 | 13.776 | 13.421 | 13.052 | 12.662 | 10.808 | 8.889 | 6.655 | 3.404 | Primary | 1641
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NG FES - System Transformation | 6.872 | 6.439 | 5.898 | 5.321 | 4.766 | 4.191 | 3.581 | 0.73 | -2.869 | -7.14 | -13.298 | Primary | 1642
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NG FES - System Transformation | 19.259 | 19.273 | 19.234 | 19.149 | 19.061 | 18.948 | 18.799 | 17.803 | 15.001 | 12.115 | 8.299 | Primary | 1643
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NG FES - System Transformation | 12.459 | 12.317 | 12.137 | 11.939 | 11.719 | 11.485 | 11.234 | 10.013 | 8.636 | 7.231 | 5.462 | Primary | 1644
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NG FES - System Transformation | 4.43 | 4.091 | 3.661 | 3.176 | 2.704 | 2.208 | 1.675 | -1.024 | -4.501 | -8.048 | -12.623 | Primary | 1645
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NG FES - System Transformation | 8.598 | 7.85 | 6.956 | 5.964 | 4.846 | 3.682 | 2.496 | -3.23 | -8.589 | -14.306 | -21.563 | Primary | 1646
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NG FES - System Transformation | 4.458 | 4.099 | 3.687 | 3.278 | 2.867 | 2.438 | 1.987 | -0.229 | -3.507 | -7.319 | -12.757 | Primary | 1647
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NG FES - System Transformation | 12.78 | 12.332 | 11.785 | 11.19 | 10.61 | 10.019 | 9.411 | 6.592 | 4.004 | 0.528 | -4.645 | Primary | 1648
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NG FES - System Transformation | 20.861 | 17.761 | 17.785 | 17.804 | 17.819 | 17.833 | 17.842 | 17.871 | 17.588 | 17.347 | 17.112 | Primary | 1649
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NG FES - System Transformation | 3.311 | 3.096 | 2.823 | 2.495 | 2.106 | 1.649 | 1.114 | -2.337 | -6.716 | -10.216 | -13.704 | Primary | 1650
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NG FES - System Transformation | 13.765 | 13.674 | 13.549 | 13.412 | 13.302 | 13.184 | 13.047 | 12.245 | 10.625 | 8.344 | 4.815 | Primary | 1651
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NG FES - System Transformation | 14.242 | 14.285 | 14.315 | 14.338 | 14.357 | 14.371 | 14.376 | 14.337 | 14.054 | 13.677 | 13.133 | Primary | 1652
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NG FES - System Transformation | 15.641 | 15.662 | 15.669 | 15.664 | 15.659 | 15.649 | 15.628 | 15.481 | 14.809 | 14.14 | 13.301 | Primary | 1653
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NG FES - System Transformation | 9.413 | 8.906 | 8.249 | 7.508 | 6.775 | 6.02 | 5.236 | 1.56 | -1.832 | -6.09 | -12.3 | Primary | 1654
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NG FES - System Transformation | 14.663 | 14.546 | 14.403 | 14.243 | 14.102 | 13.95 | 13.778 | 12.751 | 10.626 | 8.231 | 5.062 | Primary | 1655
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NG FES - System Transformation | 5.915 | 5.844 | 5.733 | 5.594 | 5.464 | 5.321 | 5.152 | 4.195 | 1.902 | -0.788 | -4.524 | Primary | 1656
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NG FES - System Transformation | 13.922 | 13.743 | 13.502 | 13.226 | 12.948 | 12.654 | 12.34 | 10.81 | 8.916 | 6.947 | 4.332 | Primary | 1657
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NG FES - System Transformation | 17.505 | 13.933 | 13.884 | 13.831 | 13.773 | 13.709 | 13.64 | 13.32 | 13.046 | 12.808 | 12.529 | Primary | 1658
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NG FES - System Transformation | 10.828 | 10.592 | 10.304 | 9.997 | 9.689 | 9.368 | 9.026 | 7.34 | 5.598 | 3.578 | 0.767 | Primary | 1659
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NG FES - System Transformation | 2.634 | 2.457 | 2.225 | 1.957 | 1.677 | 1.368 | 1.027 | -0.905 | -2.932 | -4.779 | -7.041 | Primary | 1660
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NG FES - System Transformation | 10.924 | 10.61 | 10.222 | 9.816 | 9.399 | 8.97 | 8.523 | 6.495 | 4.882 | 2.479 | -1.281 | Primary | 1661
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NG FES - System Transformation | 12.502 | 12.3 | 12.031 | 11.729 | 11.447 | 11.151 | 10.835 | 9.276 | 7.414 | 5.223 | 2.025 | Primary | 1662
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NG FES - System Transformation | 5.452 | 5.241 | 4.976 | 4.651 | 4.286 | 3.864 | 3.379 | 0.242 | -4.449 | -8.662 | -13.406 | Primary | 1663
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NG FES - System Transformation | 16.481 | 16.322 | 16.126 | 15.905 | 15.686 | 15.459 | 15.221 | 14.026 | 12.483 | 10.885 | 8.823 | Primary | 1664
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NG FES - System Transformation | 11.594 | 9.836 | 9.571 | 9.255 | 8.912 | 8.524 | 8.088 | 5.283 | 1.533 | -2.498 | -7.739 | Primary | 1665
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NG FES - System Transformation | 4.664 | 4.54 | 4.388 | 4.22 | 4.052 | 3.88 | 3.701 | 2.866 | 1.963 | 1.034 | -0.169 | Primary | 1666
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NG FES - System Transformation | 14.711 | 14.444 | 14.084 | 13.673 | 13.278 | 12.869 | 12.44 | 10.462 | 8.412 | 6.194 | 3.096 | Primary | 1667
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NG FES - System Transformation | -0.027 | -0.22 | -0.457 | -0.721 | -0.987 | -1.269 | -1.571 | -3.109 | -5.301 | -7.397 | -9.992 | Primary | 1668
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NG FES - System Transformation | 9.149 | 8.814 | 8.381 | 7.893 | 7.397 | 6.88 | 6.333 | 3.682 | 0.091 | -3.77 | -8.856 | Primary | 1669
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NG FES - System Transformation | 8.296 | 8.001 | 7.603 | 7.149 | 6.72 | 6.268 | 5.779 | 3.367 | 0.171 | -3.207 | -7.88 | Primary | 1670
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NG FES - System Transformation | 5.344 | 4.898 | 4.339 | 3.714 | 3.101 | 2.463 | 1.781 | -1.527 | -6.451 | -11.572 | -18.197 | Primary | 1671
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NG FES - System Transformation | 15.926 | 15.65 | 15.286 | 14.869 | 14.449 | 14.004 | 13.525 | 11.147 | 8.523 | 5.839 | 2.256 | Primary | 1672
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NG FES - System Transformation | 8.176 | 8.198 | 8.189 | 8.152 | 8.108 | 8.045 | 7.955 | 7.311 | 5.762 | 4.293 | 2.522 | Primary | 1673
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NG FES - System Transformation | 16.358 | 17.134 | 16.865 | 8.36 | 8.042 | 7.714 | 7.376 | 5.772 | 3.497 | 0.959 | -2.499 | Primary | 1674
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NG FES - System Transformation | 10.792 | 10.371 | 9.833 | 9.213 | 8.548 | 7.856 | 7.136 | 3.635 | 0.325 | -3.515 | -8.733 | Primary | 1675
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NG FES - System Transformation | 8.738 | 8.735 | 8.709 | 8.664 | 8.625 | 8.576 | 8.509 | 8.071 | 6.759 | 5.432 | 3.716 | Primary | 1676
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NG FES - System Transformation | 10.546 | 10.153 | 9.643 | 9.067 | 8.483 | 7.883 | 7.259 | 4.352 | 1.58 | -2.013 | -7.362 | Primary | 1677
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NG FES - System Transformation | 4.851 | 4.295 | 3.606 | 2.822 | 2.006 | 1.134 | 0.187 | -4.857 | -11.471 | -17.563 | -24.633 | Primary | 1678
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NG FES - System Transformation | 12.972 | 13.021 | 13.065 | 13.101 | 13.133 | 13.16 | 13.182 | 13.247 | 13.034 | 12.851 | 12.676 | Primary | 1679
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NG FES - System Transformation | 13.7 | 13.759 | 13.801 | 13.822 | 13.821 | 13.797 | 13.748 | 13.246 | 12.3 | 11.764 | 11.424 | Primary | 1680
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NG FES - System Transformation | 2.711 | 2.767 | 2.815 | 2.853 | 2.882 | 2.904 | 2.916 | 2.897 | 2.512 | 2.184 | 1.85 | Primary | 1681
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NG FES - System Transformation | 6.267 | 6.102 | 5.911 | 5.723 | 5.543 | 5.354 | 5.149 | 4.151 | 2.852 | 1.409 | -0.551 | Primary | 1682
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NG FES - System Transformation | 1.816 | 1.647 | 1.452 | 1.247 | 1.032 | 0.806 | 0.571 | -0.616 | -1.849 | -3.089 | -4.63 | Primary | 1683
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NG FES - System Transformation | 12.6 | 12.346 | 12.012 | 11.626 | 11.241 | 10.83 | 10.384 | 8.096 | 5.321 | 2.789 | -0.356 | Primary | 1684
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NG FES - System Transformation | 12.572 | 10.574 | 10.565 | 10.544 | 10.508 | 10.459 | 10.388 | 9.914 | 8.497 | 7.37 | 6.216 | Primary | 1685
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NG FES - System Transformation | 9.057 | 8.668 | 15.236 | 14.828 | 14.432 | 14.021 | 13.587 | 11.54 | 9.08 | 6.27 | 2.247 | Primary | 1686
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NG FES - System Transformation | 11.375 | 11.242 | 11.083 | 10.899 | 10.716 | 10.51 | 10.274 | 8.758 | 6.314 | 3.736 | 0.485 | Primary | 1687
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NG FES - System Transformation | 2.928 | 1.21 | 0.718 | 0.342 | -0.03 | -0.423 | -0.843 | -2.961 | -6.341 | -10.198 | -15.556 | Primary | 1688
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NG FES - System Transformation | 12.864 | 12.811 | 12.745 | 12.668 | 12.593 | 12.511 | 12.419 | 11.876 | 10.844 | 9.649 | 8.147 | Primary | 1689
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NG FES - System Transformation | 8.383 | 8.231 | 15.003 | 14.733 | 14.485 | 14.217 | 13.92 | 12.368 | 10.003 | 7.27 | 3.386 | Primary | 1690
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NG FES - System Transformation | 4.986 | 3.72 | 3.169 | 2.735 | 2.289 | 1.811 | 1.292 | -1.401 | -5.118 | -8.711 | -13.154 | Primary | 1691
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NG FES - System Transformation | 9.988 | 9.571 | 9.025 | 8.419 | 7.857 | 7.279 | 6.679 | 3.876 | 0.949 | -3.087 | -9.36 | Primary | 1692
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NG FES - System Transformation | 12.722 | 12.583 | 10.306 | 10.058 | 9.761 | 9.397 | 8.958 | 5.921 | 2.281 | -0.248 | -2.566 | Primary | 1693
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NG FES - System Transformation | 9.242 | 8.86 | 8.376 | 7.833 | 7.273 | 6.688 | 6.07 | 3.02 | 0.234 | -2.951 | -7.35 | Primary | 1694
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NG FES - System Transformation | 7.64 | 5.684 | 5.304 | 4.915 | 4.541 | 4.147 | 3.725 | 1.642 | -1.121 | -4.388 | -9.119 | Primary | 1695
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NG FES - System Transformation | 8.482 | 7.778 | 7.814 | 7.816 | 7.789 | 7.732 | 7.634 | 6.829 | 4.74 | 3.314 | 2.119 | Primary | 1696
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NG FES - System Transformation | 18.855 | 18.828 | 18.776 | 18.694 | 18.581 | 18.429 | 18.235 | 16.808 | 14.893 | 13.757 | 12.901 | Primary | 1697
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NG FES - System Transformation | 8.516 | 8.391 | 8.195 | 7.961 | 7.743 | 7.514 | 7.269 | 6.06 | 4.394 | 2.187 | -1.216 | Primary | 1698
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NG FES - System Transformation | 10.499 | 10.31 | 10.054 | 9.751 | 9.412 | 9.048 | 8.659 | 6.664 | 4.089 | 1.645 | -1.445 | Primary | 1699
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NG FES - System Transformation | 12.328 | 12.103 | 11.797 | 11.446 | 11.129 | 10.801 | 10.449 | 8.78 | 6.182 | 3.226 | -0.964 | Primary | 1700
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NG FES - System Transformation | 12.263 | 12.252 | 12.214 | 12.155 | 12.085 | 11.999 | 11.894 | 11.228 | 10.037 | 8.726 | 7 | Primary | 1701
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NG FES - System Transformation | 8.307 | 8.381 | 8.449 | 8.518 | 8.576 | 8.622 | 8.652 | 8.69 | 8.084 | 7.548 | 6.962 | Primary | 1702
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NG FES - System Transformation | 8.12 | 6.253 | 6.127 | 5.987 | 5.863 | 5.715 | 5.536 | 4.347 | 2.403 | -0.022 | -3.571 | Primary | 1703
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NG FES - System Transformation | 10.289 | 9.089 | 9.135 | 9.164 | 9.177 | 9.182 | 9.17 | 9.065 | 8.21 | 7.452 | 6.643 | Primary | 1704
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NG FES - System Transformation | 1.639 | 1.446 | 1.214 | 0.961 | 0.715 | 0.461 | 0.19 | -1.141 | -2.893 | -4.694 | -7.037 | Primary | 1705
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NG FES - System Transformation | 3.363 | 3.337 | 3.304 | 3.271 | 3.235 | 3.197 | 3.15 | 2.901 | 2.404 | 1.696 | 0.645 | Primary | 1706
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NG FES - System Transformation | 13.769 | 13.679 | 13.551 | 13.388 | 13.197 | 12.97 | 12.704 | 10.996 | 8.827 | 7.055 | 5.213 | Primary | 1707
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NG FES - System Transformation | 24.55 | 24.549 | 24.542 | 24.527 | 24.503 | 24.475 | 24.438 | 24.202 | 23.342 | 22.522 | 21.678 | Primary | 1708
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NG FES - System Transformation | 14.926 | 14.939 | 14.932 | 14.911 | 14.888 | 14.86 | 14.824 | 14.634 | 14.064 | 13.456 | 12.663 | Primary | 1709
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NG FES - System Transformation | -1.011 | -1.194 | -1.413 | -1.664 | -1.928 | -2.213 | -2.526 | -4.311 | -6.839 | -9.403 | -12.288 | Primary | 1710
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NG FES - System Transformation | 3.574 | 3.308 | 2.982 | 2.588 | 2.149 | 1.633 | 1.026 | -2.93 | -8.869 | -13.782 | -18.969 | Primary | 1711
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NG FES - System Transformation | 10.972 | 10.799 | 10.542 | 10.239 | 9.95 | 9.651 | 9.333 | 7.85 | 5.855 | 3.459 | -0.057 | Primary | 1712
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NG FES - System Transformation | 11.668 | 11.742 | 11.8 | 11.842 | 11.866 | 11.872 | 11.858 | 11.582 | 11.032 | 10.741 | 10.584 | Primary | 1713
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NG FES - System Transformation | 8.431 | 8.033 | 7.522 | 6.943 | 6.372 | 5.768 | 5.121 | 1.75 | -2.545 | -7.103 | -13.173 | Primary | 1714
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NG FES - System Transformation | 17.057 | 16.385 | 16.32 | 16.245 | 16.17 | 16.091 | 16.005 | 15.538 | 14.472 | 13.142 | 11.301 | Primary | 1715
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NG FES - System Transformation | 4.863 | 4.54 | 4.186 | 3.855 | 3.53 | 3.198 | 2.86 | 1.325 | -0.561 | -2.835 | -6.174 | Primary | 1716
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NG FES - System Transformation | 8.517 | 8.274 | 7.917 | 7.487 | 7.077 | 6.649 | 6.2 | 4.024 | 0.866 | -2.862 | -8.374 | Primary | 1717
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NG FES - System Transformation | -1.257 | -1.449 | -1.688 | -1.947 | -2.198 | -2.457 | -2.732 | -4.051 | -6.014 | -8.331 | -11.643 | Primary | 1718
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NG FES - System Transformation | 15.344 | 15.28 | 15.192 | 15.076 | 14.941 | 14.779 | 14.584 | 13.317 | 10.973 | 9.044 | 7.017 | Primary | 1719
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NG FES - System Transformation | 15.659 | 15.055 | 14.54 | 14.215 | 13.89 | 13.547 | 13.181 | 11.352 | 8.899 | 6.506 | 3.362 | Primary | 1720
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NG FES - System Transformation | 10.549 | 10.266 | 9.858 | 9.385 | 8.901 | 8.398 | 7.865 | 5.349 | 3.173 | 0.249 | -4.172 | Primary | 1721
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NG FES - System Transformation | 24.236 | 24.261 | 24.285 | 24.308 | 24.328 | 24.344 | 24.354 | 24.361 | 24.093 | 23.846 | 23.561 | Primary | 1722
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NG FES - System Transformation | 8.439 | 8.45 | 8.461 | 8.473 | 8.478 | 8.478 | 8.467 | 8.397 | 7.441 | 6.636 | 5.811 | Primary | 1723
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NG FES - System Transformation | 11.122 | 10.855 | 10.482 | 10.05 | 9.645 | 9.228 | 8.791 | 6.79 | 4.672 | 1.876 | -2.418 | Primary | 1724
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NG FES - System Transformation | -0.798 | -0.86 | -0.935 | -1.019 | -1.101 | -1.19 | -1.287 | -1.87 | -2.721 | -3.744 | -5.025 | Primary | 1725
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NG FES - System Transformation | 9.2 | 9.076 | 8.924 | 8.75 | 8.577 | 8.391 | 8.186 | 7.057 | 5.195 | 3.202 | 0.742 | Primary | 1726
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NG FES - System Transformation | 13.29 | 13.015 | 12.651 | 12.246 | 11.862 | 11.466 | 11.05 | 9.068 | 6.679 | 3.61 | -1.082 | Primary | 1727
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NG FES - System Transformation | 11.496 | 11.254 | 10.958 | 10.631 | 10.308 | 9.969 | 9.611 | 7.783 | 5.677 | 3.191 | -0.19 | Primary | 1728
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NG FES - System Transformation | 8.156 | 7.841 | 7.421 | 6.925 | 6.359 | 5.764 | 5.149 | 2.122 | -0.798 | -4.017 | -8.215 | Primary | 1729
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NG FES - System Transformation | 13.406 | 13.143 | 12.843 | 12.51 | 12.158 | 11.772 | 11.349 | 8.867 | 5.151 | 1.669 | -2.178 | Primary | 1730
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NG FES - System Transformation | 7.6 | 7.563 | 7.472 | 7.332 | 7.168 | 6.968 | 6.724 | 5.076 | 1.988 | -1.081 | -5.047 | Primary | 1731
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NG FES - System Transformation | 13.912 | 13.7 | 13.406 | 13.069 | 12.743 | 12.405 | 12.051 | 10.403 | 8.643 | 6.312 | 2.748 | Primary | 1732
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NG FES - System Transformation | 7.26 | 6.85 | 6.396 | 5.964 | 5.54 | 5.098 | 4.631 | 2.397 | -0.74 | -4.413 | -9.675 | Primary | 1733
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NG FES - System Transformation | 7.934 | 7.756 | 7.543 | 7.297 | 7.036 | 6.753 | 6.43 | 4.601 | 1.211 | -2.127 | -6.008 | Primary | 1734
NPgY | ABBEY ROAD | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS5 3NF | NPg Best View | 13.323 | 13.179 | 13.016 | 12.961 | 12.95 | 12.933 | 12.903 | 12.79 | 11.256 | 9.973 | 8.749 | Primary | 1735
NPgY | AIREDALE ROAD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 4LJ | NPg Best View | 12.631 | 11.014 | 10.938 | 10.803 | 10.696 | 10.543 | 10.333 | 8.964 | 6.491 | 4.849 | 3.4 | Primary | 1736
NPgY | ALDHAM | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S73 8SW | NPg Best View | 11.596 | 11.366 | 11.026 | 10.627 | 10.186 | 9.732 | 9.227 | 7.023 | 2.764 | -0.66 | -3.746 | Primary | 1737
NPgY | ALFRED GELDER STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU1 1EP | NPg Best View | 5.998 | 4.643 | 4.686 | 4.681 | 4.668 | 4.631 | 4.558 | 4.045 | 2.057 | 0.606 | -0.676 | Primary | 1738
NPgY | ALLERTON HILL T1 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS7 3QB | NPg Best View | 5.528 | 5.295 | 4.988 | 4.687 | 4.496 | 4.293 | 4.042 | 2.993 | 0.383 | -1.7 | -3.654 | Primary | 1739
NPgY | ALLERTON HILL T2 | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 3QB | NPg Best View | 5.4 | 5.419 | 5.412 | 5.397 | 5.406 | 5.41 | 5.401 | 5.353 | 4.706 | 4.168 | 3.64 | Primary | 1740
NPgY | ALVERTHORPE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 9PB | NPg Best View | 10.195 | 9.785 | 9.208 | 8.537 | 8.091 | 7.626 | 7.091 | 4.745 | -0.133 | -3.925 | -7.63 | Primary | 1741
NPgY | ARMOURIES DRIVE | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LT | NPg Best View | 17.19 | 17.251 | 17.275 | 17.281 | 17.298 | 17.311 | 17.315 | 17.36 | 16.116 | 15.075 | 14.094 | Primary | 1742
NPgY | ARMTHORPE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3DY | NPg Best View | 1.482 | 1.346 | 1.13 | 0.856 | 0.616 | 0.358 | 0.05 | -1.359 | -4.953 | -7.934 | -10.68 | Primary | 1743
NPgY | ARUNDEL STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4PJ | NPg Best View | 3.081 | 2.601 | 2.75 | 2.868 | 2.992 | 3.102 | 3.19 | 3.555 | 2.931 | 2.447 | 1.976 | Primary | 1744
NPgY | ASKERN | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN6 0BY | NPg Best View | 12.233 | 12.059 | 11.776 | 11.429 | 11.211 | 10.979 | 10.7 | 9.472 | 6.684 | 4.489 | 2.3 | Primary | 1745
NPgY | AUDBY LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 7SU | NPg Best View | 2.766 | 2.56 | 2.241 | 1.916 | 1.653 | 1.347 | 0.958 | -0.971 | -4.34 | -6.613 | -8.71 | Primary | 1746
NPgY | AUSTERFIELD | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN10 6HD | NPg Best View | 3.117 | 3.125 | 3.121 | 3.11 | 3.099 | 3.084 | 3.06 | 2.923 | 2.618 | 2.377 | 2.147 | Primary | 1747
NPgY | BAILIFF BRIDGE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 4DT | NPg Best View | 15.897 | 15.753 | 15.506 | 15.203 | 15.053 | 14.894 | 14.699 | 13.877 | 11.052 | 8.811 | 6.614 | Primary | 1748
NPgY | BALBY | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN4 8DG | NPg Best View | 12.99 | 12.551 | 12.534 | 12.503 | 12.491 | 12.475 | 12.45 | 12.342 | 11.564 | 10.891 | 10.224 | Primary | 1749
NPgY | BALME STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD1 4BA | NPg Best View | 10.635 | 10.667 | 10.635 | 10.569 | 10.518 | 10.454 | 10.369 | 9.934 | 8.092 | 6.745 | 5.53 | Primary | 1750
NPgY | BARNBURGH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 9NT | NPg Best View | 15.72 | 15.444 | 15.037 | 14.554 | 14.209 | 13.832 | 13.381 | 11.28 | 7.869 | 5.431 | 3.141 | Primary | 1751
NPgY | BARNOLDSWICK | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 5RU | NPg Best View | 8.482 | 8.527 | 8.539 | 8.526 | 8.515 | 8.49 | 8.446 | 8.135 | 6.912 | 5.985 | 5.175 | Primary | 1752
NPgY | BARNSLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1AJ | NPg Best View | 6.727 | 6.645 | 6.48 | 6.273 | 6.113 | 5.949 | 5.766 | 4.898 | 1.654 | -1.16 | -3.92 | Primary | 1753
NPgY | BARNSLEY ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 7AU | NPg Best View | 21.863 | 21.855 | 21.792 | 21.692 | 21.632 | 21.564 | 21.468 | 21.094 | 19.972 | 19.087 | 18.26 | Primary | 1754
NPgY | BARROW | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN19 7EG | NPg Best View | 3.843 | 3.739 | 3.59 | 3.421 | 3.307 | 3.188 | 3.057 | 2.414 | 0.647 | -0.911 | -2.477 | Primary | 1755
NPgY | BARUGH 66/11KV | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 1HT | NPg Best View | 11.695 | 11.321 | 10.758 | 10.076 | 9.61 | 9.1 | 8.493 | 5.587 | 0.109 | -3.996 | -7.935 | Primary | 1756
NPgY | BARWICK | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS15 8SW | NPg Best View | 9.696 | 9.424 | 9.024 | 8.589 | 8.289 | 7.966 | 7.574 | 5.853 | 1.919 | -1.123 | -3.961 | Primary | 1757
NPgY | BASLOW ROAD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S17 3LT | NPg Best View | 15.023 | 14.83 | 14.556 | 14.276 | 14.081 | 13.876 | 13.625 | 12.625 | 10.695 | 9.262 | 7.921 | Primary | 1758
NPgY | BATLEY | 11 | 33 | THORNHILL 132kV | ELLAND | WF17 6HU | NPg Best View | 2.612 | 2.61 | 2.466 | 2.246 | 2.122 | 1.956 | 1.732 | 0.463 | -2.866 | -5.228 | -7.484 | Primary | 1759
NPgY | BEAL | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 8DT | NPg Best View | 5.999 | 5.847 | 5.612 | 5.318 | 5.095 | 4.845 | 4.54 | 3.053 | 0.786 | -0.847 | -2.369 | Primary | 1760
NPgY | BEESTON ROYDS 33/11KV | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 15.16 | 15.155 | 15.122 | 15.076 | 15.032 | 14.981 | 14.92 | 14.597 | 13.326 | 12.319 | 11.405 | Primary | 1761
NPgY | BEESTON ROYDS 6/7 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 6EY | NPg Best View | 4.437 | 1.442 | 1.431 | 1.349 | 1.273 | 1.142 | 0.942 | -0.399 | -4.188 | -6.938 | -9.366 | Primary | 1762
NPgY | BEIGHTON | 11 | 66 | THURCROFT | THURCROFT | S26 4TL | NPg Best View | 8.328 | 8.26 | 8.069 | 7.816 | 7.584 | 7.309 | 6.974 | 5.168 | 1.771 | -0.646 | -2.882 | Primary | 1763
NPgY | BELLHOUSE ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S5 0PL | NPg Best View | 11.852 | 11.628 | 11.256 | 10.794 | 10.516 | 10.221 | 9.862 | 8.286 | 3.826 | 0.218 | -3.218 | Primary | 1764
NPgY | BELMONT AVENUE | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN4 8DF | NPg Best View | 6.278 | 5.939 | 5.384 | 4.708 | 4.208 | 3.661 | 3.003 | -0.079 | -6.313 | -11.068 | -15.515 | Primary | 1765
NPgY | BELMONT COVERT | 11 | 33 | WOLD NEWTON | KEADBY | LN11 9RA | NPg Best View | 6.85 | 6.837 | 6.819 | 6.797 | 6.777 | 6.757 | 6.735 | 6.634 | 6.313 | 6.026 | 5.746 | Primary | 1766
NPgY | BELTHORPE LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1SB | NPg Best View | 4.359 | 4.341 | 4.306 | 4.262 | 4.218 | 4.17 | 4.108 | 3.797 | 3.242 | 2.814 | 2.412 | Primary | 1767
NPgY | BENTLEY | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN5 0NG | NPg Best View | 13.84 | 13.57 | 13.155 | 12.667 | 12.378 | 12.073 | 11.713 | 10.151 | 6.559 | 3.772 | 0.993 | Primary | 1768
NPgY | BILLET LANE | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 14.031 | 13.979 | 13.919 | 13.845 | 13.765 | 13.678 | 13.584 | 13.086 | 11.913 | 10.76 | 9.6 | Primary | 1769
NPgY | BINBROOK | 11 | 33 | WOLD NEWTON | KEADBY | LN8 6DR | NPg Best View | 5.557 | 5.493 | 5.401 | 5.293 | 5.217 | 5.139 | 5.048 | 4.652 | 3.955 | 3.43 | 2.93 | Primary | 1770
NPgY | BINGLEY 33/11KV | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 2RD | NPg Best View | 10.735 | 10.522 | 10.16 | 9.715 | 9.46 | 9.184 | 8.84 | 7.314 | 3.173 | -0.044 | -3.134 | Primary | 1771
NPgY | BIRKBY | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 5HB | NPg Best View | 11.652 | 11.465 | 11.141 | 10.745 | 10.452 | 10.129 | 9.726 | 7.869 | 4.003 | 1.076 | -1.607 | Primary | 1772
NPgY | BLACKBURN MEADOWS 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1HF | NPg Best View | 9.376 | 9.437 | 9.437 | 9.4 | 9.411 | 9.403 | 9.369 | 9.103 | 7.466 | 6.217 | 5.013 | Primary | 1773
NPgY | BLUE BOY STREET | 11 | 33 | NEEPSEND | NEEPSEND | S3 7BA | NPg Best View | 10.457 | 10.499 | 10.494 | 10.452 | 10.447 | 10.426 | 10.37 | 10.056 | 9.007 | 8.245 | 7.524 | Primary | 1774
NPgY | BOC BRINSWORTH | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1WT | NPg Best View | 17.503 | 17.366 | 17.165 | 16.921 | 16.735 | 16.527 | 16.274 | 15.047 | 13.453 | 12.421 | 11.493 | Primary | 1775
NPgY | BOLTON ROAD | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 0JT | NPg Best View | 7.994 | 22.571 | 22.368 | 22.125 | 21.95 | 21.762 | 21.532 | 20.504 | 17.412 | 14.893 | 12.587 | Primary | 1776
NPgY | BOTTESFORD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN16 3UJ | NPg Best View | 10.832 | 10.501 | 10 | 9.392 | 8.934 | 8.463 | 7.915 | 5.627 | 0.143 | -4.443 | -8.791 | Primary | 1777
NPgY | BRAMHOPE | 11 | 33 | MENSTON | BRADFORD WEST | LS16 9HA | NPg Best View | 3.917 | 3.835 | 3.721 | 3.606 | 3.545 | 3.48 | 3.396 | 3.065 | 2.338 | 1.805 | 1.27 | Primary | 1778
NPgY | BRAMLEY | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS13 3ST | NPg Best View | 6.433 | 5.904 | 5.228 | 4.553 | 4.011 | 3.435 | 2.767 | -0.186 | -5.321 | -9.113 | -12.447 | Primary | 1779
NPgY | BRETT STREET | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 4HW | NPg Best View | 4.745 | 4.46 | 4.021 | 3.494 | 2.924 | 2.32 | 1.615 | -1.626 | -8.008 | -13.303 | -18.167 | Primary | 1780
NPgY | BRIDGES ROAD | 11 | 33 | SCUNTHORPE SOUTH | KEADBY | DN17 1HA | NPg Best View | 6.129 | 5.689 | 5.034 | 4.242 | 3.652 | 3.032 | 2.307 | -0.902 | -7.877 | -13.574 | -18.992 | Primary | 1781
NPgY | BRIGHOUSE 33/11KV | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1QE | NPg Best View | 4.359 | 4.438 | 4.503 | 4.555 | 4.6 | 4.634 | 4.654 | 4.686 | 4.502 | 4.403 | 4.324 | Primary | 1782
NPgY | BRODSWORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN5 7XB | NPg Best View | 8.047 | 7.661 | 7.044 | 6.271 | 5.691 | 5.024 | 4.208 | 0.034 | -6.352 | -10.779 | -14.853 | Primary | 1783
NPgY | BROOKFIELD STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1LD | NPg Best View | 13.097 | 13.21 | 13.304 | 13.371 | 13.427 | 13.468 | 13.492 | 13.523 | 12.778 | 12.245 | 11.789 | Primary | 1784
NPgY | BTP | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN31 2RL | NPg Best View | 10.371 | 10.533 | 10.679 | 10.812 | 10.933 | 11.044 | 11.14 | 11.552 | 11.645 | 11.729 | 11.808 | Primary | 1785
NPgY | BURLEY STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS3 1JY | NPg Best View | 11.241 | 11.419 | 11.548 | 11.66 | 11.771 | 11.862 | 11.921 | 12.133 | 10.478 | 9.162 | 7.956 | Primary | 1786
NPgY | BURMANTOFTS | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 7SS | NPg Best View | 11.817 | 11.91 | 11.971 | 12.015 | 12.066 | 12.108 | 12.132 | 12.238 | 11.651 | 11.194 | 10.756 | Primary | 1787
NPgY | BURNLEYVILLE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | BD19 4RY | NPg Best View | 11.015 | 10.78 | 10.392 | 9.922 | 9.59 | 9.208 | 8.732 | 6.361 | 2.828 | 0.521 | -1.606 | Primary | 1788
NPgY | BURTON PIDSEA | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU12 9AE | NPg Best View | 4.343 | 4.302 | 4.232 | 4.148 | 4.066 | 3.976 | 3.862 | 3.404 | 3.113 | 2.95 | 2.828 | Primary | 1789
NPgY | BURTON ROAD | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 2QG | NPg Best View | 5.37 | 5.407 | 5.406 | 5.391 | 5.368 | 5.334 | 5.278 | 5.018 | 4.459 | 3.945 | 3.427 | Primary | 1790
NPgY | BUSLINGTHORPE GREEN | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 2HG | NPg Best View | 13.932 | 13.586 | 13.121 | 12.648 | 12.323 | 11.972 | 11.542 | 9.617 | 5.224 | 1.816 | -1.309 | Primary | 1791
NPgY | BUTTERWICK | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO17 8HF | NPg Best View | 0.051 | 0.073 | 0.078 | 0.074 | 0.069 | 0.055 | 0.028 | -0.127 | -0.479 | -0.758 | -1.029 | Primary | 1792
NPgY | CAISTOR | 11 | 33 | WOLD NEWTON | KEADBY | LN7 6RE | NPg Best View | 3.379 | 3.218 | 3 | 2.753 | 2.571 | 2.381 | 2.159 | 1.204 | -0.356 | -1.54 | -2.685 | Primary | 1793
NPgY | CALDER WHARF | 11 | 33 | THORNHILL 132kV | ELLAND | WF13 3JQ | NPg Best View | 9.708 | 9.531 | 9.209 | 8.807 | 8.539 | 8.238 | 7.872 | 6.139 | 3.039 | 0.926 | -1.132 | Primary | 1794
NPgY | CARLTON HILL | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS7 1JB | NPg Best View | 9.333 | 9.278 | 9.171 | 9.079 | 9.031 | 8.968 | 8.869 | 8.408 | 6.312 | 4.643 | 3.099 | Primary | 1795
NPgY | CARR LANE | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 4PS | NPg Best View | 5.482 | 5.244 | 4.889 | 4.483 | 4.187 | 3.871 | 3.504 | 1.823 | -1.886 | -4.865 | -7.782 | Primary | 1796
NPgY | CHELKER RESERVOIR | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 0JS | NPg Best View | 4.815 | 4.847 | 4.87 | 4.885 | 4.897 | 4.903 | 4.901 | 4.851 | 4.638 | 4.494 | 4.371 | Primary | 1797
NPgY | CHEVIN END | 11 | 33 | MENSTON | BRADFORD WEST | LS29 6BE | NPg Best View | 22.064 | 21.935 | 21.732 | 21.506 | 21.388 | 21.261 | 21.101 | 20.425 | 17.965 | 15.999 | 14.137 | Primary | 1798
NPgY | CLARENCE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1JE | NPg Best View | 8.036 | 8.13 | 8.186 | 8.227 | 8.288 | 8.338 | 8.369 | 8.479 | 7.396 | 6.528 | 5.694 | Primary | 1799
NPgY | CLARENDON ROAD | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS2 9JT | NPg Best View | 13.705 | 13.479 | 13.181 | 12.907 | 12.731 | 12.539 | 12.291 | 11.219 | 8.4 | 6.171 | 4.13 | Primary | 1800
NPgY | CLARENDON STREET | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 1AP | NPg Best View | 7.384 | 7.419 | 7.369 | 7.258 | 7.188 | 7.095 | 6.953 | 6.227 | 3.609 | 1.558 | -0.339 | Primary | 1801
NPgY | CLAYWHEELS LANE | 11 | 33 | NEEPSEND | NEEPSEND | S6 1LY | NPg Best View | 5.038 | 4.521 | 3.785 | 2.968 | 2.509 | 2.008 | 1.385 | -1.375 | -7.749 | -12.584 | -17.224 | Primary | 1802
NPgY | CLOUGH LANE | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3EH | NPg Best View | 0.971 | 0.943 | 0.904 | 0.856 | 0.809 | 0.757 | 0.697 | 0.385 | -0.253 | -0.795 | -1.322 | Primary | 1803
NPgY | COMMONSIDE LANE | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF7 5DF | NPg Best View | 3.283 | 3.217 | 3.09 | 2.912 | 2.744 | 2.539 | 2.287 | 0.855 | -1.726 | -3.727 | -5.595 | Primary | 1804
NPgY | CONVAMORE ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN32 9PG | NPg Best View | 13.036 | 13.019 | 12.942 | 12.821 | 12.729 | 12.625 | 12.487 | 11.911 | 10.31 | 9.078 | 7.985 | Primary | 1805
NPgY | CONYARD ROAD | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 7LQ | NPg Best View | 14.893 | 14.746 | 15.482 | 15.142 | 14.937 | 14.719 | 14.448 | 13.264 | 9.942 | 7.283 | 4.744 | Primary | 1806
NPgY | CORNWALL STREET | 11 | 132 | CORNWALL STREET | CREYKE BECK | HU8 8AQ | NPg Best View | 22.385 | 22.403 | 22.305 | 22.086 | 21.819 | 21.445 | 20.951 | 17.745 | 13.077 | 10.241 | 7.942 | Primary | 1807
NPgY | CORRINGHAM ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1FT | NPg Best View | 9.893 | 9.653 | 9.292 | 8.869 | 8.524 | 8.161 | 7.742 | 5.863 | 1.974 | -1.186 | -4.214 | Primary | 1808
NPgY | COSTHORPE | 11 | 66 | THURCROFT | THURCROFT | S81 9QR | NPg Best View | 2.488 | 2.286 | 2.01 | 1.687 | 1.486 | 1.269 | 1.011 | -0.175 | -2.427 | -4.165 | -5.934 | Primary | 1809
NPgY | COUNTY ROAD NORTH | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 5DR | NPg Best View | 8.285 | 7.991 | 7.467 | 6.806 | 6.494 | 6.162 | 5.751 | 4.031 | -2.009 | -6.917 | -11.784 | Primary | 1810
NPgY | CRACOE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 6BE | NPg Best View | 6.126 | 3.855 | 3.853 | 3.828 | 3.8 | 3.761 | 3.7 | 3.318 | 2.143 | 1.244 | 0.438 | Primary | 1811
NPgY | CROOKESMOOR ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 3FP | NPg Best View | 7.664 | 7.311 | 6.779 | 6.146 | 5.756 | 5.336 | 4.814 | 2.528 | -2.424 | -6.212 | -9.796 | Primary | 1812
NPgY | CROSSHILLS | 11 | 33 | SILSDEN | BRADFORD WEST | BD20 7AQ | NPg Best View | 4.024 | 3.838 | 18.222 | 17.834 | 17.533 | 17.204 | 16.798 | 14.9 | 10.378 | 6.863 | 3.711 | Primary | 1813
NPgY | CROWLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN17 4BB | NPg Best View | -0.135 | -0.243 | -0.401 | -0.594 | -0.745 | -0.902 | -1.084 | -1.893 | -3.815 | -5.45 | -7.018 | Primary | 1814
NPgY | CROWN STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 2LA | NPg Best View | 2.865 | 2.883 | 2.875 | 2.851 | 2.835 | 2.814 | 2.782 | 2.598 | 1.884 | 1.373 | 0.908 | Primary | 1815
NPgY | DALTON | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD2 1FF | NPg Best View | 10.528 | 10.307 | 9.932 | 9.477 | 9.172 | 8.851 | 8.459 | 6.871 | 3.116 | 0.191 | -2.543 | Primary | 1816
NPgY | DARNALL | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 4JT | NPg Best View | 8.659 | 8.373 | 7.912 | 7.356 | 7.048 | 6.709 | 6.292 | 4.349 | -0.153 | -3.517 | -6.815 | Primary | 1817
NPgY | DEARNE ROAD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DG | NPg Best View | 12.575 | 12.512 | 12.383 | 12.209 | 12.1 | 11.969 | 11.793 | 10.906 | 9.394 | 8.331 | 7.324 | Primary | 1818
NPgY | DEIGHTON | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD2 1UP | NPg Best View | 3.897 | 3.011 | 3.042 | 3.023 | 3.001 | 2.944 | 2.84 | 2.177 | -0.041 | -1.648 | -3.103 | Primary | 1819
NPgY | DENBY DALE ROAD | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF2 7BH | NPg Best View | 15.324 | 15.264 | 15.158 | 15.009 | 14.854 | 14.668 | 14.445 | 13.156 | 11.004 | 9.422 | 7.959 | Primary | 1820
NPgY | DENBY GRANGE | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 4JG | NPg Best View | 4.13 | 4.052 | 3.935 | 3.795 | 3.698 | 3.596 | 3.475 | 2.953 | 1.666 | 0.613 | -0.402 | Primary | 1821
NPgY | DENHOLME | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 4JF | NPg Best View | 2.488 | 2.443 | 2.361 | 2.259 | 2.195 | 2.127 | 2.043 | 1.692 | 0.587 | -0.293 | -1.117 | Primary | 1822
NPgY | DINNINGTON | 11 | 66 | THURCROFT | THURCROFT | S25 3QT | NPg Best View | 15.085 | 14.807 | 14.367 | 13.823 | 13.452 | 13.039 | 12.536 | 10.047 | 5.145 | 1.412 | -2.175 | Primary | 1823
NPgY | DOUGHTY ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN32 0LR | NPg Best View | 2.047 | 1.959 | 1.728 | 1.422 | 1.169 | 0.895 | 0.55 | -1.036 | -5.705 | -9.457 | -12.914 | Primary | 1824
NPgY | DOWKER STREET | 11 | 33 | LINDLEY | ELLAND | HD3 4JB | NPg Best View | 14.834 | 14.781 | 14.634 | 14.457 | 14.371 | 14.279 | 14.175 | 13.72 | 11.572 | 9.894 | 8.236 | Primary | 1825
NPgY | DRAX PRIMARY | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | YO8 6PQ | NPg Best View | 4.747 | 4.668 | 4.557 | 4.425 | 4.314 | 4.197 | 4.061 | 3.462 | 2.268 | 1.304 | 0.397 | Primary | 1826
NPgY | DRIFFIELD | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 5XR | NPg Best View | 7.025 | 6.656 | 6.102 | 5.454 | 4.977 | 4.47 | 3.868 | 1.259 | -3.144 | -6.431 | -9.619 | Primary | 1827
NPgY | DRONFIELD | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S18 2XU | NPg Best View | 12.704 | 12.415 | 11.992 | 11.509 | 11.19 | 10.86 | 10.472 | 8.857 | 5.552 | 2.961 | 0.385 | Primary | 1828
NPgY | DUDLEY HILL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9NW | NPg Best View | 12.946 | 11.314 | 11.207 | 11.017 | 10.829 | 10.559 | 10.199 | 7.909 | 4.889 | 3.226 | 1.87 | Primary | 1829
NPgY | DUNKESWICK | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS17 9LP | NPg Best View | 3.076 | 2.877 | 2.644 | 2.468 | 2.33 | 2.184 | 2.007 | 1.338 | 0.461 | -0.103 | -0.598 | Primary | 1830
NPgY | DURKAR LOW LANE | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF4 3BJ | NPg Best View | 8.135 | 7.546 | 6.731 | 5.804 | 5.192 | 4.554 | 3.819 | 0.675 | -4.946 | -9.161 | -13.29 | Primary | 1831
NPgY | EASINGTON | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0SU | NPg Best View | 8.588 | 8.604 | 8.605 | 8.596 | 8.586 | 8.566 | 8.533 | 8.355 | 8.15 | 7.963 | 7.776 | Primary | 1832
NPgY | EASTFIELD ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LW | NPg Best View | 2.019 | 1.825 | 1.516 | 1.094 | 0.619 | 0.023 | -0.716 | -5.119 | -9.342 | -11.586 | -13.261 | Primary | 1833
NPgY | ECCLESFIELD | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 9YR | NPg Best View | 11.952 | 11.665 | 11.272 | 10.879 | 10.639 | 10.375 | 10.051 | 8.564 | 4.395 | 1.095 | -2.03 | Primary | 1834
NPgY | EDLINGTON | 11 | 66 | THURCROFT | THURCROFT | DN12 1SU | NPg Best View | 9.409 | 9.082 | 8.56 | 7.919 | 7.519 | 7.076 | 6.536 | 3.981 | -0.843 | -4.379 | -7.787 | Primary | 1835
NPgY | EGGBOROUGH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | DN14 0QA | NPg Best View | 0.928 | 0.841 | 0.701 | 0.516 | 0.329 | 0.099 | -0.186 | -1.819 | -3.46 | -4.42 | -5.223 | Primary | 1836
NPgY | ELGAR ROAD | 11 | 33 | HULL WEST | CREYKE BECK | HU4 7NY | NPg Best View | 7.544 | 7.283 | 6.858 | 6.342 | 5.991 | 5.624 | 5.184 | 3.35 | -1.614 | -5.668 | -9.548 | Primary | 1837
NPgY | ELLAND 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX5 9AE | NPg Best View | 0.977 | 0.988 | 0.922 | 0.812 | 0.774 | 0.719 | 0.635 | 0.207 | -1.974 | -3.644 | -5.22 | Primary | 1838
NPgY | ELLIFOOT LANE | 11 | 33 | SALTEND 132/33kV | SALTEND NORTH | HU12 9EB | NPg Best View | 1.491 | 1.492 | 1.493 | 1.493 | 1.493 | 1.492 | 1.491 | 1.483 | 1.467 | 1.452 | 1.437 | Primary | 1839
NPgY | ELLIN STREET 1/3 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 10.537 | 10.606 | 10.612 | 10.588 | 10.596 | 10.598 | 10.584 | 10.584 | 9.067 | 7.844 | 6.651 | Primary | 1840
NPgY | ELLIN STREET 2 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4QZ | NPg Best View | 7.15 | 7.13 | 7.077 | 7.007 | 6.968 | 6.926 | 6.87 | 6.625 | 5.754 | 5.081 | 4.423 | Primary | 1841
NPgY | ELMHIRST LANE 1 | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 8.545 | 8.489 | 8.402 | 8.293 | 8.205 | 8.112 | 7.998 | 7.526 | 6.776 | 6.207 | 5.686 | Primary | 1842
NPgY | ELMHIRST LANE 2 | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S75 4LS | NPg Best View | 3.99 | 3.825 | 3.581 | 3.299 | 3.103 | 2.879 | 2.606 | 1.237 | -1.059 | -2.722 | -4.297 | Primary | 1843
NPgY | ELSECAR | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S74 8AU | NPg Best View | 14.635 | 14.408 | 14.085 | 14.693 | 14.347 | 13.99 | 13.582 | 11.866 | 8.737 | 6.327 | 4.156 | Primary | 1844
NPgY | ENDIKE LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 8AY | NPg Best View | 10.174 | 9.151 | 8.81 | 8.387 | 8.148 | 7.894 | 7.585 | 6.275 | 2.751 | -0.054 | -2.838 | Primary | 1845
NPgY | EPWORTH | 11 | 33 | BLYTON | KEADBY | DN9 1JU | NPg Best View | 3.303 | 3.151 | 2.934 | 2.67 | 2.401 | 2.093 | 1.725 | -0.218 | -2.841 | -4.741 | -6.437 | Primary | 1846
NPgY | FARNLEY CRESCENT | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 5AN | NPg Best View | 11.084 | 10.553 | 9.955 | 9.545 | 9.313 | 9.062 | 8.75 | 7.445 | 3.513 | 0.408 | -2.564 | Primary | 1847
NPgY | FENTON LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6EZ | NPg Best View | 10.843 | 10.825 | 10.774 | 10.702 | 10.655 | 10.601 | 10.535 | 10.179 | 8.772 | 7.48 | 6.188 | Primary | 1848
NPgY | FERRYBRIDGE A 11KV | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF11 8RR | NPg Best View | -2.757 | -3.3 | -4.083 | -5.014 | -5.665 | -6.357 | -7.176 | -10.804 | -18.27 | -24.178 | -29.813 | Primary | 1849
NPgY | FIR TREE LANE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS17 7BZ | NPg Best View | 7.314 | 6.794 | 6.103 | 5.397 | 4.989 | 4.557 | 4.036 | 1.94 | -2.31 | -5.38 | -8.327 | Primary | 1850
NPgY | FIRST AVENUE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU6 9NE | NPg Best View | 5.35 | 5.407 | 5.354 | 5.235 | 5.288 | 5.324 | 5.328 | 5.212 | 2.375 | -0.01 | -2.496 | Primary | 1851
NPgY | FIRTH BROWN | 11 | 33 | SANTON | KEADBY | DN16 1XP | NPg Best View | 17.308 | 14.297 | 14.136 | 13.943 | 13.794 | 13.641 | 13.47 | 12.687 | 10.701 | 8.962 | 7.227 | Primary | 1852
NPgY | FISH DAM LANE | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 3HQ | NPg Best View | 13.938 | 13.926 | 13.88 | 13.805 | 13.718 | 13.609 | 13.47 | 12.659 | 11.314 | 10.325 | 9.414 | Primary | 1853
NPgY | FLIXBOROUGH | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8RR | NPg Best View | 9.699 | 9.532 | 9.298 | 8.994 | 8.66 | 8.256 | 7.772 | 4.939 | 1.57 | -0.786 | -2.894 | Primary | 1854
NPgY | FOLLY HALL | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 3TF | NPg Best View | 12.786 | 12.801 | 12.744 | 12.654 | 12.623 | 12.589 | 12.542 | 12.374 | 10.425 | 8.824 | 7.24 | Primary | 1855
NPgY | FOUR LANE ENDS | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD8 0LJ | NPg Best View | 11.581 | 11.658 | 11.687 | 11.691 | 11.722 | 11.745 | 11.75 | 11.79 | 11.056 | 10.499 | 9.946 | Primary | 1856
NPgY | FOXHILLS | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 8QW | NPg Best View | 4.263 | 4.126 | 3.94 | 3.697 | 3.415 | 3.07 | 2.656 | 0.177 | -2.487 | -4.313 | -5.923 | Primary | 1857
NPgY | FULLERTON ROAD | 11 | 33 | TEMPLEBOROUGH 275/33kV | TEMPLEBOROUGH 275/33kV | S60 1DL | NPg Best View | 16.368 | 16.319 | 16.217 | 16.084 | 16.012 | 15.926 | 15.821 | 15.223 | 13.557 | 12.248 | 10.975 | Primary | 1858
NPgY | FURNESS AVENUE | 11 | 33 | HOLMFIELD | BRADFORD WEST | WF8 3JA | NPg Best View | 10.886 | 10.651 | 10.26 | 9.782 | 9.547 | 9.294 | 8.984 | 7.649 | 3.72 | 0.686 | -2.322 | Primary | 1859
NPgY | GAISBY LANE | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 1BB | NPg Best View | 10.322 | 10.237 | 10.021 | 9.753 | 9.615 | 9.465 | 9.289 | 8.454 | 5.285 | 2.844 | 0.464 | Primary | 1860
NPgY | GIBRALTAR ROAD | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX1 4HL | NPg Best View | 7.182 | 6.895 | 6.416 | 5.82 | 5.433 | 5.003 | 4.467 | 1.952 | -2.722 | -6.055 | -9.163 | Primary | 1861
NPgY | GIBSON LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU14 3HH | NPg Best View | 4.655 | 4.354 | 3.904 | 3.374 | 2.98 | 2.535 | 2 | -0.622 | -5.08 | -8.291 | -11.266 | Primary | 1862
NPgY | GILDERSOME | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 7HW | NPg Best View | 11.821 | 11.848 | 11.826 | 11.765 | 11.679 | 11.543 | 11.342 | 10.052 | 8.914 | 8.445 | 8.153 | Primary | 1863
NPgY | GLEADLESS VALLEY | 11 | 33 | NORTON LEES | NORTON LEES | S14 1FP | NPg Best View | 15.473 | 15.201 | 14.769 | 14.24 | 13.983 | 13.716 | 13.395 | 12.065 | 8.166 | 5.077 | 1.971 | Primary | 1864
NPgY | GOOLE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 6SX | NPg Best View | 9.369 | 8.978 | 8.378 | 7.636 | 7.059 | 6.4 | 5.598 | 1.487 | -4.47 | -8.599 | -12.406 | Primary | 1865
NPgY | GRAINTHORPE | 11 | 33 | WOLD NEWTON | KEADBY | LN11 7JU | NPg Best View | 3.328 | 3.234 | 3.099 | 3.441 | 3.32 | 3.193 | 3.044 | 2.37 | 1.134 | 0.147 | -0.799 | Primary | 1866
NPgY | GREAT COATES | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN37 9PN | NPg Best View | 8.188 | 8.066 | 7.824 | 7.513 | 7.289 | 7.047 | 6.735 | 5.446 | 1.146 | -2.383 | -5.587 | Primary | 1867
NPgY | GREENHILL | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 7RJ | NPg Best View | 4.186 | 4.018 | 3.761 | 3.463 | 3.303 | 3.135 | 2.932 | 2.111 | 0.084 | -1.5 | -3.092 | Primary | 1868
NPgY | GREYFRIARS RD | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 12.359 | 12.378 | 12.36 | 12.322 | 12.301 | 12.27 | 12.223 | 11.962 | 10.936 | 10.073 | 9.212 | Primary | 1869
NPgY | GREYFRIARS ROAD 3/4 | 11 | 33 | DONCASTER CENTRAL | WEST MELTON / THORPE MARSH | DN1 1QN | NPg Best View | 25.344 | 25.32 | 25.266 | 25.194 | 25.144 | 25.09 | 25.028 | 24.73 | 23.539 | 22.538 | 21.556 | Primary | 1870
NPgY | GRIMETHORPE | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S72 7BQ | NPg Best View | 14.658 | 14.529 | 14.348 | 14.131 | 13.93 | 13.709 | 13.447 | 12.218 | 10.751 | 9.771 | 8.94 | Primary | 1871
NPgY | GROVE STREET | 11 | 33 | LINDLEY | ELLAND | HD1 2PB | NPg Best View | 12.755 | 12.841 | 12.896 | 12.927 | 12.964 | 12.994 | 13.009 | 13.052 | 12.087 | 11.314 | 10.593 | Primary | 1872
NPgY | GUARDIAN GLASS | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8GA | NPg Best View | 19.862 | 19.859 | 19.842 | 19.815 | 19.796 | 19.775 | 19.749 | 19.614 | 18.922 | 18.294 | 17.663 | Primary | 1873
NPgY | HACKENTHORPE | 11 | 66 | THURCROFT | THURCROFT | S12 4ET | NPg Best View | 6.878 | 6.668 | 6.321 | 5.897 | 5.663 | 5.414 | 5.109 | 3.857 | 0.9 | -1.294 | -3.455 | Primary | 1874
NPgY | HALIFAX 33/11KV | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX1 1XB | NPg Best View | 22.521 | 22.56 | 22.491 | 22.385 | 22.319 | 22.243 | 22.141 | 21.731 | 19.483 | 17.719 | 16.011 | Primary | 1875
NPgY | HALLAM STREET | 11 | 33 | MENSTON | BRADFORD WEST | LS20 8AG | NPg Best View | 14.626 | 14.589 | 14.485 | 14.348 | 14.324 | 14.296 | 14.256 | 14.035 | 11.69 | 9.763 | 7.875 | Primary | 1876
NPgY | HARDEN | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD16 1BG | NPg Best View | 4.759 | 4.69 | 4.576 | 4.439 | 4.363 | 4.282 | 4.18 | 3.724 | 2.65 | 1.835 | 1.035 | Primary | 1877
NPgY | HARPSWELL | 11 | 33 | BLYTON | KEADBY | DN21 5UT | NPg Best View | 4.52 | 4.495 | 4.452 | 4.4 | 4.345 | 4.284 | 4.209 | 3.838 | 3.52 | 3.312 | 3.132 | Primary | 1878
NPgY | HARWORTH | 11 | 66 | THURCROFT | THURCROFT | DN11 8JW | NPg Best View | 15.749 | 15.712 | 15.607 | 15.456 | 15.336 | 15.192 | 15.015 | 14.046 | 11.596 | 9.679 | 7.845 | Primary | 1879
NPgY | HAWORTH 1 | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD22 9EP | NPg Best View | 9.716 | 9.615 | 9.451 | 9.246 | 9.104 | 8.95 | 8.758 | 7.909 | 5.919 | 4.366 | 2.968 | Primary | 1880
NPgY | HAWORTH 2 | 11 | 33 | SILSDEN | BRADFORD WEST | BD22 9EP | NPg Best View | 11.566 | 11.493 | 11.37 | 11.218 | 11.131 | 11.039 | 10.926 | 10.442 | 8.845 | 7.555 | 6.345 | Primary | 1881
NPgY | HAXEY | 11 | 33 | BLYTON | KEADBY | DN9 2LT | NPg Best View | 2.373 | 2.259 | 2.103 | 1.931 | 1.767 | 1.595 | 1.395 | 0.512 | -1.095 | -2.449 | -3.697 | Primary | 1882
NPgY | HAYTON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO42 1RJ | NPg Best View | 3.519 | 3.352 | 3.086 | 2.756 | 2.549 | 2.313 | 2.036 | 0.486 | -3.511 | -6.718 | -9.904 | Primary | 1883
NPgY | HAZLEHEAD | 11 | 33 | THORNHILL 132kV | ELLAND | S36 4HG | NPg Best View | 18.951 | 18.941 | 18.911 | 18.865 | 18.824 | 18.767 | 18.694 | 18.242 | 17.636 | 17.257 | 16.923 | Primary | 1884
NPgY | HEBDEN BRIDGE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 6LX | NPg Best View | 4.87 | 4.808 | 4.708 | 4.591 | 4.511 | 4.429 | 4.329 | 3.909 | 2.668 | 1.653 | 0.708 | Primary | 1885
NPgY | HEDLEY CHASE | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS12 1YN | NPg Best View | 14.853 | 14.864 | 14.854 | 14.835 | 14.827 | 14.808 | 14.772 | 14.506 | 13.481 | 12.679 | 11.945 | Primary | 1886
NPgY | HEDON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 8ED | NPg Best View | 12.716 | 12.838 | 12.938 | 13.017 | 13.096 | 13.159 | 13.204 | 13.328 | 13.033 | 12.856 | 12.696 | Primary | 1887
NPgY | HEMSWORTH | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 5BZ | NPg Best View | 2.315 | 2.068 | 1.718 | 1.289 | 0.977 | 0.637 | 0.224 | -1.688 | -4.322 | -6.157 | -7.846 | Primary | 1888
NPgY | HESSLE ROAD 1 | 11 | 33 | HULL SOUTH | CREYKE BECK | HU4 6SP | NPg Best View | 5.923 | 5.904 | 5.848 | 5.778 | 5.724 | 5.667 | 5.602 | 5.294 | 4.292 | 3.501 | 2.73 | Primary | 1889
NPgY | HESSLE ROAD 2 | 11 | 33 | HULL WEST | CREYKE BECK | HU4 6SP | NPg Best View | 5.291 | 5.262 | 5.19 | 5.096 | 5.019 | 4.923 | 4.804 | 4.142 | 3.052 | 2.306 | 1.61 | Primary | 1890
NPgY | HIBALDSTOW | 11 | 33 | SANTON | KEADBY | DN21 4NH | NPg Best View | 5.32 | 5.046 | 4.646 | 4.172 | 3.817 | 3.437 | 2.986 | 0.884 | -3.03 | -6.075 | -8.956 | Primary | 1891
NPgY | HICKLETON | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | S63 0DE | NPg Best View | 15.359 | 15.3 | 15.191 | 15.054 | 14.964 | 14.869 | 14.76 | 14.22 | 12.439 | 10.986 | 9.58 | Primary | 1892
NPgY | HILLCREST | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS8 3AA | NPg Best View | 8.468 | 8.063 | 7.523 | 6.977 | 6.569 | 6.133 | 5.594 | 3.296 | -1.716 | -5.69 | -9.321 | Primary | 1893
NPgY | HOLBECK | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9SZ | NPg Best View | 4.973 | 4.958 | 4.852 | 4.722 | 4.608 | 4.47 | 4.295 | 3.377 | 0.237 | -2.192 | -4.431 | Primary | 1894
NPgY | HOLDERNESS | 11 | 33 | BRANSHOLME | CREYKE BECK | HU9 4AU | NPg Best View | 10.498 | 10.272 | 9.872 | 9.359 | 9.056 | 8.735 | 8.346 | 6.67 | 1.127 | -3.466 | -7.883 | Primary | 1895
NPgY | HOLME UPON SPALDING MOOR | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 4BX | NPg Best View | 0.294 | 0.24 | 0.15 | 0.031 | -0.05 | -0.144 | -0.253 | -0.857 | -2.375 | -3.609 | -4.805 | Primary | 1896
NPgY | HONLEY | 11 | 33 | LINDLEY | ELLAND | HD9 6RU | NPg Best View | 13.544 | 13.311 | 12.943 | 12.515 | 12.222 | 11.907 | 11.52 | 9.826 | 6.173 | 3.382 | 0.758 | Primary | 1897
NPgY | HOPE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S33 6RP | NPg Best View | 18.454 | 18.461 | 18.448 | 18.421 | 18.396 | 18.365 | 18.326 | 18.116 | 17.263 | 16.602 | 15.999 | Primary | 1898
NPgY | HORBURY | 11 | 33 | THORNHILL 132kV | ELLAND | WF4 6EU | NPg Best View | 12.653 | 12.461 | 12.18 | 11.862 | 11.698 | 11.524 | 11.332 | 10.41 | 7.684 | 5.397 | 2.994 | Primary | 1899
NPgY | HOUGHTON MAIN | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S72 0GX | NPg Best View | 7.199 | 7.11 | 6.957 | 6.764 | 6.594 | 6.409 | 6.191 | 5.09 | 2.373 | 0.145 | -1.921 | Primary | 1900
NPgY | HULL EAST 33/11KV | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5NP | NPg Best View | 8.315 | 8.219 | 8.016 | 7.73 | 7.511 | 7.235 | 6.89 | 4.783 | 0.486 | -2.774 | -5.812 | Primary | 1901
NPgY | HUMBER ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 3LZ | NPg Best View | 16.398 | 16.405 | 16.406 | 16.404 | 16.396 | 16.383 | 16.363 | 16.235 | 16.061 | 15.873 | 15.684 | Primary | 1902
NPgY | HUNMANBY | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO14 0JY | NPg Best View | 17.021 | 16.971 | 16.866 | 16.722 | 16.607 | 16.482 | 16.322 | 15.616 | 13.879 | 12.527 | 11.29 | Primary | 1903
NPgY | ICI FIBRES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4LT | NPg Best View | 19.011 | 18.983 | 18.932 | 18.867 | 18.822 | 18.775 | 18.721 | 18.485 | 17.537 | 16.726 | 15.953 | Primary | 1904
NPgY | IDLE | 11 | 33 | BRADFORD | BRADFORD WEST | BD10 8SA | NPg Best View | 9.355 | 8.939 | 8.414 | 7.96 | 7.721 | 7.465 | 7.151 | 5.875 | 2.12 | -0.786 | -3.643 | Primary | 1905
NPgY | ILKLEY | 11 | 33 | SILSDEN | BRADFORD WEST | LS29 9BE | NPg Best View | 10.639 | 10.31 | 9.838 | 9.323 | 9.023 | 8.701 | 8.299 | 6.522 | 2.331 | -0.908 | -4.013 | Primary | 1906
NPgY | INGS LANE | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 1UP | NPg Best View | -6.381 | -6.22 | -6.095 | -5.995 | -5.908 | -5.842 | -5.805 | -5.728 | -6.108 | -6.312 | -6.473 | Primary | 1907
NPgY | IVESON HOUSE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 6RF | NPg Best View | 10.452 | 9.946 | 9.322 | 8.79 | 8.439 | 8.07 | 7.624 | 5.76 | 0.528 | -3.694 | -7.667 | Primary | 1908
NPgY | JARRATT STREET | 11 | 33 | MALLARD WAY | WEST MELTON / THORPE MARSH | DN1 2BS | NPg Best View | 11.458 | 11.373 | 11.204 | 10.977 | 10.798 | 10.586 | 10.329 | 8.857 | 5.625 | 3.174 | 0.85 | Primary | 1909
NPgY | KEDDINGTON ROAD | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0DE | NPg Best View | 5.286 | 5.035 | 4.671 | 4.247 | 3.94 | 3.626 | 3.265 | 1.756 | -1.602 | -4.336 | -6.996 | Primary | 1910
NPgY | KEIGHLEY | 11 | 132 | KEIGHLEY | BRADFORD WEST | BD21 5AJ | NPg Best View | 24.545 | 24.56 | 24.486 | 24.363 | 24.327 | 24.285 | 24.224 | 23.926 | 21.214 | 19.024 | 16.91 | Primary | 1911
NPgY | KENMORE ROAD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF2 0XE | NPg Best View | 6.616 | 6.496 | 6.294 | 6.04 | 5.849 | 5.632 | 5.368 | 4.075 | 1.68 | -0.198 | -2.023 | Primary | 1912
NPgY | KILLINGHALL ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD3 8HN | NPg Best View | 6.771 | 6.766 | 6.752 | 6.734 | 6.725 | 6.715 | 6.701 | 6.641 | 6.473 | 6.346 | 6.226 | Primary | 1913
NPgY | KILNHURST | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S64 5TL | NPg Best View | 11.781 | 11.293 | 10.548 | 9.656 | 9.148 | 8.611 | 7.975 | 5.207 | -1.253 | -6.322 | -11.407 | Primary | 1914
NPgY | KING GEORGE DOCK | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU9 5PL | NPg Best View | 22.024 | 22.052 | 22.035 | 21.966 | 21.85 | 21.669 | 21.42 | 19.719 | 18.398 | 17.949 | 17.743 | Primary | 1915
NPgY | KIRK DRIVE | 11 | 33 | MENSTON | BRADFORD WEST | BD17 6SA | NPg Best View | 11.36 | 11.18 | 10.861 | 10.476 | 10.252 | 10.012 | 9.718 | 8.446 | 4.877 | 2.139 | -0.5 | Primary | 1916
NPgY | KIRK SANDALL | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 1QP | NPg Best View | 12.122 | 12.005 | 11.783 | 11.473 | 11.075 | 10.575 | 9.96 | 6.252 | 1.894 | -0.767 | -2.893 | Primary | 1917
NPgY | KIRKBURN | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO25 9EH | NPg Best View | 0.812 | 0.753 | 0.65 | 0.515 | 0.391 | 0.249 | 0.073 | -0.842 | -2.386 | -3.564 | -4.658 | Primary | 1918
NPgY | KIVETON PARK | 11 | 66 | THURCROFT | THURCROFT | S26 6RP | NPg Best View | 7.15 | 1.462 | 1.177 | 0.837 | 0.592 | 0.33 | 0.018 | -1.358 | -3.784 | -5.6 | -7.318 | Primary | 1919
NPgY | WETHERBY | 11 | 33 | BRAMHAM | FERRYBRIDGE B | TBC | NPg Best View | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 1920
NPgY | LEA ROAD | 11 | 33 | BLYTON | KEADBY | DN21 1ND | NPg Best View | 5.149 | 4.942 | 4.638 | 4.279 | 4.042 | 3.791 | 3.493 | 2.157 | -0.594 | -2.816 | -5.036 | Primary | 1921
NPgY | LEASOWE ROAD | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 2EY | NPg Best View | 12.975 | 12.801 | 12.5 | 12.105 | 11.697 | 11.18 | 10.53 | 6.674 | 2.35 | -0.042 | -1.929 | Primary | 1922
NPgY | LEDSTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF10 2AX | NPg Best View | 2.43 | 2.265 | 1.968 | 1.631 | 1.431 | 1.203 | 0.912 | -0.399 | -3.286 | -5.326 | -7.27 | Primary | 1923
NPgY | LEEDS ROAD | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS22 5AA | NPg Best View | 2.36 | 2.216 | 2.026 | 1.858 | 1.767 | 1.669 | 1.545 | 1.078 | -0.005 | -0.796 | -1.587 | Primary | 1924
NPgY | LEGRAMS MILL LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 2BA | NPg Best View | 13.041 | 12.933 | 12.717 | 12.441 | 12.315 | 12.176 | 11.997 | 11.172 | 8.54 | 6.513 | 4.542 | Primary | 1925
NPgY | LEYLANDS ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS2 7QB | NPg Best View | 8.012 | 8.111 | 8.181 | 8.235 | 8.285 | 8.325 | 8.347 | 8.425 | 7.25 | 6.326 | 5.491 | Primary | 1926
NPgY | LIVERSEDGE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF15 7NY | NPg Best View | 13.619 | 13.576 | 13.454 | 13.283 | 13.228 | 13.164 | 13.079 | 12.619 | 10.27 | 8.417 | 6.585 | Primary | 1927
NPgY | LOUTH | 11 | 33 | WOLD NEWTON | KEADBY | LN11 0WA | NPg Best View | 7.295 | 7.006 | 6.592 | 6.095 | 5.703 | 5.28 | 4.769 | 2.378 | -1.477 | -4.516 | -7.389 | Primary | 1928
NPgY | LOW MOOR | 11 | 33 | STAYGATE | SKELTON GRANGE | BD12 0NG | NPg Best View | 12.827 | 12.806 | 12.706 | 12.54 | 12.404 | 12.206 | 11.938 | 10.156 | 7.852 | 6.544 | 5.436 | Primary | 1929
NPgY | LOWFIELDS | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HX5 9DE | NPg Best View | 13.811 | 13.87 | 13.921 | 13.962 | 14.002 | 14.037 | 14.066 | 14.18 | 14.033 | 13.918 | 13.81 | Primary | 1930
NPgY | LOXLEY ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 6SJ | NPg Best View | 5.932 | 5.925 | 5.905 | 5.88 | 5.872 | 5.861 | 5.842 | 5.755 | 5.54 | 5.38 | 5.208 | Primary | 1931
NPgY | MANCHESTER ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD5 0QL | NPg Best View | 14.239 | 14.294 | 14.318 | 14.319 | 14.325 | 14.327 | 14.319 | 14.282 | 13.19 | 12.337 | 11.562 | Primary | 1932
NPgY | MANSFIELD ROAD 1 | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S12 2DL | NPg Best View | -3.98 | -4.222 | -4.621 | -5.112 | -5.385 | -5.674 | -6.022 | -7.514 | -11.147 | -13.892 | -16.563 | Primary | 1933
NPgY | MANSFIELD ROAD 2 | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S12 2DL | NPg Best View | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | Primary | 1934
NPgY | MARKHAM GATES | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 2FS | NPg Best View | 9.064 | 8.04 | 7.494 | 6.848 | 6.427 | 5.988 | 5.473 | 3.297 | -2.329 | -6.878 | -11.214 | Primary | 1935
NPgY | MARMION ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S11 8TS | NPg Best View | 9.131 | 8.651 | 7.957 | 7.187 | 12.787 | 12.362 | 11.84 | 9.599 | 4.247 | 0.138 | -3.965 | Primary | 1936
NPgY | MARSDEN ROAD | 11 | 33 | MOSS ROAD | GRIMSBY WEST | DN31 3SQ | NPg Best View | 4.119 | 4.242 | 4.324 | 4.376 | 4.406 | 4.423 | 4.418 | 4.346 | 2.686 | 1.305 | 0.063 | Primary | 1937
NPgY | MARTONGATE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO16 6RX | NPg Best View | 2.366 | 2.122 | 1.763 | 1.334 | 0.903 | 0.459 | -0.056 | -2.172 | -6.861 | -10.827 | -14.402 | Primary | 1938
NPgY | MELTHAM | 11 | 33 | LINDLEY | ELLAND | HD9 4AL | NPg Best View | 14.475 | 14.345 | 14.127 | 13.869 | 13.692 | 13.503 | 13.27 | 12.28 | 9.269 | 6.821 | 4.54 | Primary | 1939
NPgY | MEXBOROUGH 1_2 | 11 | 66 | THURCROFT | THURCROFT | S64 0JD | NPg Best View | 5.721 | 5.294 | 4.618 | 3.793 | 3.299 | 2.766 | 2.124 | -0.772 | -6.567 | -10.932 | -15.31 | Primary | 1940
NPgY | MIDDLETON TOWN STREET | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS10 3TQ | NPg Best View | 5.304 | 4.385 | 4.082 | 3.758 | 3.533 | 3.277 | 2.951 | 1.468 | -2.06 | -4.716 | -7.203 | Primary | 1941
NPgY | MILLHOUSES | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S7 2QH | NPg Best View | 15.155 | 15.029 | 14.823 | 14.583 | 14.466 | 14.341 | 14.184 | 13.525 | 11.484 | 9.856 | 8.229 | Primary | 1942
NPgY | MILLROYD STREET | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | HD6 1JZ | NPg Best View | 4.258 | 4.023 | 3.636 | 3.167 | 2.895 | 2.593 | 2.218 | 0.438 | -3.485 | -6.407 | -9.24 | Primary | 1943
NPgY | MILTON PLACE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF5 9EG | NPg Best View | 7.94 | 7.737 | 7.412 | 7.021 | 6.716 | 6.381 | 5.997 | 4.059 | 0.255 | -2.636 | -5.447 | Primary | 1944
NPgY | MIRFIELD | 11 | 33 | THORNHILL 132kV | ELLAND | WF14 8NF | NPg Best View | 9.036 | 8.678 | 8.131 | 7.477 | 7.087 | 6.674 | 6.182 | 4.103 | -0.069 | -3.076 | -6.048 | Primary | 1945
NPgY | MONCKTON | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | S71 4BG | NPg Best View | 6.912 | 6.643 | 6.266 | 5.825 | 5.475 | 5.108 | 4.676 | 2.867 | 0.068 | -1.99 | -3.842 | Primary | 1946
NPgY | MOOR ROAD | 11 | 33 | LEEDS NORTH | SKELTON GRANGE | LS6 4BJ | NPg Best View | 2.732 | 2.213 | 1.555 | 0.951 | 0.536 | 0.088 | -0.474 | -2.93 | -9.41 | -14.582 | -19.23 | Primary | 1947
NPgY | MOORSIDE ROAD | 11 | 33 | BRADFORD | BRADFORD WEST | BD2 3RJ | NPg Best View | 9.873 | 9.452 | 8.859 | 8.247 | 7.94 | 7.616 | 7.22 | 5.57 | 0.862 | -2.811 | -6.443 | Primary | 1948
NPgY | MORLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS27 9HS | NPg Best View | 10.839 | 10.448 | 9.902 | 9.333 | 8.929 | 8.471 | 7.901 | 5.119 | 0.396 | -2.927 | -5.978 | Primary | 1949
NPgY | MOUNT STREET | 11 | 33 | BRADFORD | BRADFORD WEST | BD4 8TB | NPg Best View | 13.452 | 13.474 | 13.431 | 13.331 | 13.237 | 13.101 | 12.915 | 11.71 | 9.592 | 8.286 | 7.189 | Primary | 1950
NPgY | MYTHOLMROYD | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX7 8NE | NPg Best View | 8.851 | 8.76 | 8.598 | 8.406 | 8.269 | 8.124 | 7.949 | 7.178 | 5.057 | 3.374 | 1.803 | Primary | 1951
NPgY | NAB LANE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 9NE | NPg Best View | 3.595 | 3.551 | 3.421 | 3.25 | 3.116 | 2.952 | 2.747 | 1.61 | -0.22 | -1.357 | -2.399 | Primary | 1952
NPgY | NABWOOD | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD18 4AA | NPg Best View | 12.966 | 12.79 | 12.493 | 12.132 | 11.921 | 11.7 | 11.43 | 10.312 | 7.2 | 4.752 | 2.397 | Primary | 1953
NPgY | NATIONAL AVENUE | 11 | 33 | HULL SOUTH | CREYKE BECK | HU5 4JN | NPg Best View | 17.652 | 17.589 | 17.459 | 17.283 | 17.156 | 17.018 | 16.842 | 16.086 | 14.292 | 12.866 | 11.548 | Primary | 1954
NPgY | NEW DROPPINGWELL ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S61 2DL | NPg Best View | 15.479 | 15.397 | 15.245 | 15.056 | 14.964 | 14.869 | 14.76 | 14.252 | 12.101 | 10.329 | 8.527 | Primary | 1955
NPgY | NEW ORCHARD LANE | 11 | 66 | THURCROFT | THURCROFT | S66 9HY | NPg Best View | 4.175 | 4.019 | 3.76 | 3.41 | 3.058 | 2.618 | 2.078 | -1.19 | -5.309 | -7.908 | -10.156 | Primary | 1956
NPgY | NEWHALL ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 2RS | NPg Best View | 10.21 | 10.289 | 10.321 | 10.318 | 10.324 | 10.314 | 10.281 | 10.044 | 8.562 | 7.47 | 6.477 | Primary | 1957
NPgY | NEWPORT 1 | 11 | 33 | HULL WEST | CREYKE BECK | HU15 2QU | NPg Best View | -1.162 | -1.235 | -1.365 | -1.532 | -1.647 | -1.784 | -1.953 | -2.921 | -4.895 | -6.369 | -7.765 | Primary | 1958
NPgY | NEWPORT 2 | 11 | 33 | OSGODBY 3/4 | DRAX | HU15 2QU | NPg Best View | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Primary | 1959
NPgY | NINELANDS LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS25 2PE | NPg Best View | 6.951 | 6.542 | 5.973 | 5.368 | 5.01 | 4.615 | 4.128 | 1.893 | -2.344 | -5.426 | -8.49 | Primary | 1960
NPgY | NORFOLK PARK | 11 | 33 | NORTON LEES | NORTON LEES | S2 3UU | NPg Best View | 14.402 | 14.127 | 13.703 | 13.187 | 12.926 | 12.648 | 12.314 | 10.847 | 7.014 | 3.99 | 0.953 | Primary | 1961
NPgY | NORMANBY | 11 | 33 | BLYTON | KEADBY | LN8 2HQ | NPg Best View | 3.504 | 3.389 | 3.224 | 3.03 | 2.901 | 2.767 | 2.609 | 1.909 | 0.347 | -0.935 | -2.206 | Primary | 1962
NPgY | NORMANTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF6 2JA | NPg Best View | 8.857 | 8.555 | 8.079 | 7.441 | 6.8 | 5.996 | 5.013 | -0.96 | -7.866 | -12.042 | -15.651 | Primary | 1963
NPgY | NORTH AVENUE | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1SX | NPg Best View | 13.237 | 12.845 | 12.338 | 11.851 | 11.537 | 11.207 | 10.811 | 9.098 | 5.183 | 2.164 | -0.733 | Primary | 1964
NPgY | NORTH THORESBY | 11 | 33 | WOLD NEWTON | KEADBY | DN36 5SB | NPg Best View | 5.085 | 5.011 | 4.902 | 4.776 | 4.68 | 4.582 | 4.468 | 3.988 | 2.854 | 1.914 | 1.029 | Primary | 1965
NPgY | NORWOOD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 9JR | NPg Best View | 6.862 | 6.516 | 5.999 | 5.379 | 4.976 | 4.554 | 4.058 | 1.926 | -3.504 | -7.94 | -12.32 | Primary | 1966
NPgY | OAKES ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 3EW | NPg Best View | 10.267 | 10.061 | 9.706 | 9.261 | 9 | 8.721 | 8.379 | 6.926 | 2.52 | -0.989 | -4.288 | Primary | 1967
NPgY | OAKWOOD LANE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 3LF | NPg Best View | 15.023 | 14.78 | 14.459 | 14.127 | 13.916 | 13.691 | 13.411 | 12.28 | 9.349 | 7 | 4.822 | Primary | 1968
NPgY | ODSAL | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 1BW | NPg Best View | 6.499 | 6.351 | 6.046 | 5.656 | 5.439 | 5.202 | 4.913 | 3.65 | -0.078 | -2.916 | -5.678 | Primary | 1969
NPgY | OLYMPIA MILLS | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 7AG | NPg Best View | 14.137 | 13.84 | 13.428 | 12.946 | 12.48 | 11.977 | 11.383 | 8.592 | 4.165 | 0.729 | -2.391 | Primary | 1970
NPgY | ORGREAVE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 9NA | NPg Best View | 13.149 | 13.123 | 13.051 | 12.958 | 12.907 | 12.853 | 12.791 | 12.516 | 11.147 | 10.027 | 8.921 | Primary | 1971
NPgY | OUTWOOD | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | WF3 3TA | NPg Best View | 9.366 | 9.084 | 8.659 | 8.169 | 7.845 | 7.482 | 7.043 | 4.987 | 1.695 | -0.607 | -2.861 | Primary | 1972
NPgY | PARK HILL | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S2 5QY | NPg Best View | 12.483 | 12.52 | 12.491 | 12.418 | 12.338 | 12.221 | 12.061 | 11.086 | 9.55 | 8.642 | 7.874 | Primary | 1973
NPgY | PARK ROAD | 11 | 33 | THORNHILL 132kV | ELLAND | WF12 9LW | NPg Best View | 7.004 | 6.979 | 6.841 | 6.63 | 6.486 | 6.295 | 6.043 | 4.54 | 1.651 | -0.241 | -1.99 | Primary | 1974
NPgY | PARK STREET | 11 | 132 | PARK STREET | WEST MELTON / THORPE MARSH | S61 1TF | NPg Best View | 25.712 | 25.645 | 25.498 | 25.299 | 25.117 | 24.896 | 24.62 | 23.101 | 20.993 | 19.579 | 18.293 | Primary | 1975
NPgY | PASTURE ROAD SOUTH | 11 | 33 | SANTON | KEADBY | DN18 5RX | NPg Best View | 4.647 | 4.499 | 4.293 | 4.043 | 3.85 | 3.638 | 3.395 | 2.029 | -1.448 | -4.528 | -7.523 | Primary | 1976
NPgY | PATRINGTON ROAD | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU12 0AD | NPg Best View | 1.917 | 1.903 | 1.866 | 1.818 | 1.779 | 1.735 | 1.677 | 1.427 | 1.029 | 0.707 | 0.389 | Primary | 1977
NPgY | PENISTONE | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 6BG | NPg Best View | 12.58 | 12.342 | 12.001 | 11.61 | 11.354 | 11.084 | 10.763 | 9.309 | 5.901 | 3.183 | 0.513 | Primary | 1978
NPgY | PENISTONE ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 2FL | NPg Best View | 10.245 | 10.273 | 10.256 | 10.204 | 10.195 | 10.172 | 10.125 | 9.795 | 8.352 | 7.256 | 6.21 | Primary | 1979
NPgY | PLANGEO | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 6EG | NPg Best View | 10.347 | 10.314 | 10.171 | 9.962 | 9.838 | 9.705 | 9.546 | 8.761 | 3.943 | -0.153 | -4.02 | Primary | 1980
NPgY | POLLINGTON | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | DN14 0RR | NPg Best View | 0.762 | 0.717 | 0.635 | 0.526 | 0.428 | 0.312 | 0.174 | -0.59 | -1.979 | -3.021 | -4.012 | Primary | 1981
NPgY | PONTEFRACT LANE 1/2 | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 0JG | NPg Best View | 9.52 | 9.555 | 9.499 | 9.335 | 9.076 | 8.697 | 8.19 | 4.837 | 1.07 | -0.882 | -2.267 | Primary | 1982
NPgY | POOL | 11 | 33 | MENSTON | BRADFORD WEST | LS21 1RP | NPg Best View | 16.516 | 16.504 | 16.46 | 16.407 | 16.38 | 16.339 | 16.274 | 15.921 | 14.924 | 14.208 | 13.542 | Primary | 1983
NPgY | PRINCE OF WALES | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF8 4PR | NPg Best View | 9.078 | 7.997 | 7.545 | 7.004 | 6.609 | 6.193 | 5.706 | 3.498 | -1.593 | -5.749 | -9.74 | Primary | 1984
NPgY | PROSPECT ROAD | 11 | 33 | LINDLEY | ELLAND | HD3 4UY | NPg Best View | 12.307 | 12.249 | 12.111 | 11.93 | 11.822 | 11.703 | 11.545 | 10.911 | 8.903 | 7.3 | 5.82 | Primary | 1985
NPgY | QUEENS ROAD | 11 | 33 | IMMINGHAM | GRIMSBY WEST | DN40 2LZ | NPg Best View | 18.236 | 18.321 | 18.289 | 18.137 | 17.881 | 17.481 | 16.92 | 13.174 | 9.961 | 8.707 | 8.015 | Primary | 1986
NPgY | QUEENSBURY | 11 | 33 | HOLMFIELD | BRADFORD WEST | HX3 7TJ | NPg Best View | 10.343 | 10.063 | 9.582 | 8.987 | 8.701 | 8.381 | 7.976 | 6.102 | 1.019 | -2.851 | -6.649 | Primary | 1987
NPgY | RAWCLIFFE | 11 | 66 | CAMBLESFORTH | CAMBLESFORTH | DN14 8PQ | NPg Best View | 4.331 | 4.288 | 4.219 | 4.134 | 4.079 | 4.019 | 3.945 | 3.611 | 2.93 | 2.386 | 1.851 | Primary | 1988
NPgY | RAWDON | 11 | 33 | RODLEY | SKELTON GRANGE | LS19 7BZ | NPg Best View | 9.586 | 9.327 | 8.935 | 8.517 | 8.308 | 8.084 | 7.808 | 6.574 | 2.828 | -0.039 | -2.787 | Primary | 1989
NPgY | RAWMARSH ROAD 1_2 | 11 | 132 | RAWMARSH ROAD 1_2 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 15.33 | 15.229 | 15.003 | 14.728 | 14.496 | 14.248 | 13.963 | 12.613 | 9.178 | 6.401 | 3.691 | Primary | 1990
NPgY | RAWMARSH ROAD 3_4 | 11 | 132 | RAWMARSH ROAD 3_4 | WEST MELTON / THORPE MARSH | S60 1RR | NPg Best View | 13.798 | 13.736 | 13.56 | 13.31 | 13.108 | 12.877 | 12.604 | 11.17 | 6.783 | 3.148 | -0.385 | Primary | 1991
NPgY | RAWSON ROAD | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD1 3SH | NPg Best View | 13.431 | 13.464 | 13.447 | 13.405 | 13.364 | 13.312 | 13.239 | 12.855 | 11.516 | 10.583 | 9.757 | Primary | 1992
NPgY | RAWSON SPRING ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 1PD | NPg Best View | 8.21 | 8.273 | 8.276 | 8.251 | 8.275 | 8.294 | 8.301 | 8.357 | 7.082 | 6.018 | 4.953 | Primary | 1993
NPgY | REVILL LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S13 7QX | NPg Best View | 17.608 | 17.499 | 17.322 | 17.105 | 16.976 | 16.837 | 16.67 | 15.954 | 14.528 | 13.507 | 12.503 | Primary | 1994
NPgY | ROCKWARE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4RH | NPg Best View | 5.941 | 5.988 | 6.011 | 6.009 | 5.987 | 5.941 | 5.863 | 5.329 | 4.528 | 3.888 | 3.296 | Primary | 1995
NPgY | RODLEY LANE | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 1LJ | NPg Best View | 2.383 | 2.008 | 1.484 | 0.949 | 0.658 | 0.349 | -0.03 | -1.632 | -6.148 | -9.664 | -13.046 | Primary | 1996
NPgY | ROMAN AVENUE | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS8 2DY | NPg Best View | 12.875 | 12.599 | 12.212 | 11.808 | 11.545 | 11.27 | 10.94 | 9.58 | 5.997 | 3.182 | 0.548 | Primary | 1997
NPgY | ROYDS LANE | 11 | 33 | WAKEFIELD NORTH | SKELTON GRANGE | LS26 0BE | NPg Best View | 10.209 | 9.807 | 9.203 | 8.527 | 8.128 | 7.674 | 7.107 | 4.33 | -1.065 | -4.844 | -8.386 | Primary | 1998
NPgY | SAINT ANDREWS ROAD 33/11KV | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD1 6SE | NPg Best View | 11.662 | 11.696 | 11.66 | 11.581 | 11.466 | 11.307 | 11.097 | 9.82 | 8.211 | 7.376 | 6.75 | Primary | 1999
NPgY | SAINT STREET | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD7 4EH | NPg Best View | 16.117 | 15.95 | 15.679 | 15.341 | 15.177 | 15.001 | 14.779 | 13.81 | 11.316 | 9.398 | 7.522 | Primary | 2000
NPgY | SALTERFORTH | 11 | 33 | SILSDEN | BRADFORD WEST | BB18 6JD | NPg Best View | 12.95 | 12.889 | 12.739 | 12.538 | 12.371 | 12.194 | 11.973 | 11.006 | 8.086 | 5.764 | 3.693 | Primary | 2001
NPgY | SALTERHEBBLE | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX3 0QH | NPg Best View | 9.514 | 9.319 | 8.97 | 8.532 | 8.256 | 7.939 | 7.538 | 5.575 | 1.801 | -0.848 | -3.348 | Primary | 2002
NPgY | SALTSHOUSE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU8 9HR | NPg Best View | 11.609 | 9.906 | 9.751 | 9.537 | 9.429 | 9.312 | 9.158 | 8.536 | 6.086 | 4.09 | 2.147 | Primary | 2003
NPgY | SANDHILL LANE | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | YO41 4DF | NPg Best View | 5.239 | 5.171 | 5.073 | 4.963 | 4.875 | 4.784 | 4.673 | 4.2 | 3.322 | 2.64 | 1.999 | Primary | 2004
NPgY | SAXON ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S8 0XQ | NPg Best View | 14.435 | 14.086 | 13.579 | 12.988 | 12.629 | 12.246 | 11.776 | 9.678 | 5.361 | 2.022 | -1.246 | Primary | 2005
NPgY | SCARTHO | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN33 3JL | NPg Best View | 3.279 | 3.043 | 2.613 | 2.082 | 1.716 | 1.327 | 0.844 | -1.159 | -6.858 | -11.416 | -15.624 | Primary | 2006
NPgY | SCHOLES | 11 | 33 | THORNHILL 132kV | ELLAND | HD9 1UG | NPg Best View | 14.971 | 14.766 | 14.447 | 14.08 | 13.864 | 13.627 | 13.33 | 12.019 | 9.202 | 7.074 | 5.001 | Primary | 2007
NPgY | SCISSETT | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | HD8 9UA | NPg Best View | 7.26 | 6.901 | 6.344 | 5.702 | 5.347 | 4.971 | 4.514 | 2.578 | -2.753 | -6.939 | -11.087 | Primary | 2008
NPgY | SCULCOATES A | 11 | 132 | SCULCOATES A | CREYKE BECK | HU5 1DA | NPg Best View | 19.442 | 19.543 | 19.54 | 19.473 | 19.429 | 19.365 | 19.26 | 18.659 | 15.245 | 12.506 | 9.955 | Primary | 2009
NPgY | SEACROFT | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 1LU | NPg Best View | 12.558 | 12.438 | 12.234 | 12.014 | 11.804 | 11.585 | 11.334 | 10.323 | 8.578 | 7.378 | 6.341 | Primary | 2010
NPgY | SEATON | 11 | 66 | DRIFFIELD/BEVERLEY GROUP | CREYKE BECK | HU11 5RQ | NPg Best View | 4.661 | 4.407 | 3.994 | 3.5 | 3.146 | 2.767 | 2.316 | 0.253 | -3.854 | -7.036 | -10.116 | Primary | 2011
NPgY | SELBY | 11 | 33 | OSGODBY 3/4 | DRAX | YO8 8NB | NPg Best View | 9.06 | 8.521 | 7.809 | 6.99 | 6.189 | 5.337 | 4.332 | -0.155 | -6.928 | -12.226 | -16.872 | Primary | 2012
NPgY | SELBY ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS15 0QE | NPg Best View | 4.751 | 4.518 | 4.162 | 3.774 | 3.494 | 3.191 | 2.817 | 1.183 | -3.573 | -7.448 | -11.031 | Primary | 2013
NPgY | SHARLSTON | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF4 1BE | NPg Best View | 13.05 | 12.635 | 12.052 | 11.385 | 10.979 | 10.562 | 10.078 | 8.077 | 3.848 | 0.5 | -2.871 | Primary | 2014
NPgY | SHEPCOTE TINSLEY | 11 | 33 | WINCOBANK | WINCOBANK | S9 1RF | NPg Best View | 20.91 | 17.831 | 17.874 | 17.909 | 17.94 | 17.968 | 17.992 | 18.097 | 17.868 | 17.683 | 17.521 | Primary | 2015
NPgY | SHERBURN | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS25 6PL | NPg Best View | 3.581 | 3.399 | 3.105 | 2.721 | 2.351 | 1.885 | 1.312 | -2.128 | -6.303 | -8.957 | -11.332 | Primary | 2016
NPgY | SHIPLEY | 11 | 33 | BRADFORD | BRADFORD WEST | DN21 5UT | NPg Best View | 13.928 | 13.85 | 13.682 | 13.471 | 13.422 | 13.366 | 13.291 | 12.872 | 10.091 | 7.792 | 5.453 | Primary | 2017
NPgY | SHIRLAND LANE | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3GD | NPg Best View | 14.349 | 14.43 | 14.486 | 14.529 | 14.588 | 14.641 | 14.683 | 14.864 | 14.599 | 14.392 | 14.165 | Primary | 2018
NPgY | SILVER STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 2DU | NPg Best View | 15.728 | 15.784 | 15.813 | 15.823 | 15.847 | 15.866 | 15.875 | 15.899 | 15.185 | 14.616 | 14.067 | Primary | 2019
NPgY | SILVERWOOD | 11 | 66 | THURCROFT | THURCROFT | S65 4PR | NPg Best View | 9.762 | 9.303 | 8.623 | 7.819 | 7.322 | 6.796 | 6.171 | 3.506 | -1.755 | -5.767 | -9.718 | Primary | 2020
NPgY | SKILLINGS LANE | 11 | 33 | HULL WEST | CREYKE BECK | HU15 1EQ | NPg Best View | 14.799 | 14.722 | 14.579 | 14.393 | 14.299 | 14.193 | 14.067 | 13.348 | 10.697 | 8.478 | 6.284 | Primary | 2021
NPgY | SKIPTON | 11 | 33 | SILSDEN | BRADFORD WEST | BD23 2RR | NPg Best View | 6.07 | 6.031 | 5.889 | 5.695 | 5.604 | 5.506 | 5.386 | 4.818 | 1.519 | -1.146 | -3.721 | Primary | 2022
NPgY | SLAITHWAITE | 11 | 33 | LINDLEY | ELLAND | HD7 6LS | NPg Best View | 14.075 | 13.942 | 13.71 | 13.422 | 13.225 | 13.012 | 12.75 | 11.591 | 9.096 | 7.263 | 5.553 | Primary | 2023
NPgY | SLEDMERE GARTH | 11 | 33 | WHINMOOR | FERRYBRIDGE B | LS14 5DS | NPg Best View | 17.575 | 14.035 | 14.001 | 13.962 | 13.931 | 13.893 | 13.839 | 13.651 | 13.321 | 13.124 | 12.949 | Primary | 2024
NPgY | SMITH STREET | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF10 2RY | NPg Best View | 11.027 | 10.817 | 10.512 | 10.167 | 9.953 | 9.722 | 9.445 | 8.183 | 5.738 | 3.885 | 2.043 | Primary | 2025
NPgY | SMITHY GREEN | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S71 1NQ | NPg Best View | 2.735 | 2.555 | 2.286 | 1.957 | 1.707 | 1.417 | 1.068 | -0.778 | -3.284 | -4.924 | -6.421 | Primary | 2026
NPgY | SNAITHING PARK ROAD | 11 | 33 | NORTON LEES | NORTON LEES | S10 3LJ | NPg Best View | 11.292 | 11.004 | 10.585 | 10.121 | 9.892 | 9.645 | 9.336 | 8.084 | 5.203 | 3.018 | 0.751 | Primary | 2027
NPgY | SNELSINS LANE | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 3UH | NPg Best View | 12.677 | 12.515 | 12.236 | 11.899 | 11.714 | 11.513 | 11.264 | 10.174 | 7.406 | 5.309 | 3.258 | Primary | 2028
NPgY | SOUTH ELMSALL | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 2JH | NPg Best View | 5.688 | 5.565 | 5.337 | 5.015 | 4.687 | 4.283 | 3.788 | 0.836 | -4.029 | -7.591 | -10.782 | Primary | 2029
NPgY | SOUTH FERRIBY | 11 | 33 | SANTON | KEADBY | DN18 6JL | NPg Best View | 16.57 | 16.456 | 16.289 | 16.088 | 15.927 | 15.756 | 15.555 | 14.613 | 12.798 | 11.328 | 9.941 | Primary | 2030
NPgY | SOUTH KIRKBY | 11 | 66 | FERRYBRIDGE A | FERRYBRIDGE A | WF9 3TJ | NPg Best View | 11.742 | 9.987 | 9.656 | 9.239 | 8.906 | 8.518 | 8.063 | 5.408 | 0.351 | -3.44 | -6.935 | Primary | 2031
NPgY | SOUTH RESTON | 11 | 33 | WOLD NEWTON | KEADBY | LN11 8JQ | NPg Best View | 4.73 | 4.632 | 4.494 | 4.335 | 4.214 | 4.09 | 3.945 | 3.317 | 2.232 | 1.375 | 0.547 | Primary | 2032
NPgY | SOUTH STREET | 11 | 33 | BINGLEY 132/33kV | BRADFORD WEST | BD21 1AH | NPg Best View | 14.885 | 14.659 | 14.302 | 13.871 | 13.604 | 13.319 | 12.971 | 11.5 | 8.634 | 6.559 | 4.583 | Primary | 2033
NPgY | SOUTHGATE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | YO43 3BE | NPg Best View | 0.092 | -0.045 | -0.251 | -0.501 | -0.704 | -0.925 | -1.189 | -2.461 | -5.029 | -7.035 | -8.897 | Primary | 2034
NPgY | SOUTHWOOD ROAD | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU16 5AN | NPg Best View | 9.44 | 9.176 | 8.767 | 8.277 | 7.931 | 7.559 | 7.116 | 5.136 | 0.637 | -2.974 | -6.467 | Primary | 2035
NPgY | SOWERBY BRIDGE 33/11KV | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | HX6 1EN | NPg Best View | 8.539 | 8.313 | 7.918 | 7.428 | 7.139 | 6.823 | 6.429 | 4.634 | 0.346 | -2.89 | -6.001 | Primary | 2036
NPgY | SPARK MILL LANE | 11 | 33 | BEVERLEY 132/33kV | CREYKE BECK | HU17 0TT | NPg Best View | 5.686 | 5.335 | 4.803 | 4.155 | 3.723 | 3.262 | 2.715 | 0.225 | -5.797 | -10.676 | -15.498 | Primary | 2037
NPgY | SPENBOROUGH | 11 | 33 | BRIGHOUSE 132/33kV | ELLAND | BD19 5BT | NPg Best View | 16.148 | 15.92 | 15.545 | 15.087 | 14.785 | 14.455 | 14.049 | 12.195 | 8.671 | 6.146 | 3.742 | Primary | 2038
NPgY | SPRING MILL STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD5 7HF | NPg Best View | 8.317 | 8.385 | 8.385 | 8.345 | 8.326 | 8.287 | 8.22 | 7.806 | 6.079 | 4.848 | 3.726 | Primary | 2039
NPgY | STAINFORTH | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN7 5HG | NPg Best View | 16.486 | 17.323 | 17.095 | 8.626 | 8.388 | 8.141 | 7.851 | 6.603 | 3.516 | 0.899 | -1.5 | Primary | 2040
NPgY | STAIRFOOT | 11 | 33 | HUNNINGLEY | WEST MELTON SECTION 3 | S71 5AD | NPg Best View | 11.087 | 10.722 | 10.196 | 9.564 | 9.085 | 8.575 | 7.975 | 5.291 | 0.518 | -3.12 | -6.524 | Primary | 2041
NPgY | STANLEY STREET | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S3 8HG | NPg Best View | 8.845 | 8.877 | 8.858 | 8.806 | 8.797 | 8.776 | 8.739 | 8.495 | 6.912 | 5.668 | 4.475 | Primary | 2042
NPgY | STANNINGTON ROAD | 11 | 33 | NEEPSEND | NEEPSEND | S6 5FH | NPg Best View | 10.911 | 10.541 | 9.986 | 9.337 | 8.959 | 8.564 | 8.087 | 6.111 | 1.539 | -1.986 | -5.43 | Primary | 2043
NPgY | STATION ROAD | 11 | 33 | SCUNTHORPE NORTH | KEADBY | DN15 6BT | NPg Best View | 5.179 | 4.731 | 4.077 | 3.291 | 2.609 | 1.862 | 0.987 | -3.392 | -10.341 | -15.699 | -20.836 | Primary | 2044
NPgY | STEVENSON ROAD | 11 | 33 | PITSMOOR 3/4 | PITSMOOR 3/4 | S9 3XG | NPg Best View | 13.056 | 13.142 | 13.221 | 13.29 | 13.353 | 13.409 | 13.457 | 13.663 | 13.587 | 13.531 | 13.485 | Primary | 2045
NPgY | STOKE STREET | 11 | 33 | ATTERCLIFFE | WEST MELTON / THORPE MARSH | S9 3QN | NPg Best View | 13.82 | 13.93 | 14.013 | 14.065 | 14.088 | 14.079 | 14.034 | 13.589 | 12.982 | 12.744 | 12.614 | Primary | 2046
NPgY | STOURTON 132/11KV | 11 | 132 | STOURTON 132/11kV | SKELTON GRANGE | LS10 1SP | NPg Best View | 2.836 | 2.948 | 3.044 | 3.124 | 3.199 | 3.262 | 3.312 | 3.495 | 3.283 | 3.148 | 3.037 | Primary | 2047
NPgY | STOURTON 33/11KV | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS10 1AX | NPg Best View | 6.442 | 6.34 | 6.169 | 5.977 | 5.874 | 5.758 | 5.607 | 4.953 | 3.172 | 1.874 | 0.675 | Primary | 2048
NPgY | STOW | 11 | 33 | BLYTON | KEADBY | LN1 2AJ | NPg Best View | 1.935 | 1.814 | 1.654 | 1.472 | 1.323 | 1.16 | 0.966 | 0.032 | -1.424 | -2.527 | -3.53 | Primary | 2049
NPgY | SWAN BANK LANE | 11 | 33 | HALIFAX 132/33kV | ELLAND | HX3 9XT | NPg Best View | 12.737 | 12.53 | 12.205 | 11.802 | 11.495 | 11.156 | 10.753 | 8.834 | 5.46 | 3.1 | 1.033 | Primary | 2050
NPgY | SWEET STREET | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS11 9TZ | NPg Best View | 12.673 | 10.718 | 10.738 | 10.731 | 10.711 | 10.674 | 10.614 | 10.212 | 8.791 | 7.76 | 6.876 | Primary | 2051
NPgY | SWINNOW MOOR | 11 | 33 | RODLEY | SKELTON GRANGE | LS13 4RJ | NPg Best View | 9.351 | 9.074 | 15.673 | 15.265 | 14.999 | 14.715 | 14.365 | 12.901 | 9.404 | 6.693 | 4.122 | Primary | 2052
NPgY | TADCASTER | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9PA | NPg Best View | 11.42 | 11.261 | 10.996 | 10.676 | 10.41 | 10.112 | 9.755 | 7.962 | 4.88 | 2.587 | 0.445 | Primary | 2053
NPgY | TANKERSLEY PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S35 2PT | NPg Best View | 3.449 | 1.95 | 1.549 | 1.224 | 1.001 | 0.753 | 0.438 | -0.942 | -5.472 | -9.169 | -12.621 | Primary | 2054
NPgY | TEMPLEBOROUGH 33/11KV | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S60 1AD | NPg Best View | 13.016 | 13.023 | 12.999 | 12.954 | 12.944 | 12.925 | 12.894 | 12.702 | 11.676 | 10.77 | 9.858 | Primary | 2055
NPgY | THORNBURY | 11 | 33 | RODLEY | SKELTON GRANGE | BD3 7AD | NPg Best View | 8.611 | 8.508 | 15.268 | 14.949 | 14.807 | 14.644 | 14.428 | 13.416 | 10.027 | 7.452 | 4.959 | Primary | 2056
NPgY | THORNE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN8 4NA | NPg Best View | 5.456 | 4.368 | 3.874 | 3.453 | 3.122 | 2.746 | 2.288 | 0.059 | -4.25 | -7.506 | -10.546 | Primary | 2057
NPgY | THORNTON | 11 | 33 | HOLMFIELD | BRADFORD WEST | BD13 3DP | NPg Best View | 10.288 | 9.9 | 9.297 | 8.584 | 8.219 | 7.839 | 7.381 | 5.496 | 0.423 | -3.535 | -7.502 | Primary | 2058
NPgY | THORPE ROAD | 11 | 33 | OSGODBY 3/4 | DRAX | DN14 7PA | NPg Best View | 12.87 | 12.747 | 10.445 | 10.136 | 9.819 | 9.401 | 8.875 | 5.577 | 2.246 | 0.419 | -1.072 | Primary | 2059
NPgY | TICKHILL ROAD | 11 | 66 | THURCROFT | THURCROFT | S66 7QN | NPg Best View | 9.533 | 9.182 | 8.657 | 8.054 | 7.642 | 7.2 | 6.677 | 4.355 | 0.46 | -2.404 | -5.207 | Primary | 2060
NPgY | TINGLEY | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | WF3 1SS | NPg Best View | 7.934 | 6.047 | 5.662 | 5.227 | 4.979 | 4.707 | 4.368 | 2.855 | -1.285 | -4.495 | -7.583 | Primary | 2061
NPgY | TINSLEY PARK ROAD | 11 | 33 | WINCOBANK | WINCOBANK | S9 5DL | NPg Best View | 8.642 | 8.002 | 8.083 | 8.107 | 8.097 | 8.046 | 7.947 | 7.18 | 5.379 | 4.267 | 3.382 | Primary | 2062
NPgY | TINSLEY WIRE INDUSTRIES | 11 | 33 | BLACKBURN MEADOWS B | WEST MELTON / THORPE MARSH | S9 1TY | NPg Best View | 18.896 | 18.873 | 18.802 | 18.681 | 18.525 | 18.315 | 18.047 | 16.353 | 14.609 | 13.749 | 13.14 | Primary | 2063
NPgY | TIVERTON ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 4DA | NPg Best View | 8.732 | 8.669 | 8.492 | 8.253 | 8.153 | 8.04 | 7.882 | 7.246 | 4.644 | 2.553 | 0.473 | Primary | 2064
NPgY | TODMORDEN | 11 | 33 | SOWERBY BRIDGE 132/33kV | ELLAND | OL14 7NB | NPg Best View | 10.629 | 10.506 | 10.296 | 10.035 | 9.769 | 9.477 | 9.125 | 7.481 | 4.386 | 2.016 | -0.014 | Primary | 2065
NPgY | TOLLER LANE | 11 | 33 | GIRLINGTON | BRADFORD WEST | BD9 5LE | NPg Best View | 12.502 | 12.311 | 11.988 | 11.581 | 11.372 | 11.152 | 10.885 | 9.725 | 5.926 | 2.94 | 0.049 | Primary | 2066
NPgY | TONG STREET | 11 | 33 | STAYGATE | SKELTON GRANGE | BD4 9PP | NPg Best View | 12.415 | 12.426 | 12.376 | 12.29 | 12.257 | 12.207 | 12.133 | 11.711 | 10.146 | 9.017 | 7.926 | Primary | 2067
NPgY | UPPER BASINGHALL STREET | 11 | 33 | KIRKSTALL C 2/5 | KIRKSTALL B | LS1 5JS | NPg Best View | 8.535 | 8.713 | 8.869 | 9.013 | 9.145 | 9.262 | 9.357 | 9.739 | 9.424 | 9.186 | 8.967 | Primary | 2068
NPgY | VARLEY STREET | 11 | 33 | RODLEY | SKELTON GRANGE | LS28 6AN | NPg Best View | 8.317 | 6.493 | 6.329 | 6.124 | 6.038 | 5.93 | 5.786 | 4.982 | 2.09 | -0.092 | -2.232 | Primary | 2069
NPgY | VICTORIA STREET | 11 | 33 | SHEFFIELD CITY | SHEFFIELD CITY | S1 4DP | NPg Best View | 10.431 | 9.288 | 9.371 | 9.434 | 9.482 | 9.523 | 9.553 | 9.707 | 8.974 | 8.408 | 7.889 | Primary | 2070
NPgY | WALESBY | 11 | 33 | WOLD NEWTON | KEADBY | LN8 3UL | NPg Best View | 1.755 | 1.608 | 1.397 | 1.148 | 0.974 | 0.789 | 0.57 | -0.446 | -2.546 | -4.248 | -5.923 | Primary | 2071
NPgY | WARREN LANE | 11 | 33 | BRAMHAM | FERRYBRIDGE B | LS24 9NT | NPg Best View | 3.46 | 3.439 | 3.389 | 3.332 | 3.324 | 3.312 | 3.294 | 3.207 | 2.416 | 1.771 | 1.09 | Primary | 2072
NPgY | WATH UPON DEARNE | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S63 7DX | NPg Best View | 13.861 | 13.786 | 13.626 | 13.424 | 13.21 | 12.955 | 12.65 | 10.959 | 8.833 | 7.525 | 6.379 | Primary | 2073
NPgY | WAVERLEY BUSINESS PARK | 11 | 33 | WINCOBANK | WINCOBANK | S60 5BL | NPg Best View | 24.681 | 24.741 | 24.79 | 24.825 | 24.85 | 24.869 | 24.88 | 24.893 | 24.269 | 23.694 | 23.136 | Primary | 2074
NPgY | WAWNE ROAD | 11 | 33 | BRANSHOLME | CREYKE BECK | HU7 5BT | NPg Best View | 15.025 | 15.081 | 15.102 | 15.103 | 15.126 | 15.143 | 15.146 | 15.186 | 14.385 | 13.714 | 13.062 | Primary | 2075
NPgY | WEELAND ROAD | 11 | 33 | KIRKHAW LANE | FERRYBRIDGE B | WF11 0LA | NPg Best View | -0.685 | -0.721 | -0.821 | -0.971 | -1.101 | -1.257 | -1.457 | -2.531 | -4.703 | -6.474 | -8.156 | Primary | 2076
NPgY | WELLINGTON STREET | 11 | 33 | FEATHERSTONE | FERRYBRIDGE B | WF10 1NW | NPg Best View | 3.829 | 3.63 | 3.301 | 2.846 | 2.414 | 1.876 | 1.217 | -2.77 | -8.702 | -12.826 | -16.59 | Primary | 2077
NPgY | WESLEY CRESCENT | 11 | 33 | HUMBERSTON | GRIMSBY WEST | DN35 0JU | NPg Best View | 11.16 | 11.031 | 10.776 | 10.452 | 10.276 | 10.089 | 9.851 | 8.899 | 5.95 | 3.651 | 1.429 | Primary | 2078
NPgY | WEST DOCKS | 11 | 33 | HULL SOUTH | CREYKE BECK | HU3 4UU | NPg Best View | 11.82 | 11.962 | 12.078 | 12.17 | 12.237 | 12.279 | 12.288 | 12.158 | 11.959 | 11.972 | 12.039 | Primary | 2079
NPgY | WEST END LANE | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN11 0PU | NPg Best View | 8.759 | 8.456 | 7.968 | 7.366 | 6.965 | 6.518 | 5.971 | 3.32 | -2.254 | -6.469 | -10.44 | Primary | 2080
NPgY | WEST MOOR PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN3 3FE | NPg Best View | 17.113 | 16.457 | 16.385 | 16.298 | 16.237 | 16.176 | 16.11 | 15.822 | 14.334 | 13.018 | 11.724 | Primary | 2081
NPgY | WEST PARK | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS16 5PS | NPg Best View | 5.092 | 4.873 | 4.577 | 4.282 | 4.071 | 3.849 | 3.58 | 2.498 | -0.344 | -2.654 | -4.777 | Primary | 2082
NPgY | WESTCOTT STREET | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU8 8JN | NPg Best View | 8.682 | 8.524 | 8.205 | 7.784 | 7.504 | 7.209 | 6.845 | 5.293 | 0.61 | -3.225 | -6.854 | Primary | 2083
NPgY | WHEATACRE ROAD | 11 | 66 | HUNSHELF | WEST MELTON SECTION 3 | S36 2GQ | NPg Best View | -1.106 | -1.262 | -1.505 | -1.791 | -1.965 | -2.147 | -2.366 | -3.317 | -6.222 | -8.569 | -10.825 | Primary | 2084
NPgY | WHEATLEY PARK | 11 | 66 | DONCASTER B/THORPE MARSH | WEST MELTON / THORPE MARSH | DN2 4PG | NPg Best View | 15.422 | 15.388 | 15.307 | 15.178 | 15.034 | 14.856 | 14.638 | 13.347 | 10.97 | 9.254 | 7.726 | Primary | 2085
NPgY | WHINGATE | 11 | 33 | KIRKSTALL C/RING ROAD HORSFORTH | KIRKSTALL B | LS12 3QT | NPg Best View | 16.095 | 15.669 | 15.204 | 14.892 | 14.643 | 14.369 | 14.037 | 12.487 | 9.3 | 6.893 | 4.722 | Primary | 2086
NPgY | WHITE LEE | 11 | 33 | HECKMONDWIKE | SKELTON GRANGE | WF17 8AF | NPg Best View | 10.873 | 10.576 | 10.093 | 9.515 | 9.205 | 8.872 | 8.466 | 6.746 | 3.031 | 0.281 | -2.522 | Primary | 2087
NPgY | WHITEHALL ROAD 2/3 | 11 | 33 | LOW ROAD | SKELTON GRANGE | LS1 4HR | NPg Best View | 24.322 | 24.387 | 24.442 | 24.492 | 24.54 | 24.582 | 24.616 | 24.749 | 24.567 | 24.423 | 24.288 | Primary | 2088
NPgY | WHITEHALL ROAD 4/5 | 11 | 33 | BEESTON ROYDS 132/33kV | KIRKSTALL B | LS1 4BN | NPg Best View | 8.547 | 8.605 | 8.651 | 8.686 | 8.713 | 8.735 | 8.749 | 8.799 | 7.863 | 7.109 | 6.437 | Primary | 2089
NPgY | WIBSEY | 11 | 33 | STAYGATE | SKELTON GRANGE | BD6 3BG | NPg Best View | 11.328 | 11.077 | 10.661 | 10.156 | 9.889 | 9.61 | 9.272 | 7.927 | 4.459 | 1.766 | -0.957 | Primary | 2090
NPgY | WITHERNSEA | 11 | 33 | HULL EAST 132/33kV | SALTEND NORTH | HU19 2QA | NPg Best View | -0.673 | -0.702 | -0.779 | -0.888 | -0.971 | -1.066 | -1.191 | -1.752 | -2.632 | -3.325 | -3.985 | Primary | 2091
NPgY | WOODCOCK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 5LL | NPg Best View | 9.347 | 9.275 | 9.141 | 8.978 | 8.848 | 8.709 | 8.549 | 7.778 | 5.771 | 4.091 | 2.424 | Primary | 2092
NPgY | WOODSEATS | 11 | 33 | JORDANTHORPE | JORDANTHORPE | S8 8QB | NPg Best View | 13.514 | 13.286 | 12.915 | 12.473 | 12.23 | 11.973 | 11.657 | 10.315 | 6.529 | 3.466 | 0.436 | Primary | 2093
NPgY | WOOLLEY | 11 | 66 | BARUGH 132/66kV | WEST MELTON SECTION 3 | S75 5JE | NPg Best View | 11.668 | 11.478 | 11.193 | 10.846 | 10.611 | 10.358 | 10.06 | 8.685 | 5.682 | 3.368 | 1.181 | Primary | 2094
NPgY | WORSBROUGH PARK | 11 | 66 | WEST MELTON | WEST MELTON SECTION 3 | S70 5LY | NPg Best View | 8.404 | 8.12 | 7.706 | 7.208 | 6.771 | 6.307 | 5.76 | 3.307 | -0.662 | -3.658 | -6.371 | Primary | 2095
NPgY | WRAWBY | 11 | 33 | SANTON | KEADBY | DN20 8SX | NPg Best View | 13.62 | 13.447 | 13.203 | 12.908 | 12.614 | 12.281 | 11.898 | 9.791 | 6.268 | 3.454 | 0.805 | Primary | 2096
NPgY | YARBOROUGH ROAD 33/11KV | 11 | 33 | YARBOROUGH ROAD 132/33kV | GRIMSBY WEST | DN34 4BL | NPg Best View | 7.737 | 7.745 | 7.642 | 7.474 | 7.317 | 7.121 | 6.868 | 5.412 | 1.545 | -1.34 | -3.923 | Primary | 2097
NPgY | YEW GREEN ROAD | 11 | 33 | SAINT ANDREWS ROAD 132/33kV | SKELTON GRANGE | HD4 5DD | NPg Best View | 14.116 | 13.91 | 13.575 | 13.174 | 12.966 | 12.746 | 12.478 | 11.374 | 8.458 | 6.194 | 3.906 | Primary | 2098
NPgY | YORK ROAD | 11 | 33 | LEEDS EAST | SKELTON GRANGE | LS9 6TF | NPg Best View | 7.599 | 7.303 | 6.879 | 6.44 | 6.157 | 5.854 | 5.483 | 3.888 | -0.713 | -4.408 | -7.889 | Primary | 2099
NPgY | YORK STREET | 11 | 33 | WAKEFIELD MONCKTON ROAD | WEST MELTON SECTION 3 | WF1 3AZ | NPg Best View | 8.165 | 8.054 | 7.863 | 7.612 | 7.416 | 7.194 | 6.933 | 5.513 | 1.971 | -0.935 | -3.797 | Primary | 2100
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Consumer Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2101
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Falling Short | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2102
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - Leading the Way | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2103
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NG FES - System Transformation | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2104
NPgY | NETHERLANDS WAY | 33 | 132 | NETHERLANDS WAY | GRIMSBY WEST | TBC | NPg Best View | 0 | 0 | 0 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | BSP | 2105
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 35.501 | 32.933 | 31.511 | 29.842 | 28.676 | 27.667 | 26.441 | 20.628 | 5.88 | -5.355 | -16.446 | BSP | 2106
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Consumer Transformation | 47.508 | 47.454 | 46.071 | 45.994 | 46.101 | 46.256 | 46.319 | 46.239 | 40.242 | 35.63 | 31.012 | BSP | 2107
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Consumer Transformation | 58.451 | 56.644 | 55.514 | 54.265 | 53.411 | 52.683 | 51.801 | 47.643 | 33.004 | 20.938 | 9.19 | BSP | 2108
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Consumer Transformation | 35.994 | 34.061 | 31.681 | 29.081 | 27.012 | 25.098 | 22.812 | 11.82 | -13.322 | -33.431 | -52.817 | BSP | 2109
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Consumer Transformation | 24.223 | 22.131 | 20.243 | 18.243 | 16.723 | 15.356 | 13.682 | 6.127 | -11.02 | -24.561 | -37.858 | BSP | 2110
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Consumer Transformation | 15.605 | 14.766 | 13.561 | 12.438 | 11.518 | 10.653 | 9.536 | 4.53 | -3.966 | -9.77 | -15.104 | BSP | 2111
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 33.701 | 33.035 | 32.359 | 31.591 | 31.023 | 30.486 | 29.782 | 26.134 | 15.584 | 7.549 | 0.274 | BSP | 2112
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Consumer Transformation | 40.907 | 39.529 | 38.344 | 36.971 | 35.977 | 35.083 | 28.716 | -8.724 | -21.309 | -30.234 | -38.664 | BSP | 2113
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 99.094 | 97.244 | 96.408 | 95.326 | 94.682 | 94.124 | 93.309 | 88.572 | 67.782 | 51.107 | 35.426 | BSP | 2114
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Consumer Transformation | 38.573 | 37.956 | 37.472 | 36.91 | 36.428 | 35.953 | 35.365 | 32.401 | 24.165 | 17.38 | 11.127 | BSP | 2115
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Consumer Transformation | 41.027 | 39.448 | 38.135 | 36.686 | 35.713 | 34.904 | 33.862 | 28.975 | 15.512 | 5.167 | -5.181 | BSP | 2116
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Consumer Transformation | 68.863 | 66.988 | 65.537 | 62.376 | 61.296 | 60.333 | 59.136 | 53.974 | 43.939 | 36.411 | 28.953 | BSP | 2117
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 21.826 | 20.611 | 20.29 | 19.912 | 19.61 | 19.314 | 18.954 | 16.904 | 11.717 | 7.469 | 3.439 | BSP | 2118
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Consumer Transformation | 53.767 | 51.92 | 50.49 | 48.847 | 47.391 | 45.953 | 44.271 | 35.303 | 17.505 | 3.501 | -9.479 | BSP | 2119
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Consumer Transformation | 24.831 | 20.732 | 18.909 | 17.094 | 15.46 | 13.855 | 11.837 | 3.019 | -10.58 | -20.215 | -28.892 | BSP | 2120
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Consumer Transformation | 20.766 | 18.814 | 17.52 | 16.093 | 14.941 | 13.887 | 12.57 | 6.349 | -9.278 | -21.42 | -32.964 | BSP | 2121
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 66.348 | 61.059 | 58.621 | 56.041 | 54.097 | 52.397 | 50.231 | 40.297 | 15.434 | -3.433 | -21.773 | BSP | 2122
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 28.879 | 27.429 | 25.93 | 24.09 | 22.693 | 21.369 | 19.744 | 10.427 | -12.557 | -30.177 | -46.692 | BSP | 2123
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.17 | 19.745 | 18.21 | 16.516 | 15.327 | 14.321 | 13.094 | 7.481 | -8.367 | -20.891 | -33.508 | BSP | 2124
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Consumer Transformation | 35.123 | 34.351 | 34.18 | 33.809 | 33.498 | 33.12 | 32.096 | 26.108 | 17.56 | 12.538 | 8.854 | BSP | 2125
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 32.239 | 31.101 | 29.789 | 28.212 | 26.916 | 25.677 | 24.077 | 16.605 | -2.725 | -17.83 | -31.863 | BSP | 2126
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Consumer Transformation | 68.43 | 68.35 | 68.334 | 68.313 | 68.289 | 68.26 | 68.229 | 68.019 | 67.67 | 67.285 | 66.895 | BSP | 2127
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | -1.429 | -1.444 | -1.468 | -1.495 | -1.517 | -1.539 | -1.57 | -1.713 | -1.988 | -2.185 | -2.367 | BSP | 2128
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Consumer Transformation | 116.215 | 103.09 | 90.549 | 85.244 | 81.001 | 77.098 | 72.361 | 50.997 | 16.806 | -6.976 | -29.385 | BSP | 2129
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 56.926 | 56.174 | 55.283 | 54.161 | 53.529 | 53.036 | 52.423 | 48.587 | 32.463 | 19.254 | 6.245 | BSP | 2130
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 26.831 | 25.594 | 25.149 | 24.568 | 24.164 | 23.788 | 23.281 | 19.556 | 9.632 | 2.494 | -3.986 | BSP | 2131
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 35.132 | 32.99 | 32.37 | 31.603 | 30.648 | 29.575 | 28.504 | 23.609 | 19.553 | 16.419 | 14.224 | BSP | 2132
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Falling Short | 46.771 | 46.653 | 45.345 | 45.398 | 45.372 | 45.292 | 45.188 | 44.458 | 43.507 | 42.774 | 42.378 | BSP | 2133
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Falling Short | 58.239 | 56.74 | 56.191 | 55.536 | 54.744 | 53.86 | 52.977 | 49.408 | 47.421 | 46.022 | 45.122 | BSP | 2134
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Falling Short | 35.44 | 34.015 | 32.628 | 31.028 | 29.13 | 27.037 | 24.947 | 15.369 | 7.573 | 1.374 | -3.309 | BSP | 2135
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Falling Short | 24.133 | 22.699 | 21.88 | 20.915 | 19.719 | 18.381 | 17.075 | 11.5 | 7.687 | 5.028 | 3.172 | BSP | 2136
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Falling Short | 15.638 | 15.28 | 14.808 | 14.264 | 13.535 | 12.681 | 11.842 | 8.181 | 5.654 | 4.122 | 3.43 | BSP | 2137
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 33.54 | 33.069 | 32.786 | 32.412 | 31.905 | 31.307 | 30.699 | 27.844 | 25.516 | 23.949 | 23.194 | BSP | 2138
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Falling Short | 40.468 | 39.478 | 39.019 | 38.397 | 37.564 | 36.588 | 30.386 | -6.054 | -10.005 | -12.819 | -14.415 | BSP | 2139
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 98.421 | 96.735 | 96.425 | 95.945 | 95.251 | 94.405 | 93.519 | 89.313 | 85.905 | 83.508 | 82.336 | BSP | 2140
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Falling Short | 38.36 | 37.766 | 37.419 | 37.002 | 36.49 | 35.916 | 35.335 | 32.632 | 30.397 | 28.654 | 27.423 | BSP | 2141
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Falling Short | 40.598 | 39.479 | 38.986 | 38.364 | 37.559 | 36.633 | 35.707 | 31.71 | 29.007 | 27.134 | 25.991 | BSP | 2142
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Falling Short | 68.905 | 67.627 | 67.045 | 64.595 | 63.768 | 62.832 | 61.929 | 58.062 | 55.415 | 53.637 | 52.395 | BSP | 2143
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 21.446 | 20.146 | 19.811 | 19.438 | 19.014 | 18.556 | 18.081 | 15.608 | 13.099 | 10.845 | 8.953 | BSP | 2144
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Falling Short | 52.711 | 50.728 | 49.406 | 47.918 | 46.225 | 44.388 | 42.498 | 32.737 | 22.78 | 14.099 | 7.137 | BSP | 2145
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Falling Short | 25.124 | 21.701 | 20.911 | 19.961 | 18.728 | 17.317 | 15.955 | 10.167 | 6.473 | 4.444 | 3.56 | BSP | 2146
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Falling Short | 20.386 | 18.776 | 18.119 | 17.307 | 16.289 | 15.142 | 14.001 | 8.838 | 4.811 | 1.917 | 0.007 | BSP | 2147
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 65.823 | 61.447 | 60.475 | 59.265 | 57.711 | 55.928 | 54.164 | 46.503 | 41.159 | 37.59 | 35.531 | BSP | 2148
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 27.712 | 26.294 | 25.195 | 23.88 | 22.311 | 20.554 | 18.715 | 9.051 | -0.942 | -9.321 | -15.372 | BSP | 2149
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 20.613 | 19.612 | 18.866 | 17.981 | 16.898 | 15.695 | 14.506 | 9.192 | 5.023 | 1.686 | -0.998 | BSP | 2150
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Falling Short | 34.605 | 33.776 | 33.679 | 33.487 | 33.177 | 32.753 | 31.752 | 26.404 | 21.326 | 17.475 | 15.88 | BSP | 2151
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 31.997 | 31.254 | 30.72 | 29.967 | 28.952 | 27.775 | 26.619 | 21.54 | 17.945 | 15.748 | 14.626 | BSP | 2152
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Falling Short | 68.194 | 67.996 | 67.863 | 67.725 | 67.582 | 67.435 | 67.283 | 66.468 | 65.563 | 64.599 | 63.608 | BSP | 2153
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | -1.433 | -1.436 | -1.444 | -1.455 | -1.47 | -1.489 | -1.507 | -1.591 | -1.66 | -1.7 | -1.719 | BSP | 2154
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Falling Short | 116.415 | 105.216 | 95.628 | 93.126 | 89.988 | 86.429 | 82.939 | 67.686 | 56.655 | 49.43 | 45.589 | BSP | 2155
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 56.291 | 55.724 | 55.295 | 54.768 | 54.139 | 53.435 | 52.692 | 48.944 | 45.368 | 42.371 | 40.211 | BSP | 2156
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 26.255 | 25.077 | 24.846 | 24.536 | 24.127 | 23.631 | 23.067 | 19.548 | 15.253 | 11.851 | 9.938 | BSP | 2157
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 35.369 | 32.495 | 30.677 | 28.65 | 27.358 | 26.367 | 24.642 | 7.134 | -5.883 | -14.63 | -13.576 | BSP | 2158
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - Leading the Way | 47.444 | 47.259 | 45.705 | 45.481 | 45.537 | 45.709 | 45.562 | 38.696 | 33.477 | 29.984 | 31.954 | BSP | 2159
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - Leading the Way | 58.359 | 56.328 | 54.873 | 53.299 | 52.316 | 51.591 | 50.064 | 32.815 | 19.67 | 10.164 | 11.633 | BSP | 2160
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - Leading the Way | 35.831 | 33.56 | 30.68 | 27.574 | 25.33 | 23.428 | 20.338 | -9.314 | -32.023 | -48.457 | -48.582 | BSP | 2161
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - Leading the Way | 24.119 | 21.803 | 19.572 | 17.227 | 15.641 | 14.369 | 12.135 | -8.872 | -24.306 | -35.071 | -34.379 | BSP | 2162
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - Leading the Way | 15.574 | 14.638 | 13.254 | 11.949 | 10.985 | 10.147 | 8.791 | -2.177 | -9.513 | -13.819 | -12.72 | BSP | 2163
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 33.661 | 32.883 | 32.026 | 31.067 | 30.429 | 29.874 | 28.749 | 16.303 | 7.2 | 1.175 | 2.649 | BSP | 2164
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - Leading the Way | 40.802 | 39.212 | 37.72 | 36.044 | 34.937 | 34.042 | 27.274 | -19.757 | -30.53 | -37.138 | -35.627 | BSP | 2165
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 98.98 | 96.854 | 95.608 | 94.106 | 93.293 | 92.702 | 90.929 | 66.917 | 48.613 | 35.782 | 38.899 | BSP | 2166
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - Leading the Way | 38.533 | 37.828 | 37.211 | 36.507 | 35.968 | 35.475 | 34.55 | 24.995 | 17.545 | 11.982 | 12.161 | BSP | 2167
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - Leading the Way | 40.909 | 39.102 | 37.451 | 35.661 | 34.585 | 33.831 | 32.296 | 15.963 | 4.095 | -3.764 | -2.252 | BSP | 2168
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - Leading the Way | 68.82 | 66.824 | 65.17 | 61.82 | 60.721 | 59.839 | 58.43 | 45.81 | 36.765 | 30.674 | 31.226 | BSP | 2169
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 21.806 | 20.538 | 20.136 | 19.677 | 19.337 | 19.027 | 18.504 | 12.668 | 7.983 | 4.43 | 4.138 | BSP | 2170
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - Leading the Way | 53.679 | 51.627 | 49.913 | 48 | 46.392 | 44.857 | 42.706 | 22.682 | 6.696 | -5.185 | -7.033 | BSP | 2171
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - Leading the Way | 24.836 | 20.654 | 18.65 | 16.658 | 15.039 | 13.524 | 11.273 | -6.77 | -18.871 | -26.584 | -25.509 | BSP | 2172
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - Leading the Way | 20.675 | 18.493 | 16.884 | 15.175 | 13.932 | 12.903 | 11.171 | -7.686 | -21.709 | -31.631 | -30.405 | BSP | 2173
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 66.222 | 60.552 | 57.562 | 54.481 | 52.394 | 50.798 | 47.999 | 17.271 | -4.75 | -19.632 | -16.544 | BSP | 2174
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 28.703 | 26.892 | 24.899 | 22.57 | 20.911 | 19.456 | 17.058 | -9.114 | -29.347 | -43.531 | -43.396 | BSP | 2175
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 21.062 | 19.356 | 17.435 | 15.394 | 14.102 | 13.156 | 11.494 | -7.276 | -21.556 | -31.746 | -30.691 | BSP | 2176
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - Leading the Way | 35.031 | 34.037 | 33.597 | 32.983 | 32.462 | 31.886 | 30.46 | 19.145 | 12.476 | 9.267 | 10.393 | BSP | 2177
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 32.162 | 30.806 | 29.183 | 27.321 | 25.985 | 24.826 | 22.66 | -1.081 | -18.332 | -30.345 | -28.153 | BSP | 2178
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - Leading the Way | 68.43 | 68.349 | 68.332 | 68.311 | 68.287 | 68.259 | 68.227 | 67.944 | 67.595 | 67.211 | 66.896 | BSP | 2179
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | -1.429 | -1.447 | -1.475 | -1.504 | -1.525 | -1.543 | -1.575 | -1.942 | -2.186 | -2.344 | -2.299 | BSP | 2180
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - Leading the Way | 115.921 | 102.264 | 88.92 | 82.799 | 78.307 | 74.468 | 68.707 | 25.371 | -4.187 | -21.893 | -20.262 | BSP | 2181
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 56.771 | 55.737 | 54.463 | 52.958 | 52.162 | 51.652 | 50.353 | 32.211 | 17.918 | 7.618 | 8.743 | BSP | 2182
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 26.726 | 25.321 | 24.641 | 23.818 | 23.257 | 22.779 | 21.866 | 10.763 | 2.25 | -3.239 | -2.831 | BSP | 2183
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 34.9 | 32.566 | 31.659 | 30.69 | 29.62 | 28.454 | 27.094 | 19.814 | 9.467 | -2.769 | -20.066 | BSP | 2184
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NG FES - System Transformation | 46.988 | 46.931 | 45.65 | 45.747 | 45.767 | 45.719 | 45.549 | 44.043 | 38.592 | 32.828 | 25.012 | BSP | 2185
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NG FES - System Transformation | 57.94 | 56.243 | 55.441 | 54.641 | 53.767 | 52.835 | 51.864 | 46.372 | 37.434 | 25.476 | 7.016 | BSP | 2186
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NG FES - System Transformation | 35.088 | 33.293 | 31.401 | 29.484 | 27.403 | 25.197 | 22.817 | 10.063 | -8.904 | -29.867 | -58.661 | BSP | 2187
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NG FES - System Transformation | 23.655 | 21.813 | 20.476 | 19.174 | 17.767 | 16.287 | 14.673 | 6.347 | -6.06 | -19.822 | -39.796 | BSP | 2188
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NG FES - System Transformation | 15.164 | 14.384 | 13.427 | 12.616 | 11.712 | 10.738 | 9.66 | 4.221 | -2.164 | -8.56 | -17.277 | BSP | 2189
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 33.386 | 32.747 | 32.242 | 31.729 | 31.132 | 30.471 | 29.734 | 25.33 | 17.4 | 9.29 | -1.94 | BSP | 2190
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NG FES - System Transformation | 40.276 | 39.076 | 38.299 | 37.455 | 36.485 | 35.41 | 28.959 | -9.541 | -19.276 | -29.369 | -42.87 | BSP | 2191
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 98.361 | 96.533 | 95.992 | 95.384 | 94.618 | 93.723 | 92.68 | 85.627 | 70.545 | 53.644 | 28.887 | BSP | 2192
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NG FES - System Transformation | 38.344 | 37.676 | 37.212 | 36.716 | 36.164 | 35.569 | 34.933 | 31.225 | 24.884 | 18.113 | 8.585 | BSP | 2193
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NG FES - System Transformation | 40.338 | 38.98 | 38.168 | 37.349 | 36.427 | 35.427 | 34.296 | 28.218 | 18.65 | 7.473 | -8.945 | BSP | 2194
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NG FES - System Transformation | 68.395 | 66.68 | 65.607 | 62.902 | 61.916 | 60.882 | 59.731 | 54.219 | 46.265 | 38.097 | 27.036 | BSP | 2195
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 21.555 | 20.284 | 19.955 | 19.605 | 19.211 | 18.78 | 18.304 | 15.421 | 10.574 | 5.643 | -0.537 | BSP | 2196
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NG FES - System Transformation | 52.964 | 50.986 | 49.578 | 48.066 | 46.4 | 44.597 | 42.59 | 31.348 | 14.644 | -1.678 | -20.905 | BSP | 2197
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NG FES - System Transformation | 24.473 | 20.425 | 18.879 | 17.44 | 15.877 | 14.235 | 12.479 | 3.932 | -6.914 | -16.465 | -28.72 | BSP | 2198
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NG FES - System Transformation | 20.134 | 18.26 | 17.245 | 16.214 | 15.062 | 13.824 | 12.446 | 5.131 | -6.87 | -19.549 | -36.502 | BSP | 2199
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 65.123 | 60.174 | 58.488 | 56.874 | 55.066 | 53.108 | 50.9 | 39.485 | 21.157 | 1.204 | -26.143 | BSP | 2200
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 27.881 | 26.475 | 25.275 | 23.915 | 22.347 | 20.583 | 18.551 | 6.346 | -13.217 | -33.238 | -58.568 | BSP | 2201
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 20.375 | 19.155 | 18.106 | 17.062 | 15.908 | 14.671 | 13.267 | 5.986 | -6.103 | -20.057 | -39.238 | BSP | 2202
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NG FES - System Transformation | 34.71 | 33.906 | 33.793 | 33.579 | 33.23 | 32.713 | 31.469 | 24.203 | 17.58 | 11.8 | 5.407 | BSP | 2203
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 31.755 | 30.685 | 29.678 | 28.575 | 27.327 | 25.975 | 24.462 | 16.223 | 1.402 | -13.336 | -33.661 | BSP | 2204
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NG FES - System Transformation | 68.314 | 68.171 | 68.087 | 67.997 | 67.898 | 67.79 | 67.675 | 66.992 | 66.083 | 65.129 | 64.169 | BSP | 2205
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | -1.439 | -1.453 | -1.472 | -1.489 | -1.51 | -1.532 | -1.56 | -1.704 | -1.961 | -2.168 | -2.406 | BSP | 2206
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NG FES - System Transformation | 114.914 | 102.508 | 91.385 | 87.803 | 83.953 | 79.886 | 75.44 | 53.506 | 29.831 | 4.798 | -29.86 | BSP | 2207
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 56.304 | 55.76 | 55.314 | 54.785 | 54.161 | 53.456 | 52.622 | 47.086 | 35.362 | 21.651 | 1.898 | BSP | 2208
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 26.349 | 25.189 | 24.941 | 24.629 | 24.21 | 23.686 | 22.998 | 18.243 | 9.747 | 1.83 | -8.022 | BSP | 2209
NPgN | ANNFIELD | 66 | 132 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 35.706 | 33.321 | 32.032 | 30.516 | 29.425 | 28.482 | 27.378 | 22.447 | 8.587 | -2.181 | -13.1 | BSP | 2210
NPgN | BARRACK ROAD | 33 | 132 | BARRACK ROAD | STELLA NORTH | NE4 6DB | NPg Best View | 47.837 | 47.958 | 46.669 | 46.693 | 46.805 | 46.954 | 47.008 | 47.072 | 41.357 | 36.904 | 32.314 | BSP | 2211
NPgN | BLUCHER | 33 | 132 | BLUCHER | STELLA NORTH | NE15 9SD | NPg Best View | 58.612 | 56.971 | 55.917 | 54.776 | 53.91 | 53.176 | 52.335 | 48.818 | 34.763 | 23 | 11.386 | BSP | 2212
NPgN | BOWESFIELD | 33 | 132 | BOWESFIELD | NORTON | TS18 3HP | NPg Best View | 36.362 | 34.735 | 32.587 | 30.231 | 28.312 | 26.534 | 24.473 | 14.961 | -8.639 | -27.901 | -46.958 | BSP | 2213
NPgN | CHIRTON GRANGE | 33 | 132 | CHIRTON GRANGE | TYNEMOUTH | NE29 8EY | NPg Best View | 24.53 | 22.7 | 21.06 | 19.314 | 18.027 | 16.899 | 15.567 | 9.702 | -6.392 | -19.426 | -32.483 | BSP | 2214
NPgN | COALBURNS | 66 | 132 | COALBURNS | STELLA SOUTH | NE40 4JP | NPg Best View | 16.26 | 15.796 | 14.971 | 14.157 | 13.564 | 12.992 | 12.204 | 8.631 | 1.174 | -4.117 | -9.255 | BSP | 2215
NPgN | DARLINGTON CENTRAL | 33 | 132 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 33.918 | 33.406 | 32.839 | 32.175 | 31.653 | 31.147 | 30.502 | 27.355 | 17.545 | 9.923 | 2.77 | BSP | 2216
NPgN | DARLINGTON NORTH | 33 | 132 | DARLINGTON NORTH | NORTON | DL3 0XE | NPg Best View | 41.194 | 40.025 | 38.991 | 37.775 | 36.859 | 36.023 | 29.755 | -6.866 | -18.315 | -26.6 | -34.814 | BSP | 2217
NPgN | DUNSTON | 66 | 132 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 99.584 | 98.043 | 97.412 | 96.537 | 95.96 | 95.442 | 94.694 | 90.669 | 71.003 | 54.946 | 39.418 | BSP | 2218
NPgN | FLATWORTH | 33 | 132 | FLATWORTH | TYNEMOUTH | NE29 7FN | NPg Best View | 38.698 | 38.178 | 37.758 | 37.267 | 36.803 | 36.339 | 35.781 | 33.153 | 25.403 | 18.885 | 12.712 | BSP | 2219
NPgN | GOSFORTH | 33 | 132 | GOSFORTH | TYNEMOUTH | NE3 1XL | NPg Best View | 41.328 | 39.977 | 38.821 | 37.544 | 36.655 | 35.927 | 35.023 | 31.1 | 18.463 | 8.547 | -1.629 | BSP | 2220
NPgN | HARROGATE 132/33KV | 33 | 132 | HARROGATE 132/33kV | KNARESBOROUGH | HG1 2LA | NPg Best View | 69.307 | 67.741 | 66.555 | 63.637 | 62.762 | 61.998 | 61.069 | 57.302 | 48.063 | 40.906 | 33.64 | BSP | 2221
NPgN | HUSTHWAITE | 33 | 132 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 22.008 | 20.887 | 20.634 | 20.317 | 20.045 | 19.766 | 19.417 | 17.463 | 12.584 | 8.529 | 4.548 | BSP | 2222
NPgN | LEEMING BAR_SKEEBY | 33 | 132 | LEEMING BAR_SKEEBY | NORTON | DL7 0RL | NPg Best View | 54.074 | 52.486 | 51.175 | 49.694 | 48.181 | 46.668 | 44.941 | 36.444 | 20.184 | 7.113 | -5.609 | BSP | 2223
NPgN | LINTON | 66 | 132 | LINTON | BLYTH 132kV | NE61 5DA | NPg Best View | 25.366 | 21.66 | 20.254 | 18.827 | 17.613 | 16.425 | 14.961 | 8.586 | -3.515 | -12.43 | -20.788 | BSP | 2224
NPgN | MALTON GRID | 66 | 132 | MALTON GRID | OSBALDWICK | YO17 6RD | NPg Best View | 21.091 | 19.386 | 18.279 | 17.046 | 16.013 | 15.069 | 13.932 | 8.806 | -5.836 | -17.468 | -28.829 | BSP | 2225
NPgN | MELROSEGATE 132/33KV | 33 | 132 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 66.938 | 62.103 | 59.99 | 57.748 | 56.001 | 54.501 | 52.674 | 44.81 | 21.572 | 3.548 | -14.436 | BSP | 2226
NPgN | NORTH TEES | 66 | 132 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 29.401 | 28.255 | 26.95 | 25.289 | 23.922 | 22.567 | 20.9 | 11.912 | -9.234 | -25.707 | -41.929 | BSP | 2227
NPgN | POTTER HOUSE 132/66KV | 66 | 132 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 21.519 | 20.358 | 19.013 | 17.522 | 16.437 | 15.533 | 14.467 | 9.936 | -5.124 | -17.266 | -29.717 | BSP | 2228
NPgN | RAVENSWORTH | 66 | 132 | RAVENSWORTH | STELLA SOUTH | DH3 1RQ | NPg Best View | 35.294 | 34.599 | 34.413 | 34.002 | 33.539 | 32.958 | 31.691 | 25.017 | 17.791 | 13.681 | 10.143 | BSP | 2229
NPgN | SCARBOROUGH GRID | 33 | 132 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 32.547 | 31.671 | 30.572 | 29.245 | 28.133 | 27.09 | 25.807 | 19.996 | 1.811 | -12.713 | -26.501 | BSP | 2230
NPgN | SEAL SANDS | 66 | 132 | SEAL SANDS | SALTHOLME | TS2 1FB | NPg Best View | 68.613 | 68.606 | 68.651 | 68.683 | 68.7 | 68.701 | 68.675 | 68.489 | 68.145 | 67.766 | 67.382 | BSP | 2231
NPgN | SPADEADAM 33KV | 33 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | -1.418 | -1.424 | -1.442 | -1.461 | -1.476 | -1.491 | -1.51 | -1.606 | -1.859 | -2.044 | -2.221 | BSP | 2232
NPgN | SPENNYMOOR 132/66KV | 66 | 132 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5LJ | NPg Best View | 117.26 | 104.894 | 93.272 | 88.796 | 85.518 | 82.504 | 78.862 | 62.282 | 32.009 | 10.198 | -11.493 | BSP | 2233
NPgN | TORONTO | 66 | 132 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 56.919 | 56.24 | 55.284 | 54.159 | 53.33 | 52.653 | 51.894 | 47.98 | 32.469 | 19.66 | 6.745 | BSP | 2234
NPgN | WORMALD GREEN 132/33KV | 33 | 132 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 26.956 | 25.798 | 25.34 | 24.741 | 24.2 | 23.659 | 22.971 | 18.828 | 9.872 | 3.396 | -2.967 | BSP | 2235
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Consumer Transformation | 5.565 | 5.195 | 4.593 | 3.889 | 3.444 | 3.109 | 2.697 | 0.916 | -4.634 | -8.93 | -13.435 | Primary | 2236
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Consumer Transformation | 12.024 | 11.098 | 9.017 | 8.049 | 7.304 | 6.659 | 5.883 | 2.53 | -6.131 | -12.638 | -19.017 | Primary | 2237
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Consumer Transformation | 7.996 | 7.615 | 9.028 | 8.357 | 7.878 | 7.456 | 6.936 | 4.564 | -0.752 | -4.809 | -8.86 | Primary | 2238
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Consumer Transformation | 6.223 | 5.948 | 5.468 | 4.899 | 4.514 | 4.194 | 3.792 | 2.043 | -3.259 | -7.459 | -11.671 | Primary | 2239
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Consumer Transformation | 26.375 | 26.377 | 26.378 | 26.379 | 26.38 | 26.381 | 26.382 | 26.386 | 26.389 | 26.392 | 26.394 | Primary | 2240
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Consumer Transformation | 2.828 | 2.784 | 2.674 | 2.532 | 2.459 | 2.401 | 2.315 | 1.83 | -0.08 | -1.545 | -2.991 | Primary | 2241
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Consumer Transformation | 4.071 | 4.042 | 4.004 | 3.967 | 3.93 | 3.893 | 3.845 | 3.634 | 3.387 | 3.201 | 3.032 | Primary | 2242
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Consumer Transformation | 4.613 | 4.453 | 4.222 | 3.95 | 3.724 | 3.513 | 3.264 | 1.89 | -1.057 | -3.348 | -5.537 | Primary | 2243
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Consumer Transformation | 8.527 | 8.412 | 8.207 | 7.961 | 7.812 | 7.702 | 7.557 | 6.798 | 3.747 | 1.304 | -1.191 | Primary | 2244
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Consumer Transformation | 12.497 | 12.194 | 11.715 | 11.211 | 10.813 | 10.441 | 9.965 | 7.823 | 4.178 | 1.69 | -0.593 | Primary | 2245
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Consumer Transformation | 5.008 | 4.414 | 3.953 | 3.456 | 3.066 | 2.707 | 2.273 | 0.169 | -5.993 | -11.023 | -15.813 | Primary | 2246
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Consumer Transformation | 11.88 | 11.324 | 11.011 | 10.635 | 10.396 | 10.195 | 9.933 | 8.578 | 3.869 | 0.083 | -3.61 | Primary | 2247
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Consumer Transformation | 7.549 | 7.147 | 6.602 | 6.009 | 5.571 | 5.164 | 4.681 | 2.062 | -2.855 | -6.403 | -9.703 | Primary | 2248
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Consumer Transformation | 6.762 | 6.11 | 5.725 | 5.293 | 5.003 | 4.743 | 4.419 | 2.831 | -1.475 | -4.859 | -8.114 | Primary | 2249
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 13.302 | 13.163 | 12.933 | 12.664 | 12.433 | 12.188 | 11.39 | 7.709 | 4.411 | 2.396 | 0.858 | Primary | 2250
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Consumer Transformation | 16.845 | 16.859 | 16.825 | 16.723 | 16.631 | 16.536 | 16.42 | 15.757 | 14.612 | 14.055 | 13.647 | Primary | 2251
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Consumer Transformation | 9.711 | 8.796 | 8.628 | 8.416 | 8.243 | 8.063 | 7.826 | 6.422 | 2.171 | -1.115 | -3.991 | Primary | 2252
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Consumer Transformation | 10.928 | 10.297 | 9.923 | 9.501 | 9.162 | 8.841 | 8.455 | 6.573 | 1.527 | -2.575 | -6.383 | Primary | 2253
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Consumer Transformation | 16.115 | 15.932 | 15.661 | 15.366 | 15.145 | 14.947 | 14.704 | 13.523 | 10.101 | 7.355 | 4.768 | Primary | 2254
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Consumer Transformation | 10.428 | 10.357 | 10.243 | 10.092 | 9.947 | 9.781 | 9.571 | 7.995 | 5.405 | 3.859 | 2.757 | Primary | 2255
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Consumer Transformation | 21.589 | 21.318 | 20.95 | 20.551 | 20.193 | 19.838 | 19.413 | 17.1 | 12.404 | 8.803 | 5.53 | Primary | 2256
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 17.773 | 17.618 | 17.401 | 17.162 | 16.953 | 16.747 | 16.505 | 15.297 | 12.401 | 9.943 | 7.61 | Primary | 2257
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Consumer Transformation | 13.232 | 12.496 | 11.809 | 11.028 | 10.466 | 9.973 | 9.381 | 6.7 | 0.46 | -4.383 | -9.175 | Primary | 2258
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Consumer Transformation | 7.878 | 7.346 | 7.224 | 7.076 | 6.989 | 6.929 | 6.843 | 6.438 | 4.404 | 2.807 | 1.207 | Primary | 2259
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Consumer Transformation | 9.164 | 8.782 | 8.141 | 7.387 | 6.864 | 6.429 | 5.878 | 3.043 | -3.531 | -8.178 | -12.786 | Primary | 2260
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Consumer Transformation | 7.887 | 7.239 | 6.642 | 6.052 | 5.57 | 5.144 | 4.62 | 2.415 | -1.588 | -4.509 | -7.364 | Primary | 2261
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Consumer Transformation | 8.088 | 7.801 | 7.358 | 6.847 | 6.47 | 6.146 | 5.741 | 3.831 | -1.012 | -4.662 | -8.194 | Primary | 2262
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Consumer Transformation | 9.14 | 8.926 | 8.582 | 8.178 | 7.829 | 7.498 | 7.085 | 5.239 | 0.865 | -2.663 | -5.97 | Primary | 2263
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Consumer Transformation | 3.953 | 3.685 | 3.22 | 2.659 | 2.26 | 1.897 | 1.441 | -0.763 | -6.922 | -11.741 | -16.317 | Primary | 2264
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Consumer Transformation | 7.827 | 7.453 | 6.936 | 6.355 | 5.864 | 5.404 | 4.861 | 2.346 | -2.826 | -7.08 | -11.263 | Primary | 2265
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Consumer Transformation | 10.356 | 10.171 | 10.258 | 10.312 | 10.387 | 10.459 | 10.503 | 10.587 | 8.984 | 7.742 | 6.573 | Primary | 2266
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Consumer Transformation | 6.444 | 5.512 | 5.263 | 5.012 | 4.799 | 4.595 | 4.333 | 3.101 | 0.307 | -1.861 | -3.885 | Primary | 2267
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Consumer Transformation | 17.096 | 15.793 | 15.097 | 14.276 | 13.672 | 13.132 | 12.475 | 9.309 | 2.385 | -2.652 | -7.539 | Primary | 2268
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Consumer Transformation | 13 | 12.978 | 12.899 | 12.796 | 12.74 | 12.699 | 12.63 | 12.31 | 10.935 | 9.882 | 8.8 | Primary | 2269
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Consumer Transformation | 6.784 | 6.756 | 6.717 | 6.674 | 6.64 | 6.61 | 6.574 | 6.412 | 6.096 | 5.853 | 5.615 | Primary | 2270
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 12.734 | 12.734 | 12.688 | 12.609 | 12.569 | 12.537 | 12.483 | 12.076 | 10.211 | 8.807 | 7.499 | Primary | 2271
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Consumer Transformation | 16.844 | 16.802 | 16.713 | 16.589 | 16.512 | 16.444 | 16.349 | 15.635 | 13.622 | 12.211 | 10.934 | Primary | 2272
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Consumer Transformation | 4.777 | 4.73 | 4.66 | 4.584 | 4.547 | 4.528 | 4.503 | 4.361 | 3.4 | 2.591 | 1.724 | Primary | 2273
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Consumer Transformation | 9.17 | 9.017 | 8.794 | 8.557 | 8.399 | 8.264 | 8.1 | 7.345 | 5.266 | 3.657 | 2.081 | Primary | 2274
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Consumer Transformation | 10.346 | 10.152 | 9.831 | 9.468 | 9.198 | 8.95 | 8.632 | 7.156 | 2.787 | -0.67 | -3.912 | Primary | 2275
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Consumer Transformation | 23.142 | 22.862 | 22.825 | 22.78 | 22.753 | 22.729 | 22.685 | 22.484 | 21.23 | 20.195 | 19.253 | Primary | 2276
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Consumer Transformation | 6.812 | 6.71 | 6.502 | 6.256 | 6.077 | 5.898 | 5.651 | 4.116 | 0.089 | -2.71 | -5.093 | Primary | 2277
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Consumer Transformation | 5.141 | 4.318 | 3.672 | 2.919 | 2.343 | 1.816 | 1.155 | -2.136 | -8.517 | -12.819 | -16.721 | Primary | 2278
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Consumer Transformation | 12.069 | 10.801 | 10.399 | 9.924 | 9.571 | 9.248 | 8.839 | 6.886 | 1.185 | -3.226 | -7.392 | Primary | 2279
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 8.94 | 8.809 | 8.586 | 8.35 | 8.13 | 7.903 | 7.6 | 6.159 | 3.1 | 0.765 | -1.281 | Primary | 2280
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Consumer Transformation | 14.274 | 14.005 | 13.59 | 13.15 | 12.812 | 12.5 | 12.105 | 10.304 | 4.963 | 0.589 | -3.532 | Primary | 2281
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Consumer Transformation | 4.292 | 3.828 | 3.706 | 3.559 | 3.451 | 3.359 | 3.237 | 2.648 | 0.298 | -1.645 | -3.594 | Primary | 2282
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Consumer Transformation | 18.325 | 18.14 | 17.83 | 17.457 | 17.154 | 16.869 | 16.512 | 14.76 | 10.035 | 6.34 | 2.937 | Primary | 2283
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Consumer Transformation | 18.913 | 18.903 | 18.869 | 18.82 | 18.795 | 18.773 | 18.741 | 18.561 | 17.492 | 16.57 | 15.675 | Primary | 2284
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Consumer Transformation | 8.133 | 7.955 | 7.664 | 7.355 | 7.13 | 6.932 | 6.664 | 5.448 | 2.78 | 0.808 | -1.168 | Primary | 2285
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Consumer Transformation | 9.076 | 9.069 | 9.033 | 8.982 | 8.936 | 8.883 | 8.805 | 8.255 | 7.104 | 6.315 | 5.649 | Primary | 2286
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Consumer Transformation | 1.72 | 1.542 | 1.195 | 0.751 | 0.465 | 0.238 | -0.059 | -1.429 | -6.207 | -10.03 | -13.887 | Primary | 2287
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Consumer Transformation | 5.394 | 4.633 | 3.662 | 2.827 | 2.116 | 1.428 | 0.582 | -3.187 | -9.409 | -13.84 | -17.787 | Primary | 2288
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Consumer Transformation | 10.61 | 10.138 | 8.707 | 7.95 | 7.411 | 6.961 | 6.42 | 3.859 | -2.374 | -7.056 | -11.779 | Primary | 2289
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Consumer Transformation | 15.66 | 15.341 | 15.296 | 15.225 | 15.157 | 15.078 | 14.966 | 14.227 | 12.64 | 11.534 | 10.619 | Primary | 2290
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Consumer Transformation | 10.913 | 9.477 | 9.131 | 8.704 | 8.41 | 8.156 | 7.818 | 6.102 | -0.381 | -5.451 | -10.279 | Primary | 2291
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Consumer Transformation | 8.018 | 7.584 | 6.923 | 6.187 | 5.632 | 5.133 | 4.513 | 1.656 | -4.478 | -9.146 | -13.696 | Primary | 2292
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Consumer Transformation | 22.68 | 22.18 | 21.486 | 20.835 | 20.296 | 19.787 | 19.129 | 16.239 | 11.863 | 8.841 | 5.962 | Primary | 2293
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Consumer Transformation | 5.227 | 4.964 | 4.541 | 4.047 | 3.698 | 3.4 | 3.034 | 1.303 | -3.362 | -7.031 | -10.681 | Primary | 2294
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Consumer Transformation | 11.82 | 11.59 | 11.241 | 10.861 | 10.63 | 10.455 | 10.238 | 9.328 | 6.517 | 4.317 | 1.975 | Primary | 2295
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Consumer Transformation | 18.308 | 18.204 | 18.003 | 17.75 | 17.562 | 17.388 | 17.163 | 16.014 | 12.323 | 9.404 | 6.68 | Primary | 2296
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Consumer Transformation | 9.389 | 9.395 | 7.904 | 7.813 | 7.769 | 7.732 | 7.666 | 7.142 | 5.194 | 3.836 | 2.593 | Primary | 2297
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Consumer Transformation | 27.466 | 27.51 | 27.533 | 27.53 | 27.51 | 27.466 | 27.395 | 26.687 | 25.428 | 24.774 | 24.435 | Primary | 2298
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Consumer Transformation | 14.594 | 14.119 | 14.086 | 14.028 | 14.044 | 14.091 | 14.116 | 14.191 | 13.025 | 12.097 | 11.015 | Primary | 2299
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Consumer Transformation | 2.827 | 2.6 | 2.197 | 1.702 | 1.144 | 0.494 | -0.345 | -5.436 | -10.796 | -13.314 | -14.465 | Primary | 2300
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Consumer Transformation | 18.156 | 18.271 | 18.37 | 18.453 | 18.537 | 18.618 | 18.689 | 18.977 | 18.775 | 18.589 | 18.379 | Primary | 2301
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 7.483 | 6.946 | 6.441 | 5.872 | 5.407 | 4.971 | 4.44 | 2.093 | -2.502 | -5.962 | -9.247 | Primary | 2302
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Consumer Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2303
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Consumer Transformation | 3.124 | 2.987 | 2.723 | 2.4 | 2.255 | 2.173 | 2.06 | 1.51 | -1.807 | -4.464 | -7.297 | Primary | 2304
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Consumer Transformation | 14.311 | 13.972 | 13.481 | 12.956 | 12.518 | 12.091 | 11.558 | 9.034 | 4.956 | 2.071 | -0.591 | Primary | 2305
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Consumer Transformation | 15.286 | 12.906 | 12.908 | 12.884 | 12.879 | 12.866 | 12.814 | 12.389 | 10.451 | 9.018 | 7.774 | Primary | 2306
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Consumer Transformation | 8.687 | 7.892 | 7.209 | 6.509 | 5.988 | 5.528 | 4.955 | 2.284 | -4.564 | -9.866 | -15.057 | Primary | 2307
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Consumer Transformation | 18.48 | 18.373 | 18.207 | 18.041 | 17.927 | 17.835 | 17.715 | 17.181 | 15.412 | 14.008 | 12.565 | Primary | 2308
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Consumer Transformation | 8.644 | 8.07 | 7.229 | 6.311 | 5.66 | 5.12 | 4.454 | 1.516 | -5.03 | -9.949 | -15.064 | Primary | 2309
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Consumer Transformation | 4.229 | 3.481 | 2.898 | 2.215 | 1.671 | 1.159 | 0.537 | -2.419 | -8.438 | -12.81 | -16.853 | Primary | 2310
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Consumer Transformation | 2.94 | 2.544 | 2.011 | 1.496 | 1.113 | 0.793 | 0.399 | -1.323 | -4.812 | -7.368 | -9.977 | Primary | 2311
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Consumer Transformation | 8.546 | 8.512 | 8.447 | 23.765 | 23.701 | 23.639 | 23.558 | 22.978 | 21.854 | 21.181 | 20.635 | Primary | 2312
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Consumer Transformation | 21.058 | 20.777 | 20.753 | 20.717 | 20.696 | 20.682 | 20.666 | 20.593 | 19.833 | 19.223 | 18.633 | Primary | 2313
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Consumer Transformation | 19.302 | 19.113 | 18.802 | 18.44 | 18.201 | 18.022 | 17.798 | 16.764 | 13.528 | 11.085 | 8.569 | Primary | 2314
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Consumer Transformation | 16.736 | 16.876 | 17.008 | 17.132 | 17.251 | 17.363 | 17.468 | 17.926 | 18.234 | 18.494 | 18.727 | Primary | 2315
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Consumer Transformation | 14.789 | 14.876 | 14.907 | 14.916 | 14.956 | 14.998 | 15.003 | 14.915 | 13.794 | 13.055 | 12.361 | Primary | 2316
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Consumer Transformation | 1.44 | 1.447 | 1.355 | 1.175 | 20.935 | 20.755 | 20.491 | 18.159 | 12.587 | 8.875 | 5.969 | Primary | 2317
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Consumer Transformation | 7.736 | 7.369 | 6.838 | 6.265 | 5.85 | 5.482 | 5.034 | 3.06 | -1.384 | -4.839 | -8.306 | Primary | 2318
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Consumer Transformation | 6.882 | 6.498 | 5.919 | 5.277 | 4.781 | 4.324 | 3.765 | 1.246 | -3.428 | -6.667 | -9.702 | Primary | 2319
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Consumer Transformation | 17.738 | 17.669 | 17.563 | 17.443 | 17.322 | 17.194 | 17.034 | 16.223 | 14.463 | 13.062 | 11.835 | Primary | 2320
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Consumer Transformation | 6.71 | 6.574 | 6.362 | 6.137 | 5.966 | 5.811 | 5.61 | 4.671 | 2.118 | 0.189 | -1.639 | Primary | 2321
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Consumer Transformation | 6.868 | 6.545 | 6.115 | 5.684 | 5.306 | 4.939 | 4.49 | 2.414 | -1.039 | -3.641 | -6.093 | Primary | 2322
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Consumer Transformation | 18.668 | 18.655 | 18.613 | 18.558 | 18.52 | 18.485 | 18.434 | 18.144 | 17.252 | 16.583 | 15.96 | Primary | 2323
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Consumer Transformation | 7.049 | 6.794 | 6.412 | 6.013 | 5.735 | 5.496 | 5.197 | 3.922 | 0.778 | -1.634 | -4.067 | Primary | 2324
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Consumer Transformation | 2.79 | 2.77 | 2.74 | 2.709 | 2.682 | 2.655 | 2.62 | 2.455 | 2.152 | 1.935 | 1.734 | Primary | 2325
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Consumer Transformation | 9.297 | 8.961 | 8.823 | 8.653 | 8.538 | 8.435 | 8.301 | 7.505 | 4.93 | 2.918 | 1.03 | Primary | 2326
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Consumer Transformation | 15.083 | 14.906 | 14.638 | 14.347 | 14.113 | 13.897 | 13.623 | 12.417 | 10.008 | 8.181 | 6.409 | Primary | 2327
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Consumer Transformation | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary | 2328
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Consumer Transformation | 21.267 | 21.102 | 20.864 | 20.618 | 20.435 | 20.275 | 20.075 | 19.153 | 16.648 | 14.716 | 12.843 | Primary | 2329
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Consumer Transformation | 8.565 | 8.26 | 7.795 | 7.298 | 7 | 6.78 | 6.505 | 5.279 | 1.304 | -1.794 | -5.054 | Primary | 2330
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Consumer Transformation | 14.265 | 14.013 | 13.634 | 13.21 | 12.928 | 12.693 | 12.406 | 11.037 | 7.53 | 4.88 | 2.241 | Primary | 2331
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Consumer Transformation | 33.362 | 33.003 | 32.967 | 32.925 | 32.899 | 32.882 | 32.857 | 32.752 | 32.158 | 31.699 | 31.239 | Primary | 2332
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Consumer Transformation | 4.367 | 3.515 | 2.782 | 1.975 | 1.376 | 0.876 | 0.262 | -2.299 | -7.585 | -11.423 | -15.369 | Primary | 2333
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Consumer Transformation | 15.032 | 14.288 | 13.968 | 13.581 | 13.257 | 12.944 | 12.587 | 10.55 | 5.644 | 1.722 | -2.048 | Primary | 2334
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Consumer Transformation | 12.019 | 11.924 | 11.752 | 11.545 | 11.347 | 11.144 | 10.883 | 9.472 | 5.152 | 1.676 | -1.424 | Primary | 2335
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Consumer Transformation | 15.02 | 14.97 | 14.881 | 14.772 | 14.702 | 14.644 | 14.569 | 14.106 | 12.451 | 11.139 | 9.857 | Primary | 2336
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Consumer Transformation | 24.355 | 22.518 | 22.154 | 21.767 | 21.462 | 21.175 | 20.823 | 19.308 | 16.372 | 14.149 | 12.036 | Primary | 2337
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Consumer Transformation | 5.278 | 4.762 | 4.386 | 3.961 | 3.615 | 3.289 | 2.906 | 1.046 | -3.836 | -7.929 | -11.843 | Primary | 2338
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Consumer Transformation | 1.489 | 0.663 | 0.021 | -0.647 | -1.143 | -1.568 | -2.086 | -4.404 | -10.526 | -15.514 | -20.547 | Primary | 2339
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Consumer Transformation | 3.371 | 3.328 | 1.982 | 1.916 | 1.855 | 1.793 | 1.712 | 1.313 | 0.819 | 0.511 | 0.256 | Primary | 2340
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Consumer Transformation | 8.846 | 8.369 | 10.006 | 9.63 | 9.334 | 9.049 | 8.676 | 6.902 | 1.973 | -1.889 | -5.485 | Primary | 2341
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Consumer Transformation | 7.321 | 7.184 | 6.907 | 6.546 | 6.396 | 6.315 | 6.196 | 5.508 | 0.871 | -2.946 | -6.943 | Primary | 2342
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Consumer Transformation | 32.739 | 31.373 | 31.319 | 31.25 | 31.187 | 31.12 | 31.033 | 30.497 | 28.688 | 27.175 | 25.823 | Primary | 2343
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Consumer Transformation | 12.237 | 12.107 | 11.879 | 11.609 | 11.396 | 11.194 | 10.94 | 9.772 | 5.841 | 2.572 | -0.462 | Primary | 2344
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Consumer Transformation | 8.941 | 8.232 | 7.953 | 7.704 | 7.513 | 7.337 | 7.118 | 6.2 | 3.932 | 2.176 | 0.517 | Primary | 2345
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Consumer Transformation | 8.854 | 8.914 | 8.936 | 8.934 | 8.975 | 9.024 | 9.06 | 9.137 | 8.236 | 7.538 | 6.808 | Primary | 2346
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Consumer Transformation | 13.987 | 13.948 | 13.849 | 13.709 | 13.587 | 13.466 | 13.306 | 12.511 | 9.622 | 7.283 | 5.169 | Primary | 2347
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Consumer Transformation | 14.778 | 14.756 | 14.674 | 14.529 | 14.348 | 14.113 | 13.798 | 11.4 | 7.578 | 5.285 | 3.715 | Primary | 2348
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Consumer Transformation | 18.921 | 18.78 | 18.562 | 18.293 | 18.128 | 17.99 | 17.827 | 16.946 | 13.613 | 10.714 | 7.729 | Primary | 2349
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Consumer Transformation | 5.673 | 4.637 | 4.315 | 3.934 | 3.638 | 3.367 | 3.056 | 1.454 | -2.483 | -5.709 | -8.88 | Primary | 2350
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Consumer Transformation | 5.851 | 4.209 | 2.968 | 1.583 | 0.492 | -0.462 | -1.576 | -6.359 | -14.669 | -20.824 | -27.028 | Primary | 2351
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Consumer Transformation | 13.346 | 12.464 | 11.983 | 11.552 | 11.213 | 10.918 | 10.555 | 9.024 | 6.058 | 3.866 | 1.661 | Primary | 2352
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Consumer Transformation | 15.838 | 14.997 | 14.542 | 14.025 | 13.653 | 13.321 | 12.906 | 11.044 | 6.11 | 2.267 | -1.407 | Primary | 2353
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Consumer Transformation | 9.987 | 9.831 | 9.541 | 9.19 | 8.921 | 8.674 | 8.352 | 6.904 | 3.061 | 0.037 | -2.801 | Primary | 2354
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Consumer Transformation | 11.112 | 11.161 | 11.203 | 11.239 | 11.269 | 11.296 | 11.315 | 11.373 | 11.281 | 11.189 | 11.093 | Primary | 2355
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Consumer Transformation | 21.529 | 21.455 | 21.313 | 21.128 | 21.005 | 20.902 | 20.774 | 20.199 | 18.597 | 17.358 | 16.103 | Primary | 2356
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Consumer Transformation | 16.319 | 16.459 | 16.577 | 16.677 | 16.78 | 16.878 | 16.962 | 17.307 | 16.754 | 16.311 | 15.887 | Primary | 2357
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 10.833 | 10.42 | 9.828 | 9.181 | 8.703 | 8.285 | 7.788 | 5.568 | 0.536 | -3.325 | -7.164 | Primary | 2358
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Consumer Transformation | 21.967 | 21.939 | 21.885 | 21.826 | 21.79 | 21.762 | 21.721 | 21.53 | 20.911 | 20.418 | 19.902 | Primary | 2359
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Consumer Transformation | 2.695 | 2.446 | 2.024 | 1.533 | 1.203 | 0.931 | 0.589 | -0.881 | -5.681 | -9.466 | -13.194 | Primary | 2360
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Consumer Transformation | 6.609 | 6.595 | 6.57 | 6.541 | 6.522 | 6.506 | 6.484 | 6.378 | 6.024 | 5.748 | 5.48 | Primary | 2361
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Consumer Transformation | 8.145 | 7.347 | 7.046 | 6.743 | 6.539 | 6.39 | 6.195 | 5.351 | 2.94 | 1.166 | -0.72 | Primary | 2362
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Consumer Transformation | 12.992 | 12.406 | 11.541 | 10.556 | 9.734 | 8.96 | 8.014 | 3.325 | -6.97 | -14.869 | -22.133 | Primary | 2363
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Consumer Transformation | 10.52 | 9.018 | 8.116 | 7.587 | 7.193 | 6.835 | 6.383 | 4.119 | -1.844 | -6.337 | -10.528 | Primary | 2364
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 3.963 | 3.807 | 3.599 | 3.371 | 3.159 | 2.941 | 2.684 | 1.326 | -1.362 | -3.496 | -5.414 | Primary | 2365
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Consumer Transformation | 3.962 | 3.912 | 3.852 | 3.789 | 3.727 | 3.664 | 3.593 | 3.221 | 2.692 | 2.227 | 1.792 | Primary | 2366
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Consumer Transformation | 3.268 | 2.875 | 23.93 | 23.628 | 23.41 | 23.212 | 22.953 | 21.264 | 17.413 | 14.742 | 12.284 | Primary | 2367
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Consumer Transformation | 13.88 | 13.319 | 12.887 | 12.439 | 12.053 | 11.689 | 11.234 | 9.334 | 6.994 | 5.513 | 4.179 | Primary | 2368
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Consumer Transformation | 4.362 | 4.205 | 3.984 | 3.749 | 3.566 | 3.397 | 3.197 | 2.347 | 0.885 | -0.222 | -1.289 | Primary | 2369
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Consumer Transformation | 3.598 | 3.471 | 3.3 | 3.122 | 2.958 | 2.792 | 2.59 | 1.608 | 0.094 | -1.027 | -2.024 | Primary | 2370
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Consumer Transformation | 14.045 | 13.407 | 12.996 | 12.502 | 12.11 | 11.749 | 11.288 | 9.18 | 3.483 | -1.016 | -5.316 | Primary | 2371
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Consumer Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2372
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Consumer Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2373
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Consumer Transformation | 17.649 | 17.118 | 16.892 | 16.63 | 16.455 | 16.304 | 16.111 | 15.228 | 12.137 | 9.658 | 7.258 | Primary | 2374
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Consumer Transformation | 15.292 | 14.247 | 14.179 | 14.097 | 14.013 | 13.922 | 13.807 | 13.151 | 11.964 | 11.072 | 10.308 | Primary | 2375
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Consumer Transformation | 10.955 | 10.71 | 10.337 | 9.942 | 9.67 | 9.444 | 9.154 | 7.752 | 4.353 | 1.866 | -0.611 | Primary | 2376
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Consumer Transformation | 12.991 | 12.69 | 12.287 | 11.892 | 11.554 | 11.229 | 10.826 | 8.944 | 5.741 | 3.349 | 1.096 | Primary | 2377
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Consumer Transformation | 10.513 | 9.719 | 9.498 | 9.225 | 9.009 | 8.804 | 8.552 | 7.344 | 4.041 | 1.351 | -1.189 | Primary | 2378
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Consumer Transformation | 11.305 | 11.164 | 10.921 | 10.633 | 10.456 | 10.313 | 10.126 | 9.105 | 5.864 | 3.379 | 0.923 | Primary | 2379
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Consumer Transformation | 18.742 | 17.958 | 17.925 | 17.861 | 17.834 | 17.818 | 17.773 | 17.458 | 15.556 | 14.051 | 12.589 | Primary | 2380
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Consumer Transformation | 16.518 | 16.196 | 15.709 | 15.176 | 14.776 | 14.402 | 13.931 | 11.42 | 6.346 | 2.755 | -0.55 | Primary | 2381
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Consumer Transformation | 8.886 | 8.748 | 8.537 | 8.318 | 8.12 | 7.923 | 7.671 | 6.565 | 4.95 | 3.816 | 2.808 | Primary | 2382
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Consumer Transformation | 12.849 | 12.386 | 10.424 | 9.83 | 9.437 | 9.099 | 8.676 | 6.513 | 0.59 | -3.683 | -7.768 | Primary | 2383
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Consumer Transformation | 23.286 | 13.72 | 6.548 | 6.074 | 5.725 | 5.416 | 5.037 | 3.088 | -1.587 | -5.043 | -8.361 | Primary | 2384
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Consumer Transformation | 2.501 | 1.629 | 0.832 | -1.733 | -2.324 | -2.85 | -3.503 | -6.346 | -12.158 | -16.589 | -20.967 | Primary | 2385
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Consumer Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2386
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Consumer Transformation | 5.51 | 5.391 | 5.224 | 5.029 | 4.882 | 4.744 | 4.581 | 3.642 | 1.218 | -0.722 | -2.564 | Primary | 2387
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Consumer Transformation | 12.153 | 11.318 | 10.939 | 10.453 | 10.1 | 9.79 | 9.423 | 7.677 | 3.521 | 0.483 | -2.472 | Primary | 2388
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 8.028 | 6.37 | 6.229 | 6.031 | 5.927 | 5.849 | 5.733 | 5.039 | 1.965 | -0.352 | -2.596 | Primary | 2389
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Consumer Transformation | 27.962 | 27.985 | 28.008 | 28.03 | 28.05 | 28.07 | 28.089 | 28.17 | 28.235 | 28.289 | 28.337 | Primary | 2390
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Consumer Transformation | 19.994 | 18.919 | 18.506 | 18.037 | 17.699 | 17.404 | 17.047 | 15.473 | 11.713 | 8.756 | 5.809 | Primary | 2391
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Consumer Transformation | 8.385 | 7.786 | 7.939 | 8.027 | 8.081 | 8.079 | 8 | 6.768 | 4.155 | 2.896 | 2.296 | Primary | 2392
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Consumer Transformation | 4.207 | 4.13 | 4.114 | 4.095 | 4.072 | 4.045 | 4.015 | 3.818 | 3.487 | 3.124 | 2.756 | Primary | 2393
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Consumer Transformation | 14.423 | 14.067 | 13.545 | 12.993 | 12.624 | 12.324 | 11.959 | 10.314 | 5.121 | 0.862 | -3.44 | Primary | 2394
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Consumer Transformation | 2.514 | 2.207 | 1.782 | 1.319 | 0.893 | 0.466 | -0.055 | -2.594 | -6.879 | -10.132 | -13.083 | Primary | 2395
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Consumer Transformation | 8.844 | 7.894 | 7.551 | 7.189 | 6.868 | 6.57 | 6.201 | 4.635 | 2.515 | 1.064 | -0.35 | Primary | 2396
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Consumer Transformation | 25.255 | 24.714 | 24.226 | 23.669 | 23.226 | 22.808 | 22.298 | 19.887 | 14.087 | 9.48 | 5.147 | Primary | 2397
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Consumer Transformation | 11.801 | 11.478 | 10.951 | 10.335 | 9.93 | 9.607 | 9.204 | 7.37 | 2.3 | -1.5 | -5.36 | Primary | 2398
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Consumer Transformation | 11.334 | 10.964 | 10.42 | 9.824 | 9.376 | 8.976 | 8.485 | 6.251 | 0.794 | -3.577 | -7.894 | Primary | 2399
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Consumer Transformation | 14.012 | 13.833 | 13.928 | 13.999 | 14.096 | 14.197 | 14.28 | 14.61 | 13.905 | 13.348 | 12.756 | Primary | 2400
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Consumer Transformation | 32.718 | 32.298 | 31.743 | 31.181 | 30.708 | 30.252 | 29.712 | 27.235 | 21.616 | 16.945 | 12.486 | Primary | 2401
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Consumer Transformation | 9.781 | 8.23 | 8.144 | 8.027 | 7.933 | 7.832 | 7.68 | 6.83 | 4.481 | 2.713 | 1.168 | Primary | 2402
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Consumer Transformation | 8.306 | 7.577 | 7.214 | 6.795 | 6.466 | 6.158 | 5.78 | 4.048 | -0.549 | -4.331 | -7.954 | Primary | 2403
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Consumer Transformation | 30.746 | 30.756 | 30.766 | 30.774 | 30.784 | 30.794 | 30.804 | 30.846 | 30.841 | 30.838 | 30.829 | Primary | 2404
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Consumer Transformation | 9.132 | 9.108 | 24.425 | 24.311 | 24.261 | 24.239 | 24.199 | 23.996 | 22.176 | 20.668 | 19.116 | Primary | 2405
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Consumer Transformation | 8.732 | 7.065 | 21.673 | 21.259 | 20.918 | 20.587 | 20.17 | 18.244 | 13.339 | 9.469 | 5.865 | Primary | 2406
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Consumer Transformation | 9.548 | 9.299 | 8.961 | 8.585 | 8.232 | 7.88 | 7.454 | 5.317 | 1.625 | -1.252 | -3.934 | Primary | 2407
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Consumer Transformation | 12.117 | 12.008 | 11.85 | 11.691 | 11.552 | 11.418 | 11.256 | 10.609 | 9.395 | 8.449 | 7.598 | Primary | 2408
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Consumer Transformation | 20.28 | 19.748 | 19.649 | 19.524 | 19.449 | 19.383 | 19.286 | 18.796 | 16.259 | 14.12 | 12.089 | Primary | 2409
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Consumer Transformation | 10.982 | 10.518 | 9.86 | 9.229 | 8.718 | 8.243 | 7.644 | 4.895 | -0.369 | -4.145 | -7.669 | Primary | 2410
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Consumer Transformation | 12.327 | 11.927 | 11.595 | 11.211 | 10.936 | 10.697 | 10.407 | 9.094 | 4.756 | 1.147 | -2.378 | Primary | 2411
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Consumer Transformation | 10.932 | 10.327 | 9.924 | 9.479 | 9.106 | 8.755 | 8.317 | 6.43 | 2.288 | -1.013 | -4.131 | Primary | 2412
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 4.893 | 4.883 | 4.844 | 4.788 | 4.766 | 4.75 | 4.725 | 4.56 | 3.592 | 2.843 | 2.117 | Primary | 2413
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Consumer Transformation | 4.755 | 4.744 | 4.708 | 4.648 | 4.612 | 4.579 | 4.533 | 4.218 | 3.014 | 2.14 | 1.35 | Primary | 2414
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 7.538 | 7.438 | 7.284 | 7.111 | 6.973 | 6.848 | 6.69 | 5.99 | 4.729 | 3.829 | 2.952 | Primary | 2415
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Consumer Transformation | 7.413 | 7.31 | 7.149 | 6.963 | 6.825 | 6.709 | 6.562 | 5.909 | 4.247 | 2.987 | 1.73 | Primary | 2416
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Consumer Transformation | 13.169 | 12.968 | 12.673 | 12.349 | 12.071 | 11.802 | 11.479 | 10.028 | 5.845 | 2.21 | -1.213 | Primary | 2417
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Consumer Transformation | 22.12 | 21.697 | 21.131 | 20.594 | 20.187 | 19.83 | 19.384 | 17.389 | 13.554 | 10.745 | 7.947 | Primary | 2418
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Consumer Transformation | 29.807 | 28.928 | 28.903 | 28.874 | 28.844 | 28.812 | 28.774 | 28.528 | 28.159 | 27.871 | 27.624 | Primary | 2419
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Consumer Transformation | 5.818 | 5.4 | 5.369 | 5.335 | 5.307 | 5.283 | 5.251 | 5.106 | 4.643 | 4.276 | 3.921 | Primary | 2420
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Consumer Transformation | 11.67 | 11.698 | 11.688 | 11.656 | 11.653 | 11.659 | 11.648 | 11.562 | 9.86 | 8.438 | 7.105 | Primary | 2421
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Falling Short | 5.354 | 5.249 | 5.081 | 4.85 | 4.548 | 4.203 | 3.864 | 2.518 | 1.708 | 1.157 | 0.797 | Primary | 2422
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Falling Short | 11.918 | 11.344 | 9.805 | 9.405 | 8.887 | 8.304 | 7.743 | 5.368 | 3.758 | 2.833 | 2.337 | Primary | 2423
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Falling Short | 7.916 | 7.723 | 9.47 | 9.157 | 8.767 | 8.328 | 7.895 | 6.003 | 4.627 | 3.62 | 2.913 | Primary | 2424
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Falling Short | 6.086 | 5.975 | 5.804 | 5.572 | 5.268 | 4.922 | 4.586 | 3.246 | 2.527 | 2.103 | 1.854 | Primary | 2425
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Falling Short | 26.374 | 26.375 | 26.375 | 26.376 | 26.376 | 26.377 | 26.377 | 26.378 | 26.379 | 26.379 | 26.379 | Primary | 2426
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Falling Short | 2.653 | 2.605 | 2.538 | 2.448 | 2.334 | 2.201 | 2.062 | 1.373 | 0.697 | 0.107 | -0.357 | Primary | 2427
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Falling Short | 4.071 | 4.049 | 4.024 | 3.997 | 3.963 | 3.927 | 3.892 | 3.73 | 3.601 | 3.502 | 3.421 | Primary | 2428
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Falling Short | 4.35 | 4.161 | 3.948 | 3.706 | 3.429 | 3.128 | 2.816 | 1.165 | -0.585 | -2.143 | -3.409 | Primary | 2429
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Falling Short | 8.264 | 8.163 | 8.036 | 7.883 | 7.696 | 7.488 | 7.274 | 6.21 | 5.154 | 4.196 | 3.378 | Primary | 2430
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Falling Short | 12.49 | 12.376 | 12.202 | 11.977 | 11.67 | 11.308 | 10.951 | 9.378 | 8.293 | 7.651 | 7.37 | Primary | 2431
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Falling Short | 4.921 | 4.448 | 4.206 | 3.922 | 3.574 | 3.185 | 2.799 | 1.047 | -0.334 | -1.359 | -2.07 | Primary | 2432
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Falling Short | 11.772 | 11.304 | 11.175 | 11.004 | 10.785 | 10.533 | 10.274 | 9.142 | 8.369 | 7.828 | 7.548 | Primary | 2433
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Falling Short | 7.448 | 7.156 | 6.823 | 6.45 | 6.014 | 5.528 | 5.027 | 2.503 | 0.097 | -1.863 | -3.21 | Primary | 2434
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Falling Short | 6.672 | 6.107 | 5.913 | 5.684 | 5.403 | 5.087 | 4.77 | 3.343 | 2.239 | 1.379 | 0.755 | Primary | 2435
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 13.203 | 13.113 | 12.988 | 12.827 | 12.614 | 12.354 | 11.583 | 8.26 | 6.479 | 5.207 | 4.714 | Primary | 2436
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Falling Short | 16.71 | 16.698 | 16.672 | 16.632 | 16.575 | 16.503 | 16.422 | 15.83 | 14.79 | 13.865 | 13.269 | Primary | 2437
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Falling Short | 9.656 | 8.764 | 8.677 | 8.553 | 8.384 | 8.179 | 7.96 | 6.855 | 5.853 | 5.167 | 4.893 | Primary | 2438
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Falling Short | 10.901 | 10.351 | 10.136 | 9.874 | 9.559 | 9.206 | 8.849 | 7.333 | 6.403 | 5.784 | 5.453 | Primary | 2439
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Falling Short | 16.138 | 16.045 | 15.927 | 15.786 | 15.609 | 15.406 | 15.205 | 14.341 | 13.748 | 13.351 | 13.145 | Primary | 2440
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Falling Short | 10.399 | 10.358 | 10.3 | 10.219 | 10.108 | 9.965 | 9.793 | 8.6 | 7.026 | 5.876 | 5.443 | Primary | 2441
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Falling Short | 21.508 | 21.312 | 21.083 | 20.816 | 20.499 | 20.143 | 19.772 | 17.878 | 16.046 | 14.646 | 13.795 | Primary | 2442
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 17.608 | 17.417 | 17.206 | 16.971 | 16.705 | 16.419 | 16.132 | 14.738 | 13.452 | 12.291 | 11.257 | Primary | 2443
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Falling Short | 13.207 | 12.699 | 12.405 | 12.051 | 11.618 | 11.136 | 10.666 | 8.654 | 7.233 | 6.182 | 5.423 | Primary | 2444
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Falling Short | 7.781 | 7.305 | 7.283 | 7.241 | 7.177 | 7.1 | 7.023 | 6.681 | 6.423 | 6.261 | 6.168 | Primary | 2445
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Falling Short | 8.861 | 8.753 | 8.568 | 8.304 | 7.946 | 7.523 | 7.085 | 4.979 | 3.181 | 1.991 | 1.506 | Primary | 2446
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Falling Short | 7.911 | 7.509 | 7.261 | 6.971 | 6.608 | 6.202 | 5.808 | 4.207 | 3.22 | 2.582 | 2.178 | Primary | 2447
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Falling Short | 8.12 | 8.019 | 7.874 | 7.687 | 7.435 | 7.144 | 6.856 | 5.549 | 4.449 | 3.675 | 3.248 | Primary | 2448
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Falling Short | 9.101 | 8.958 | 8.769 | 8.527 | 8.224 | 7.884 | 7.554 | 6.158 | 5.258 | 4.652 | 4.239 | Primary | 2449
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Falling Short | 3.916 | 3.803 | 3.631 | 3.396 | 3.084 | 2.722 | 2.36 | 0.781 | -0.331 | -1.051 | -1.399 | Primary | 2450
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Falling Short | 7.644 | 7.336 | 6.982 | 6.576 | 6.107 | 5.6 | 5.099 | 2.768 | 0.774 | -0.915 | -2.37 | Primary | 2451
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Falling Short | 10.126 | 9.878 | 9.931 | 9.962 | 9.969 | 9.96 | 9.944 | 9.776 | 9.515 | 9.319 | 9.217 | Primary | 2452
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Falling Short | 6.371 | 5.495 | 5.358 | 5.197 | 4.994 | 4.762 | 4.533 | 3.477 | 2.638 | 2.017 | 1.578 | Primary | 2453
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Falling Short | 16.913 | 15.824 | 15.529 | 15.164 | 14.706 | 14.186 | 13.667 | 11.161 | 8.829 | 7.017 | 5.81 | Primary | 2454
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Falling Short | 12.905 | 12.912 | 12.902 | 12.874 | 12.823 | 12.76 | 12.697 | 12.413 | 12.201 | 12.064 | 11.982 | Primary | 2455
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Falling Short | 6.785 | 6.769 | 6.751 | 6.728 | 6.702 | 6.673 | 6.644 | 6.52 | 6.427 | 6.355 | 6.299 | Primary | 2456
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 12.639 | 12.644 | 12.634 | 12.607 | 12.559 | 12.497 | 12.426 | 12.02 | 11.568 | 11.235 | 11.083 | Primary | 2457
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Falling Short | 16.787 | 16.779 | 16.757 | 16.719 | 16.66 | 16.584 | 16.494 | 15.921 | 15.215 | 14.698 | 14.5 | Primary | 2458
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Falling Short | 4.723 | 4.708 | 4.689 | 4.668 | 4.641 | 4.61 | 4.58 | 4.43 | 4.292 | 4.171 | 4.063 | Primary | 2459
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Falling Short | 9.185 | 9.125 | 9.05 | 8.96 | 8.847 | 8.719 | 8.596 | 8.081 | 7.769 | 7.585 | 7.493 | Primary | 2460
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Falling Short | 10.318 | 10.229 | 10.102 | 9.936 | 9.715 | 9.461 | 9.213 | 8.159 | 7.483 | 7.073 | 6.853 | Primary | 2461
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Falling Short | 23.089 | 22.804 | 22.786 | 22.756 | 22.709 | 22.65 | 22.592 | 22.362 | 22.253 | 22.186 | 22.144 | Primary | 2462
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Falling Short | 6.708 | 6.668 | 6.594 | 6.483 | 6.318 | 6.111 | 5.885 | 4.638 | 3.331 | 2.431 | 2.1 | Primary | 2463
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Falling Short | 5.049 | 4.491 | 4.275 | 3.972 | 3.561 | 3.074 | 2.58 | 0.203 | -1.846 | -3.169 | -3.678 | Primary | 2464
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Falling Short | 12.022 | 10.896 | 10.744 | 10.54 | 10.269 | 9.957 | 9.649 | 8.266 | 7.221 | 6.568 | 6.235 | Primary | 2465
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 8.931 | 8.856 | 8.747 | 8.605 | 8.412 | 8.184 | 7.956 | 6.949 | 6.255 | 5.834 | 5.645 | Primary | 2466
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Falling Short | 14.279 | 14.142 | 13.962 | 13.741 | 13.455 | 13.128 | 12.807 | 11.511 | 10.803 | 10.376 | 10.135 | Primary | 2467
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Falling Short | 4.093 | 3.617 | 3.52 | 3.402 | 3.255 | 3.094 | 2.934 | 2.135 | 1.369 | 0.695 | 0.079 | Primary | 2468
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Falling Short | 18.277 | 18.188 | 18.057 | 17.879 | 17.643 | 17.372 | 17.101 | 15.87 | 14.92 | 14.31 | 14.027 | Primary | 2469
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Falling Short | 18.836 | 18.809 | 18.775 | 18.733 | 18.681 | 18.623 | 18.565 | 18.285 | 18.037 | 17.805 | 17.585 | Primary | 2470
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Falling Short | 8.046 | 7.989 | 7.898 | 7.779 | 7.612 | 7.415 | 7.222 | 6.379 | 5.829 | 5.501 | 5.336 | Primary | 2471
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Falling Short | 8.941 | 8.902 | 8.851 | 8.787 | 8.704 | 8.608 | 8.499 | 7.86 | 7.122 | 6.508 | 6.11 | Primary | 2472
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Falling Short | 1.573 | 1.503 | 1.381 | 1.203 | 0.964 | 0.687 | 0.413 | -0.725 | -1.409 | -1.897 | -2.242 | Primary | 2473
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Falling Short | 5.627 | 5.229 | 4.771 | 4.29 | 3.695 | 3.019 | 2.357 | -0.443 | -2.224 | -3.319 | -3.85 | Primary | 2474
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Falling Short | 10.426 | 10.231 | 9.231 | 8.918 | 8.528 | 8.089 | 7.65 | 5.633 | 3.897 | 2.606 | 1.765 | Primary | 2475
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Falling Short | 15.503 | 15.134 | 15.062 | 14.969 | 14.85 | 14.711 | 14.557 | 13.674 | 12.662 | 11.82 | 11.253 | Primary | 2476
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Falling Short | 10.743 | 9.433 | 9.324 | 9.155 | 8.919 | 8.64 | 8.359 | 7.034 | 5.924 | 5.192 | 4.814 | Primary | 2477
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Falling Short | 8.009 | 7.812 | 7.545 | 7.211 | 6.79 | 6.311 | 5.837 | 3.841 | 2.614 | 1.866 | 1.521 | Primary | 2478
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Falling Short | 22.787 | 22.596 | 22.348 | 22.064 | 21.686 | 21.245 | 20.821 | 19 | 17.802 | 17.131 | 16.816 | Primary | 2479
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Falling Short | 5.019 | 4.862 | 4.657 | 4.398 | 4.08 | 3.724 | 3.365 | 1.766 | 0.522 | -0.451 | -1.166 | Primary | 2480
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Falling Short | 11.76 | 11.678 | 11.564 | 11.424 | 11.246 | 11.047 | 10.85 | 10.099 | 9.745 | 9.509 | 9.35 | Primary | 2481
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Falling Short | 18.228 | 18.175 | 18.091 | 17.974 | 17.815 | 17.628 | 17.439 | 16.559 | 15.858 | 15.384 | 15.138 | Primary | 2482
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Falling Short | 9.265 | 9.288 | 7.853 | 7.836 | 7.795 | 7.735 | 7.664 | 7.19 | 6.581 | 6.141 | 5.965 | Primary | 2483
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Falling Short | 27.393 | 27.409 | 27.413 | 27.399 | 27.367 | 27.315 | 27.242 | 26.641 | 25.765 | 25.139 | 24.956 | Primary | 2484
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Falling Short | 14.36 | 13.885 | 13.896 | 13.892 | 13.87 | 13.835 | 13.795 | 13.606 | 13.469 | 13.329 | 13.204 | Primary | 2485
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Falling Short | 2.752 | 2.584 | 2.332 | 1.982 | 1.504 | 0.913 | 0.258 | -3.603 | -7.966 | -11.015 | -12.118 | Primary | 2486
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Falling Short | 17.932 | 17.951 | 17.96 | 17.958 | 17.947 | 17.928 | 17.904 | 17.718 | 17.438 | 17.118 | 16.785 | Primary | 2487
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 7.441 | 7.043 | 6.792 | 6.489 | 6.112 | 5.691 | 5.282 | 3.501 | 2.179 | 1.22 | 0.556 | Primary | 2488
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Falling Short | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2489
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Falling Short | 2.982 | 2.973 | 2.935 | 2.869 | 2.771 | 2.652 | 2.532 | 2.043 | 1.727 | 1.49 | 1.32 | Primary | 2490
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Falling Short | 14.293 | 14.111 | 13.881 | 13.605 | 13.257 | 12.864 | 12.473 | 10.651 | 9.19 | 8.19 | 7.597 | Primary | 2491
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Falling Short | 15.147 | 12.735 | 12.738 | 12.72 | 12.668 | 12.593 | 12.508 | 12.019 | 11.514 | 11.16 | 11.038 | Primary | 2492
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Falling Short | 8.589 | 8.038 | 7.75 | 7.411 | 6.979 | 6.489 | 6.007 | 3.783 | 1.951 | 0.59 | -0.376 | Primary | 2493
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Falling Short | 18.359 | 18.298 | 18.222 | 18.131 | 18.016 | 17.887 | 17.76 | 17.164 | 16.652 | 16.228 | 15.858 | Primary | 2494
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Falling Short | 8.541 | 8.335 | 8.053 | 7.699 | 7.245 | 6.733 | 6.232 | 4.143 | 2.813 | 1.979 | 1.486 | Primary | 2495
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Falling Short | 4.113 | 3.522 | 3.237 | 2.883 | 2.439 | 1.937 | 1.435 | -0.88 | -2.822 | -4.245 | -5.1 | Primary | 2496
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Falling Short | 2.942 | 2.783 | 2.585 | 2.359 | 2.076 | 1.753 | 1.44 | 0.144 | -0.617 | -1.083 | -1.33 | Primary | 2497
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Falling Short | 8.489 | 8.483 | 8.467 | 23.839 | 23.797 | 23.742 | 23.675 | 23.231 | 22.649 | 22.23 | 22.083 | Primary | 2498
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Falling Short | 21.019 | 20.747 | 20.742 | 20.731 | 20.715 | 20.697 | 20.679 | 20.596 | 20.513 | 20.457 | 20.415 | Primary | 2499
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Falling Short | 19.151 | 19.103 | 19.022 | 18.908 | 18.752 | 18.571 | 18.39 | 17.587 | 16.91 | 16.416 | 16.117 | Primary | 2500
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Falling Short | 16.589 | 16.657 | 16.72 | 16.776 | 16.828 | 16.874 | 16.916 | 17.063 | 17.134 | 17.16 | 17.171 | Primary | 2501
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Falling Short | 14.622 | 14.678 | 14.715 | 14.733 | 14.724 | 14.694 | 14.657 | 14.398 | 14.077 | 13.839 | 13.731 | Primary | 2502
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Falling Short | 1.29 | 1.284 | 1.242 | 1.153 | 20.906 | 20.701 | 20.436 | 18.575 | 16.129 | 14.374 | 13.829 | Primary | 2503
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Falling Short | 7.677 | 7.481 | 7.239 | 6.953 | 6.603 | 6.213 | 5.833 | 4.243 | 3.235 | 2.532 | 2.023 | Primary | 2504
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Falling Short | 6.868 | 6.705 | 6.483 | 6.203 | 5.841 | 5.427 | 5.019 | 3.209 | 1.788 | 0.832 | 0.312 | Primary | 2505
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Falling Short | 17.704 | 17.64 | 17.559 | 17.46 | 17.337 | 17.198 | 17.057 | 16.38 | 15.8 | 15.374 | 15.108 | Primary | 2506
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Falling Short | 6.607 | 6.519 | 6.404 | 6.263 | 6.084 | 5.879 | 5.673 | 4.751 | 4.054 | 3.547 | 3.216 | Primary | 2507
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Falling Short | 6.899 | 6.714 | 6.497 | 6.251 | 5.949 | 5.613 | 5.282 | 3.774 | 2.596 | 1.773 | 1.231 | Primary | 2508
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Falling Short | 18.62 | 18.615 | 18.601 | 18.576 | 18.538 | 18.491 | 18.441 | 18.191 | 17.961 | 17.799 | 17.724 | Primary | 2509
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Falling Short | 6.999 | 6.887 | 6.737 | 6.56 | 6.333 | 6.076 | 5.824 | 4.827 | 4.258 | 3.869 | 3.613 | Primary | 2510
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Falling Short | 2.79 | 2.783 | 2.774 | 2.761 | 2.743 | 2.722 | 2.702 | 2.608 | 2.532 | 2.489 | 2.468 | Primary | 2511
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Falling Short | 9.132 | 8.795 | 8.7 | 8.583 | 8.44 | 8.274 | 8.101 | 7.201 | 6.298 | 5.539 | 4.994 | Primary | 2512
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Falling Short | 15.048 | 14.954 | 14.833 | 14.684 | 14.496 | 14.286 | 14.081 | 13.205 | 12.614 | 12.224 | 11.958 | Primary | 2513
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Falling Short | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary | 2514
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Falling Short | 21.25 | 21.184 | 21.098 | 20.993 | 20.858 | 20.703 | 20.552 | 19.893 | 19.44 | 19.165 | 19.031 | Primary | 2515
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Falling Short | 8.444 | 8.333 | 8.185 | 8.008 | 7.782 | 7.528 | 7.278 | 6.257 | 5.648 | 5.214 | 4.893 | Primary | 2516
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Falling Short | 14.175 | 14.063 | 13.919 | 13.744 | 13.525 | 13.28 | 13.035 | 11.94 | 11.106 | 10.502 | 10.112 | Primary | 2517
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Falling Short | 33.322 | 32.977 | 32.97 | 32.955 | 32.933 | 32.905 | 32.878 | 32.764 | 32.686 | 32.64 | 32.611 | Primary | 2518
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Falling Short | 4.217 | 3.684 | 3.447 | 3.136 | 2.727 | 2.261 | 1.812 | -0.015 | -1.104 | -1.737 | -2.082 | Primary | 2519
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Falling Short | 14.785 | 14.054 | 13.801 | 13.51 | 13.18 | 12.822 | 12.447 | 10.403 | 7.974 | 5.835 | 4.188 | Primary | 2520
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Falling Short | 11.862 | 11.74 | 11.583 | 11.387 | 11.143 | 10.868 | 10.584 | 9.205 | 7.999 | 7.084 | 6.504 | Primary | 2521
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Falling Short | 14.914 | 14.868 | 14.81 | 14.739 | 14.652 | 14.553 | 14.448 | 13.902 | 13.341 | 12.866 | 12.516 | Primary | 2522
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Falling Short | 24.411 | 22.711 | 22.563 | 22.381 | 22.151 | 21.891 | 21.64 | 20.633 | 20.062 | 19.73 | 19.564 | Primary | 2523
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Falling Short | 5.126 | 4.618 | 4.326 | 3.994 | 3.612 | 3.199 | 2.783 | 0.87 | -0.732 | -2.105 | -3.257 | Primary | 2524
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Falling Short | 1.373 | 0.78 | 0.502 | 0.178 | -0.221 | -0.666 | -1.099 | -2.937 | -4.188 | -5.099 | -5.797 | Primary | 2525
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Falling Short | 3.332 | 3.293 | 1.963 | 1.906 | 1.837 | 1.757 | 1.676 | 1.273 | 0.906 | 0.613 | 0.409 | Primary | 2526
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Falling Short | 8.826 | 8.455 | 10.291 | 10.092 | 9.827 | 9.52 | 9.217 | 7.891 | 6.997 | 6.453 | 6.186 | Primary | 2527
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Falling Short | 7.162 | 7.161 | 7.133 | 7.074 | 6.982 | 6.871 | 6.757 | 6.248 | 5.85 | 5.551 | 5.347 | Primary | 2528
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Falling Short | 32.707 | 31.327 | 31.272 | 31.205 | 31.125 | 31.033 | 30.933 | 30.463 | 30.094 | 29.821 | 29.693 | Primary | 2529
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Falling Short | 12.213 | 12.128 | 12.011 | 11.858 | 11.662 | 11.439 | 11.222 | 10.344 | 9.868 | 9.582 | 9.416 | Primary | 2530
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Falling Short | 8.956 | 8.335 | 8.194 | 8.044 | 7.86 | 7.655 | 7.455 | 6.679 | 6.309 | 6.088 | 5.949 | Primary | 2531
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Falling Short | 8.7 | 8.731 | 8.751 | 8.759 | 8.755 | 8.741 | 8.72 | 8.572 | 8.355 | 8.145 | 7.989 | Primary | 2532
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Falling Short | 13.929 | 13.902 | 13.853 | 13.774 | 13.665 | 13.539 | 13.413 | 12.838 | 12.398 | 12.126 | 11.987 | Primary | 2533
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Falling Short | 14.531 | 14.429 | 14.296 | 14.119 | 13.89 | 13.609 | 13.279 | 11.056 | 8.154 | 5.888 | 4.71 | Primary | 2534
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Falling Short | 18.67 | 18.499 | 18.311 | 18.1 | 17.868 | 17.622 | 17.374 | 16.14 | 14.956 | 13.816 | 12.709 | Primary | 2535
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Falling Short | 5.465 | 4.421 | 4.154 | 3.856 | 3.523 | 3.168 | 2.807 | 0.979 | -0.878 | -2.567 | -4.038 | Primary | 2536
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Falling Short | 5.607 | 4.317 | 3.679 | 2.931 | 2.041 | 1.066 | 0.119 | -4.035 | -7.422 | -10.246 | -12.558 | Primary | 2537
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Falling Short | 13.373 | 12.709 | 12.53 | 12.338 | 12.096 | 11.822 | 11.559 | 10.445 | 9.68 | 9.175 | 8.827 | Primary | 2538
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Falling Short | 15.842 | 15.166 | 14.996 | 14.775 | 14.485 | 14.151 | 13.825 | 12.49 | 11.681 | 11.185 | 10.923 | Primary | 2539
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Falling Short | 9.937 | 9.867 | 9.752 | 9.591 | 9.374 | 9.122 | 8.876 | 7.866 | 7.275 | 6.927 | 6.749 | Primary | 2540
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Falling Short | 10.988 | 10.978 | 10.964 | 10.943 | 10.918 | 10.889 | 10.858 | 10.657 | 10.406 | 10.133 | 9.857 | Primary | 2541
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Falling Short | 21.433 | 21.371 | 21.291 | 21.19 | 21.067 | 20.931 | 20.795 | 20.168 | 19.592 | 19.074 | 18.634 | Primary | 2542
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Falling Short | 16.14 | 16.21 | 16.27 | 16.317 | 16.352 | 16.379 | 16.403 | 16.455 | 16.427 | 16.392 | 16.362 | Primary | 2543
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 10.821 | 10.62 | 10.367 | 10.067 | 9.697 | 9.285 | 8.882 | 7.157 | 5.936 | 5.046 | 4.416 | Primary | 2544
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Falling Short | 21.886 | 21.855 | 21.817 | 21.771 | 21.714 | 21.652 | 21.588 | 21.285 | 21.015 | 20.763 | 20.528 | Primary | 2545
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Falling Short | 2.618 | 2.517 | 2.364 | 2.158 | 1.886 | 1.575 | 1.27 | 0.068 | -0.577 | -0.994 | -1.262 | Primary | 2546
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Falling Short | 6.605 | 6.6 | 6.593 | 6.582 | 6.567 | 6.549 | 6.532 | 6.46 | 6.411 | 6.383 | 6.367 | Primary | 2547
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Falling Short | 7.94 | 7.27 | 7.172 | 7.049 | 6.889 | 6.705 | 6.52 | 5.748 | 5.272 | 4.944 | 4.751 | Primary | 2548
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Falling Short | 12.993 | 12.669 | 12.246 | 11.72 | 11.059 | 10.307 | 9.551 | 6.066 | 3.261 | 1.312 | 0.28 | Primary | 2549
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Falling Short | 10.419 | 9.055 | 8.416 | 8.172 | 7.849 | 7.473 | 7.092 | 5.345 | 3.985 | 3.098 | 2.713 | Primary | 2550
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Falling Short | 3.89 | 3.734 | 3.56 | 3.362 | 3.135 | 2.886 | 2.631 | 1.347 | 0.11 | -0.917 | -1.69 | Primary | 2551
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Falling Short | 3.853 | 3.753 | 3.649 | 3.54 | 3.425 | 3.306 | 3.185 | 2.555 | 1.9 | 1.25 | 0.623 | Primary | 2552
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Falling Short | 3.048 | 2.725 | 23.922 | 23.783 | 23.598 | 23.377 | 23.131 | 21.654 | 19.911 | 18.561 | 17.822 | Primary | 2553
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Falling Short | 13.921 | 13.528 | 13.357 | 13.14 | 12.857 | 12.531 | 12.22 | 10.939 | 10.18 | 9.765 | 9.573 | Primary | 2554
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Falling Short | 4.37 | 4.27 | 4.151 | 4.015 | 3.853 | 3.676 | 3.506 | 2.789 | 2.316 | 1.957 | 1.663 | Primary | 2555
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Falling Short | 3.585 | 3.488 | 3.375 | 3.247 | 3.095 | 2.925 | 2.755 | 1.936 | 1.22 | 0.667 | 0.28 | Primary | 2556
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Falling Short | 13.964 | 13.471 | 13.323 | 13.114 | 12.832 | 12.505 | 12.19 | 10.815 | 9.845 | 9.25 | 8.913 | Primary | 2557
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Falling Short | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2558
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Falling Short | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2559
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Falling Short | 17.573 | 17.099 | 16.997 | 16.868 | 16.7 | 16.51 | 16.322 | 15.526 | 14.989 | 14.6 | 14.32 | Primary | 2560
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Falling Short | 15.21 | 14.14 | 14.061 | 13.969 | 13.86 | 13.738 | 13.611 | 12.924 | 12.204 | 11.594 | 11.14 | Primary | 2561
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Falling Short | 10.87 | 10.782 | 10.66 | 10.508 | 10.308 | 10.076 | 9.84 | 8.779 | 7.983 | 7.451 | 7.196 | Primary | 2562
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Falling Short | 13.019 | 12.842 | 12.633 | 12.397 | 12.107 | 11.782 | 11.461 | 9.995 | 8.864 | 8.056 | 7.516 | Primary | 2563
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Falling Short | 10.407 | 9.622 | 9.47 | 9.282 | 9.054 | 8.8 | 8.546 | 7.409 | 6.53 | 5.828 | 5.297 | Primary | 2564
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Falling Short | 11.224 | 11.181 | 11.109 | 11.011 | 10.874 | 10.712 | 10.542 | 9.734 | 9.05 | 8.575 | 8.355 | Primary | 2565
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Falling Short | 18.617 | 17.836 | 17.84 | 17.824 | 17.788 | 17.738 | 17.683 | 17.376 | 17.057 | 16.824 | 16.696 | Primary | 2566
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Falling Short | 16.42 | 16.255 | 16.043 | 15.783 | 15.454 | 15.07 | 14.673 | 12.683 | 10.834 | 9.489 | 8.761 | Primary | 2567
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Falling Short | 8.91 | 8.842 | 8.748 | 8.631 | 8.477 | 8.298 | 8.126 | 7.392 | 6.925 | 6.665 | 6.557 | Primary | 2568
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Falling Short | 12.71 | 12.4 | 10.741 | 10.519 | 10.224 | 9.879 | 9.527 | 7.79 | 6.089 | 4.79 | 4.028 | Primary | 2569
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Falling Short | 23.071 | 13.618 | 6.659 | 6.417 | 6.115 | 5.771 | 5.417 | 3.68 | 2.034 | 0.753 | -0.075 | Primary | 2570
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Falling Short | 2.564 | 2.013 | 1.691 | -0.47 | -0.93 | -1.453 | -1.957 | -4.091 | -5.484 | -6.41 | -7.043 | Primary | 2571
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Falling Short | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2572
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Falling Short | 5.424 | 5.316 | 5.194 | 5.057 | 4.9 | 4.728 | 4.549 | 3.613 | 2.654 | 1.83 | 1.195 | Primary | 2573
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Falling Short | 12.02 | 11.263 | 11.069 | 10.833 | 10.544 | 10.224 | 9.902 | 8.313 | 6.641 | 5.211 | 4.14 | Primary | 2574
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 7.877 | 6.278 | 6.261 | 6.214 | 6.133 | 6.03 | 5.922 | 5.335 | 4.737 | 4.334 | 4.153 | Primary | 2575
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Falling Short | 27.936 | 27.948 | 27.958 | 27.968 | 27.977 | 27.985 | 27.992 | 28.019 | 28.032 | 28.037 | 28.039 | Primary | 2576
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Falling Short | 19.949 | 19.006 | 18.823 | 18.599 | 18.323 | 18.016 | 17.717 | 16.473 | 15.684 | 15.12 | 14.701 | Primary | 2577
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Falling Short | 8.073 | 7.359 | 7.423 | 7.443 | 7.41 | 7.323 | 7.186 | 5.933 | 4.01 | 2.618 | 2.202 | Primary | 2578
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Falling Short | 3.989 | 3.804 | 3.68 | 3.553 | 3.42 | 3.284 | 3.144 | 2.389 | 1.553 | 0.662 | -0.254 | Primary | 2579
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Falling Short | 14.394 | 14.247 | 14.061 | 13.84 | 13.566 | 13.257 | 12.958 | 11.781 | 11.2 | 10.85 | 10.626 | Primary | 2580
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Falling Short | 2.466 | 2.238 | 1.967 | 1.651 | 1.269 | 0.846 | 0.421 | -1.612 | -3.362 | -4.689 | -5.599 | Primary | 2581
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Falling Short | 8.77 | 7.934 | 7.769 | 7.566 | 7.312 | 7.028 | 6.753 | 5.584 | 4.78 | 4.244 | 3.89 | Primary | 2582
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Falling Short | 25.198 | 24.78 | 24.528 | 24.222 | 23.845 | 23.424 | 23.008 | 21.179 | 19.85 | 18.903 | 18.271 | Primary | 2583
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Falling Short | 11.719 | 11.638 | 11.499 | 11.306 | 11.042 | 10.733 | 10.429 | 9.123 | 8.162 | 7.521 | 7.181 | Primary | 2584
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Falling Short | 11.308 | 11.133 | 10.911 | 10.645 | 10.315 | 9.945 | 9.586 | 8.042 | 6.953 | 6.192 | 5.65 | Primary | 2585
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Falling Short | 13.803 | 13.566 | 13.627 | 13.672 | 13.704 | 13.724 | 13.741 | 13.763 | 13.717 | 13.662 | 13.616 | Primary | 2586
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Falling Short | 32.7 | 32.378 | 32.015 | 31.616 | 31.15 | 30.643 | 30.143 | 27.958 | 26.365 | 25.1 | 24.066 | Primary | 2587
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Falling Short | 9.695 | 8.142 | 8.099 | 8.027 | 7.918 | 7.781 | 7.637 | 6.928 | 6.339 | 5.955 | 5.817 | Primary | 2588
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Falling Short | 8.255 | 7.592 | 7.386 | 7.133 | 6.826 | 6.484 | 6.146 | 4.745 | 3.918 | 3.343 | 2.944 | Primary | 2589
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Falling Short | 30.729 | 30.736 | 30.741 | 30.746 | 30.75 | 30.753 | 30.756 | 30.767 | 30.773 | 30.773 | 30.773 | Primary | 2590
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Falling Short | 8.998 | 9.001 | 24.389 | 24.359 | 24.312 | 24.253 | 24.194 | 23.948 | 23.772 | 23.629 | 23.521 | Primary | 2591
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Falling Short | 8.752 | 7.208 | 22.032 | 21.818 | 21.541 | 21.225 | 20.918 | 19.596 | 18.731 | 18.219 | 17.959 | Primary | 2592
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Falling Short | 9.46 | 9.266 | 9.041 | 8.778 | 8.466 | 8.123 | 7.775 | 6.026 | 4.343 | 3.001 | 2.026 | Primary | 2593
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Falling Short | 12.141 | 12.075 | 11.99 | 11.89 | 11.765 | 11.624 | 11.49 | 10.986 | 10.772 | 10.663 | 10.603 | Primary | 2594
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Falling Short | 20.218 | 19.694 | 19.65 | 19.585 | 19.494 | 19.385 | 19.277 | 18.836 | 18.612 | 18.469 | 18.388 | Primary | 2595
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Falling Short | 11 | 10.798 | 10.541 | 10.243 | 9.853 | 9.401 | 8.955 | 6.992 | 5.594 | 4.731 | 4.341 | Primary | 2596
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Falling Short | 12.266 | 11.952 | 11.787 | 11.582 | 11.334 | 11.057 | 10.785 | 9.709 | 9.169 | 8.808 | 8.573 | Primary | 2597
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Falling Short | 10.928 | 10.449 | 10.268 | 10.037 | 9.74 | 9.403 | 9.076 | 7.779 | 7.106 | 6.736 | 6.534 | Primary | 2598
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 4.859 | 4.862 | 4.859 | 4.847 | 4.826 | 4.799 | 4.772 | 4.626 | 4.484 | 4.387 | 4.338 | Primary | 2599
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Falling Short | 4.702 | 4.705 | 4.698 | 4.681 | 4.652 | 4.614 | 4.571 | 4.308 | 3.984 | 3.757 | 3.663 | Primary | 2600
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 7.533 | 7.5 | 7.451 | 7.384 | 7.294 | 7.19 | 7.088 | 6.648 | 6.325 | 6.125 | 6.02 | Primary | 2601
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Falling Short | 7.393 | 7.362 | 7.316 | 7.252 | 7.167 | 7.069 | 6.975 | 6.563 | 6.246 | 6.043 | 5.92 | Primary | 2602
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Falling Short | 13.166 | 13.011 | 12.824 | 12.603 | 12.337 | 12.044 | 11.759 | 10.604 | 9.942 | 9.47 | 9.097 | Primary | 2603
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Falling Short | 22.142 | 21.965 | 21.75 | 21.512 | 21.208 | 20.863 | 20.527 | 19.04 | 17.942 | 17.188 | 16.696 | Primary | 2604
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Falling Short | 29.718 | 28.795 | 28.73 | 28.662 | 28.589 | 28.512 | 28.431 | 27.982 | 27.471 | 26.977 | 26.537 | Primary | 2605
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Falling Short | 5.803 | 5.393 | 5.38 | 5.363 | 5.34 | 5.314 | 5.288 | 5.171 | 5.076 | 5.008 | 4.959 | Primary | 2606
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Falling Short | 11.56 | 11.567 | 11.562 | 11.541 | 11.505 | 11.458 | 11.409 | 11.194 | 11.043 | 10.92 | 10.833 | Primary | 2607
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - Leading the Way | 5.477 | 4.966 | 4.183 | 3.31 | 2.809 | 2.508 | 1.89 | -4.757 | -9.662 | -12.875 | -12.185 | Primary | 2608
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - Leading the Way | 11.964 | 10.888 | 8.616 | 7.497 | 6.719 | 6.124 | 5.241 | -5.37 | -13.177 | -18.601 | -17.617 | Primary | 2609
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - Leading the Way | 7.957 | 7.486 | 8.77 | 7.974 | 7.462 | 7.062 | 6.375 | -0.147 | -4.873 | -8.053 | -7.745 | Primary | 2610
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - Leading the Way | 6.18 | 5.824 | 5.225 | 4.531 | 4.118 | 3.823 | 3.222 | -3.182 | -7.975 | -11.302 | -10.738 | Primary | 2611
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - Leading the Way | 26.375 | 26.377 | 26.378 | 26.379 | 26.38 | 26.381 | 26.382 | 26.386 | 26.389 | 26.391 | 26.394 | Primary | 2612
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - Leading the Way | 2.809 | 2.729 | 2.567 | 2.376 | 2.282 | 2.223 | 2.065 | -0.118 | -1.769 | -2.873 | -2.588 | Primary | 2613
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - Leading the Way | 4.072 | 4.043 | 4.005 | 3.967 | 3.932 | 3.898 | 3.849 | 3.516 | 3.289 | 3.131 | 3.1 | Primary | 2614
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - Leading the Way | 4.586 | 4.378 | 4.085 | 3.755 | 3.498 | 3.272 | 2.946 | -0.335 | -2.978 | -4.912 | -5.186 | Primary | 2615
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - Leading the Way | 8.492 | 8.304 | 8.007 | 7.683 | 7.502 | 7.396 | 7.155 | 3.707 | 0.978 | -0.985 | -0.733 | Primary | 2616
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - Leading the Way | 12.467 | 12.11 | 11.549 | 10.961 | 10.542 | 10.181 | 9.582 | 4.906 | 1.794 | 0.039 | 0.55 | Primary | 2617
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - Leading the Way | 4.98 | 4.317 | 3.751 | 3.147 | 2.722 | 2.365 | 1.718 | -5.45 | -11.054 | -15.212 | -14.982 | Primary | 2618
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - Leading the Way | 11.843 | 11.209 | 10.784 | 10.294 | 10.009 | 9.804 | 9.328 | 3.761 | -0.436 | -3.393 | -2.906 | Primary | 2619
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - Leading the Way | 7.509 | 7.027 | 6.361 | 5.635 | 5.129 | 4.685 | 3.997 | -1.75 | -5.944 | -8.613 | -8.762 | Primary | 2620
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - Leading the Way | 6.742 | 6.035 | 5.558 | 5.024 | 4.705 | 4.451 | 3.94 | -1.126 | -4.88 | -7.417 | -7.104 | Primary | 2621
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 13.286 | 13.107 | 12.807 | 12.45 | 12.151 | 11.841 | 10.881 | 5.35 | 2.708 | 1.356 | 1.537 | Primary | 2622
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - Leading the Way | 16.82 | 16.724 | 16.591 | 16.446 | 16.317 | 16.197 | 16.055 | 14.801 | 13.968 | 13.695 | 14.006 | Primary | 2623
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - Leading the Way | 9.699 | 8.747 | 8.516 | 8.231 | 8.019 | 7.81 | 7.376 | 2.473 | -1.233 | -3.772 | -3.334 | Primary | 2624
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - Leading the Way | 10.897 | 10.204 | 9.74 | 9.225 | 8.842 | 8.509 | 7.897 | 1.844 | -2.694 | -5.956 | -5.609 | Primary | 2625
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - Leading the Way | 16.096 | 15.862 | 15.517 | 15.147 | 14.898 | 14.699 | 14.298 | 10.244 | 7.209 | 5.086 | 5.39 | Primary | 2626
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - Leading the Way | 10.404 | 10.297 | 10.128 | 9.914 | 9.706 | 9.475 | 9.14 | 6.216 | 4.14 | 3.057 | 3.051 | Primary | 2627
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - Leading the Way | 21.552 | 21.218 | 20.76 | 20.268 | 19.858 | 19.472 | 18.892 | 13.462 | 9.282 | 6.32 | 6.126 | Primary | 2628
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 17.766 | 17.59 | 17.338 | 17.057 | 16.837 | 16.632 | 16.298 | 13.014 | 10.345 | 8.246 | 7.998 | Primary | 2629
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - Leading the Way | 13.182 | 12.325 | 11.479 | 10.549 | 9.948 | 9.48 | 8.672 | 1.072 | -4.448 | -8.173 | -7.756 | Primary | 2630
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - Leading the Way | 7.86 | 7.293 | 7.12 | 6.932 | 6.836 | 6.787 | 6.651 | 4.25 | 2.425 | 1.145 | 1.522 | Primary | 2631
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - Leading the Way | 9.063 | 8.536 | 7.698 | 6.751 | 6.141 | 5.702 | 4.932 | -2.966 | -8.696 | -12.211 | -11.642 | Primary | 2632
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - Leading the Way | 7.869 | 7.154 | 6.463 | 5.788 | 5.289 | 4.895 | 4.306 | -0.911 | -4.417 | -6.67 | -6.195 | Primary | 2633
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - Leading the Way | 8.047 | 7.643 | 7.056 | 6.429 | 6.011 | 5.7 | 5.125 | -0.776 | -4.987 | -7.729 | -7.131 | Primary | 2634
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - Leading the Way | 9.132 | 8.876 | 8.467 | 8 | 7.643 | 7.328 | 6.781 | 1.4 | -2.568 | -5.456 | -5.173 | Primary | 2635
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - Leading the Way | 3.92 | 3.57 | 2.98 | 2.287 | 1.845 | 1.485 | 0.768 | -6.556 | -12.008 | -15.727 | -15.159 | Primary | 2636
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - Leading the Way | 7.8 | 7.365 | 6.763 | 6.106 | 5.599 | 5.157 | 4.504 | -1.599 | -6.386 | -10.051 | -10.429 | Primary | 2637
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - Leading the Way | 10.349 | 10.14 | 10.194 | 10.221 | 10.289 | 10.365 | 10.361 | 8.523 | 7.121 | 6.147 | 6.788 | Primary | 2638
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - Leading the Way | 6.446 | 5.496 | 5.21 | 4.92 | 4.701 | 4.503 | 4.166 | 0.787 | -1.733 | -3.519 | -3.363 | Primary | 2639
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - Leading the Way | 17.021 | 15.541 | 14.633 | 13.641 | 12.97 | 12.433 | 11.568 | 3.275 | -2.766 | -6.625 | -6.119 | Primary | 2640
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - Leading the Way | 12.987 | 12.938 | 12.823 | 12.689 | 12.629 | 12.601 | 12.499 | 10.799 | 9.571 | 8.74 | 9.05 | Primary | 2641
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - Leading the Way | 6.783 | 6.75 | 6.704 | 6.655 | 6.621 | 6.593 | 6.55 | 6.163 | 5.885 | 5.694 | 5.706 | Primary | 2642
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 12.717 | 12.68 | 12.587 | 12.463 | 12.4 | 12.36 | 12.231 | 10.096 | 8.49 | 7.421 | 7.765 | Primary | 2643
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - Leading the Way | 16.819 | 16.731 | 16.585 | 16.402 | 16.288 | 16.198 | 16.011 | 13.704 | 12.013 | 10.985 | 11.197 | Primary | 2644
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - Leading the Way | 4.763 | 4.697 | 4.6 | 4.499 | 4.454 | 4.442 | 4.385 | 3.31 | 2.424 | 1.759 | 1.83 | Primary | 2645
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - Leading the Way | 9.158 | 8.977 | 8.709 | 8.424 | 8.256 | 8.129 | 7.885 | 5.392 | 3.568 | 2.353 | 2.574 | Primary | 2646
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - Leading the Way | 10.332 | 10.088 | 9.692 | 9.254 | 8.969 | 8.735 | 8.267 | 3.01 | -0.859 | -3.549 | -2.979 | Primary | 2647
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - Leading the Way | 23.143 | 22.855 | 22.803 | 22.741 | 22.711 | 22.69 | 22.581 | 21.122 | 20.044 | 19.297 | 19.629 | Primary | 2648
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - Leading the Way | 6.79 | 6.639 | 6.353 | 6.021 | 5.792 | 5.575 | 5.152 | 0.488 | -2.86 | -4.856 | -4.242 | Primary | 2649
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - Leading the Way | 5.08 | 4.152 | 3.353 | 2.444 | 1.799 | 1.247 | 0.371 | -7.385 | -12.787 | -15.926 | -15.282 | Primary | 2650
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - Leading the Way | 12.053 | 10.714 | 10.208 | 9.642 | 9.268 | 8.963 | 8.393 | 1.519 | -3.571 | -7.118 | -6.422 | Primary | 2651
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 8.941 | 8.794 | 8.538 | 8.267 | 8.043 | 7.822 | 7.415 | 3.578 | 0.9 | -0.89 | -0.521 | Primary | 2652
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - Leading the Way | 14.26 | 13.944 | 13.448 | 12.921 | 12.565 | 12.267 | 11.646 | 5.242 | 0.458 | -2.973 | -2.448 | Primary | 2653
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - Leading the Way | 4.28 | 3.781 | 3.614 | 3.437 | 3.324 | 3.244 | 3.099 | 0.397 | -1.787 | -3.504 | -3.328 | Primary | 2654
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - Leading the Way | 18.299 | 18.056 | 17.662 | 17.209 | 16.879 | 16.594 | 16.064 | 10.426 | 6.224 | 3.295 | 3.71 | Primary | 2655
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - Leading the Way | 18.909 | 18.888 | 18.838 | 18.773 | 18.743 | 18.726 | 18.653 | 17.446 | 16.486 | 15.752 | 15.877 | Primary | 2656
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - Leading the Way | 8.108 | 7.887 | 7.531 | 7.163 | 6.929 | 6.76 | 6.427 | 2.975 | 0.606 | -0.894 | -0.509 | Primary | 2657
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - Leading the Way | 9.065 | 9.04 | 8.98 | 8.905 | 8.838 | 8.77 | 8.65 | 7.339 | 6.371 | 5.769 | 5.807 | Primary | 2658
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - Leading the Way | 1.673 | 1.396 | 0.918 | 0.352 | 0.026 | -0.18 | -0.65 | -6.421 | -10.7 | -13.692 | -13.026 | Primary | 2659
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - Leading the Way | 5.409 | 4.614 | 3.542 | 2.593 | 1.852 | 1.167 | 0.119 | -7.774 | -13.161 | -16.5 | -15.989 | Primary | 2660
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - Leading the Way | 10.527 | 9.919 | 8.309 | 7.39 | 6.789 | 6.351 | 5.635 | -1.769 | -7.314 | -11.015 | -10.686 | Primary | 2661
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - Leading the Way | 15.65 | 15.312 | 15.238 | 15.137 | 15.045 | 14.944 | 14.773 | 12.988 | 11.649 | 10.795 | 10.85 | Primary | 2662
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - Leading the Way | 10.875 | 9.346 | 8.875 | 8.34 | 8.013 | 7.773 | 7.253 | -0.434 | -6.223 | -10.317 | -9.339 | Primary | 2663
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - Leading the Way | 7.979 | 7.462 | 6.67 | 5.796 | 5.202 | 4.722 | 3.888 | -3.788 | -9.259 | -12.909 | -12.506 | Primary | 2664
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - Leading the Way | 22.668 | 22.127 | 21.352 | 20.622 | 20.089 | 19.626 | 18.9 | 12.968 | 9.114 | 6.797 | 7.242 | Primary | 2665
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - Leading the Way | 5.176 | 4.829 | 4.29 | 3.682 | 3.292 | 3.003 | 2.472 | -3.048 | -7.21 | -10.107 | -9.849 | Primary | 2666
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - Leading the Way | 11.789 | 11.498 | 11.06 | 10.592 | 10.334 | 10.176 | 9.852 | 6.435 | 3.934 | 2.252 | 2.579 | Primary | 2667
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - Leading the Way | 18.287 | 18.133 | 17.863 | 17.544 | 17.333 | 17.158 | 16.79 | 12.447 | 9.161 | 6.858 | 7.267 | Primary | 2668
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - Leading the Way | 9.367 | 9.333 | 7.789 | 7.648 | 7.576 | 7.525 | 7.383 | 5.16 | 3.521 | 2.525 | 2.893 | Primary | 2669
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - Leading the Way | 27.457 | 27.485 | 27.485 | 27.454 | 27.397 | 27.309 | 27.172 | 25.785 | 24.83 | 24.417 | 24.566 | Primary | 2670
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - Leading the Way | 14.569 | 14.052 | 13.965 | 13.856 | 13.856 | 13.914 | 13.89 | 12.536 | 11.516 | 10.856 | 11.266 | Primary | 2671
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - Leading the Way | 2.791 | 2.52 | 2.033 | 1.416 | 0.731 | -0.081 | -1.157 | -7.745 | -11.789 | -13.264 | -13.292 | Primary | 2672
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - Leading the Way | 18.152 | 18.26 | 18.35 | 18.429 | 18.51 | 18.594 | 18.663 | 18.51 | 18.337 | 18.19 | 18.415 | Primary | 2673
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 7.469 | 6.852 | 6.244 | 5.593 | 5.111 | 4.695 | 4.045 | -1.67 | -5.726 | -8.438 | -8.091 | Primary | 2674
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - Leading the Way | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2675
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - Leading the Way | 3.078 | 2.858 | 2.484 | 2.054 | 1.876 | 1.814 | 1.554 | -2.271 | -5.195 | -7.169 | -6.617 | Primary | 2676
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - Leading the Way | 14.299 | 13.921 | 13.363 | 12.773 | 12.325 | 11.914 | 11.311 | 6.13 | 2.576 | 0.329 | 0.491 | Primary | 2677
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - Leading the Way | 15.28 | 12.88 | 12.845 | 12.778 | 12.751 | 12.723 | 12.569 | 10.338 | 8.693 | 7.647 | 8.11 | Primary | 2678
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - Leading the Way | 8.655 | 7.767 | 6.944 | 6.115 | 5.563 | 5.128 | 4.371 | -3.798 | -9.957 | -14.284 | -13.851 | Primary | 2679
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - Leading the Way | 18.467 | 18.33 | 18.124 | 17.925 | 17.803 | 17.725 | 17.572 | 15.5 | 13.88 | 12.7 | 12.848 | Primary | 2680
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - Leading the Way | 8.567 | 7.858 | 6.831 | 5.738 | 5.043 | 4.554 | 3.727 | -4.458 | -10.318 | -14.186 | -13.704 | Primary | 2681
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - Leading the Way | 4.199 | 3.333 | 2.603 | 1.794 | 1.199 | 0.68 | -0.123 | -7.44 | -12.64 | -15.978 | -15.431 | Primary | 2682
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - Leading the Way | 2.902 | 2.43 | 1.791 | 1.178 | 0.761 | 0.461 | -0.024 | -4.468 | -7.558 | -9.551 | -9.212 | Primary | 2683
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - Leading the Way | 8.527 | 8.467 | 8.369 | 23.651 | 23.56 | 23.478 | 23.346 | 22.073 | 21.168 | 20.716 | 20.797 | Primary | 2684
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - Leading the Way | 21.053 | 20.758 | 20.718 | 20.672 | 20.647 | 20.636 | 20.609 | 19.764 | 19.071 | 18.547 | 18.696 | Primary | 2685
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - Leading the Way | 19.246 | 18.965 | 18.541 | 18.081 | 17.804 | 17.636 | 17.3 | 13.478 | 10.616 | 8.754 | 9.148 | Primary | 2686
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - Leading the Way | 16.736 | 16.875 | 17.007 | 17.131 | 17.249 | 17.362 | 17.468 | 17.856 | 18.17 | 18.435 | 18.733 | Primary | 2687
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - Leading the Way | 14.78 | 14.841 | 14.836 | 14.813 | 14.839 | 14.881 | 14.844 | 13.503 | 12.604 | 12.139 | 12.697 | Primary | 2688
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - Leading the Way | 1.398 | 1.334 | 1.129 | 0.807 | 20.451 | 20.155 | 19.577 | 13.351 | 8.784 | 6.156 | 6.611 | Primary | 2689
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - Leading the Way | 7.726 | 7.304 | 6.681 | 6.014 | 5.581 | 5.239 | 4.664 | -0.815 | -4.807 | -7.578 | -7.33 | Primary | 2690
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - Leading the Way | 6.859 | 6.384 | 5.684 | 4.938 | 4.413 | 3.969 | 3.289 | -2.54 | -6.514 | -8.874 | -8.319 | Primary | 2691
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - Leading the Way | 17.731 | 17.648 | 17.52 | 17.376 | 17.244 | 17.109 | 16.882 | 14.794 | 13.214 | 12.059 | 12.06 | Primary | 2692
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - Leading the Way | 6.719 | 6.555 | 6.296 | 6.026 | 5.841 | 5.688 | 5.426 | 2.347 | 0.104 | -1.449 | -1.085 | Primary | 2693
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - Leading the Way | 6.867 | 6.52 | 6.044 | 5.567 | 5.185 | 4.831 | 4.322 | -0.003 | -3.125 | -5.304 | -5.362 | Primary | 2694
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - Leading the Way | 18.659 | 18.63 | 18.567 | 18.489 | 18.441 | 18.403 | 18.313 | 17.262 | 16.489 | 15.988 | 16.116 | Primary | 2695
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - Leading the Way | 7.024 | 6.712 | 6.244 | 5.76 | 5.458 | 5.236 | 4.825 | 0.909 | -1.862 | -3.674 | -3.268 | Primary | 2696
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - Leading the Way | 2.79 | 2.767 | 2.733 | 2.699 | 2.673 | 2.65 | 2.614 | 2.212 | 1.941 | 1.765 | 1.805 | Primary | 2697
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - Leading the Way | 9.278 | 8.906 | 8.716 | 8.491 | 8.349 | 8.235 | 7.991 | 5.101 | 2.855 | 1.305 | 1.475 | Primary | 2698
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - Leading the Way | 15.072 | 14.866 | 14.555 | 14.224 | 13.988 | 13.79 | 13.471 | 10.404 | 8.236 | 6.763 | 6.95 | Primary | 2699
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - Leading the Way | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary | 2700
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - Leading the Way | 21.251 | 21.053 | 20.764 | 20.47 | 20.272 | 20.119 | 19.847 | 16.821 | 14.559 | 12.985 | 13.211 | Primary | 2701
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - Leading the Way | 8.517 | 8.123 | 7.535 | 6.919 | 6.587 | 6.396 | 5.97 | 1.21 | -2.275 | -4.559 | -4.054 | Primary | 2702
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - Leading the Way | 14.229 | 13.914 | 13.443 | 12.929 | 12.62 | 12.394 | 11.986 | 7.824 | 4.772 | 2.79 | 3.081 | Primary | 2703
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - Leading the Way | 33.356 | 32.986 | 32.935 | 32.883 | 32.855 | 32.841 | 32.804 | 32.104 | 31.566 | 31.187 | 31.319 | Primary | 2704
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - Leading the Way | 4.291 | 3.32 | 2.431 | 1.482 | 0.848 | 0.393 | -0.35 | -7.023 | -11.722 | -14.675 | -14.137 | Primary | 2705
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - Leading the Way | 14.981 | 14.143 | 13.715 | 13.234 | 12.853 | 12.511 | 12.04 | 6.611 | 2.162 | -1.203 | -1.558 | Primary | 2706
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - Leading the Way | 11.999 | 11.852 | 11.61 | 11.338 | 11.104 | 10.878 | 10.463 | 5.479 | 1.614 | -1.257 | -0.944 | Primary | 2707
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - Leading the Way | 15.005 | 14.926 | 14.798 | 14.651 | 14.562 | 14.499 | 14.365 | 12.498 | 11.02 | 9.954 | 10.046 | Primary | 2708
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - Leading the Way | 24.348 | 22.485 | 22.073 | 21.634 | 21.322 | 21.053 | 20.607 | 16.86 | 14.253 | 12.521 | 12.756 | Primary | 2709
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - Leading the Way | 5.262 | 4.699 | 4.245 | 3.736 | 3.361 | 3.026 | 2.47 | -3.102 | -7.588 | -11.045 | -11.214 | Primary | 2710
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - Leading the Way | 1.435 | 0.515 | -0.259 | -1.051 | -1.579 | -1.968 | -2.683 | -10.075 | -15.691 | -19.793 | -19.612 | Primary | 2711
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - Leading the Way | 3.37 | 3.325 | 1.97 | 1.894 | 1.828 | 1.763 | 1.67 | 1.039 | 0.63 | 0.406 | 0.402 | Primary | 2712
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - Leading the Way | 8.842 | 8.323 | 9.885 | 9.429 | 9.115 | 8.84 | 8.31 | 2.304 | -2.129 | -5.258 | -4.677 | Primary | 2713
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - Leading the Way | 7.268 | 7.029 | 6.616 | 6.129 | 5.942 | 5.89 | 5.576 | 0.221 | -3.926 | -6.862 | -6.185 | Primary | 2714
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - Leading the Way | 32.732 | 31.348 | 31.268 | 31.171 | 31.089 | 31.005 | 30.819 | 28.73 | 27.109 | 25.887 | 25.983 | Primary | 2715
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - Leading the Way | 12.231 | 12.07 | 11.788 | 11.46 | 11.235 | 11.04 | 10.617 | 5.956 | 2.419 | -0.175 | 0.254 | Primary | 2716
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - Leading the Way | 8.955 | 8.231 | 7.913 | 7.625 | 7.427 | 7.261 | 6.973 | 4.18 | 2.195 | 0.853 | 1.195 | Primary | 2717
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - Leading the Way | 8.84 | 8.874 | 8.863 | 8.828 | 8.855 | 8.904 | 8.894 | 7.901 | 7.141 | 6.656 | 6.988 | Primary | 2718
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - Leading the Way | 13.978 | 13.91 | 13.773 | 13.599 | 13.472 | 13.355 | 13.108 | 9.702 | 7.124 | 5.238 | 5.639 | Primary | 2719
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - Leading the Way | 14.749 | 14.684 | 14.54 | 14.321 | 14.057 | 13.722 | 13.265 | 8.991 | 5.903 | 4.197 | 4.111 | Primary | 2720
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - Leading the Way | 18.9 | 18.709 | 18.424 | 18.092 | 17.912 | 17.788 | 17.539 | 13.829 | 10.753 | 8.299 | 8.208 | Primary | 2721
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - Leading the Way | 5.649 | 4.542 | 4.133 | 3.684 | 3.36 | 3.085 | 2.689 | -1.708 | -5.263 | -7.984 | -8.222 | Primary | 2722
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - Leading the Way | 5.738 | 3.857 | 2.336 | 0.722 | -0.45 | -1.366 | -2.685 | -12.902 | -20.195 | -24.914 | -24.803 | Primary | 2723
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - Leading the Way | 13.328 | 12.404 | 11.855 | 11.365 | 11.018 | 10.748 | 10.332 | 6.624 | 3.951 | 2.174 | 2.341 | Primary | 2724
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - Leading the Way | 15.816 | 14.917 | 14.368 | 13.751 | 13.356 | 13.04 | 12.423 | 6.441 | 2.115 | -0.78 | -0.2 | Primary | 2725
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - Leading the Way | 9.972 | 9.772 | 9.418 | 9.001 | 8.722 | 8.492 | 8.018 | 3.292 | -0.078 | -2.341 | -1.797 | Primary | 2726
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - Leading the Way | 11.113 | 11.16 | 11.201 | 11.237 | 11.269 | 11.297 | 11.318 | 11.239 | 11.157 | 11.073 | 11.112 | Primary | 2727
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - Leading the Way | 21.511 | 21.389 | 21.19 | 20.961 | 20.823 | 20.723 | 20.533 | 18.651 | 17.244 | 16.3 | 16.444 | Primary | 2728
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - Leading the Way | 16.319 | 16.45 | 16.557 | 16.652 | 16.755 | 16.858 | 16.93 | 16.325 | 15.847 | 15.503 | 15.964 | Primary | 2729
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 10.798 | 10.294 | 9.576 | 8.813 | 8.299 | 7.9 | 7.251 | 1.135 | -3.352 | -6.415 | -6.13 | Primary | 2730
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - Leading the Way | 21.96 | 21.919 | 21.847 | 21.774 | 21.733 | 21.709 | 21.655 | 20.924 | 20.368 | 19.972 | 20.029 | Primary | 2731
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - Leading the Way | 2.66 | 2.319 | 1.772 | 1.163 | 0.797 | 0.545 | 0.015 | -5.744 | -9.937 | -12.757 | -11.982 | Primary | 2732
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - Leading the Way | 6.608 | 6.59 | 6.559 | 6.524 | 6.506 | 6.491 | 6.459 | 6.03 | 5.717 | 5.501 | 5.559 | Primary | 2733
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - Leading the Way | 8.113 | 7.254 | 6.868 | 6.488 | 6.256 | 6.123 | 5.87 | 2.927 | 0.799 | -0.556 | -0.164 | Primary | 2734
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - Leading the Way | 12.926 | 12.193 | 11.126 | 9.941 | 9.033 | 8.234 | 6.895 | -5.522 | -14.6 | -20.819 | -20.357 | Primary | 2735
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - Leading the Way | 10.481 | 8.899 | 7.877 | 7.22 | 6.773 | 6.4 | 5.715 | -1.392 | -6.641 | -10.142 | -9.551 | Primary | 2736
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - Leading the Way | 3.958 | 3.785 | 3.548 | 3.285 | 3.055 | 2.822 | 2.478 | -0.599 | -3.012 | -4.798 | -5.011 | Primary | 2737
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - Leading the Way | 3.961 | 3.909 | 3.846 | 3.778 | 3.714 | 3.649 | 3.569 | 3.005 | 2.512 | 2.088 | 1.848 | Primary | 2738
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - Leading the Way | 3.217 | 2.747 | 23.699 | 23.3 | 23.019 | 22.788 | 22.393 | 17.989 | 14.705 | 12.675 | 12.809 | Primary | 2739
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - Leading the Way | 13.875 | 13.289 | 12.813 | 12.321 | 11.937 | 11.594 | 11.107 | 7.881 | 5.897 | 4.844 | 5.114 | Primary | 2740
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - Leading the Way | 4.359 | 4.185 | 3.936 | 3.673 | 3.486 | 3.325 | 3.08 | 1.253 | -0.037 | -0.895 | -0.871 | Primary | 2741
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - Leading the Way | 3.596 | 3.459 | 3.269 | 3.07 | 2.899 | 2.73 | 2.493 | 0.635 | -0.705 | -1.619 | -1.702 | Primary | 2742
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - Leading the Way | 14.012 | 13.294 | 12.778 | 12.196 | 11.793 | 11.469 | 10.858 | 3.848 | -1.3 | -4.939 | -4.332 | Primary | 2743
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - Leading the Way | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2744
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - Leading the Way | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2745
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - Leading the Way | 17.636 | 17.066 | 16.78 | 16.457 | 16.266 | 16.123 | 15.812 | 12.17 | 9.421 | 7.481 | 7.875 | Primary | 2746
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - Leading the Way | 15.29 | 14.238 | 14.156 | 14.059 | 13.965 | 13.865 | 13.712 | 12.336 | 11.298 | 10.572 | 10.499 | Primary | 2747
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - Leading the Way | 10.92 | 10.612 | 10.147 | 9.659 | 9.355 | 9.135 | 8.733 | 4.592 | 1.614 | -0.281 | 0.072 | Primary | 2748
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - Leading the Way | 12.985 | 12.656 | 12.203 | 11.756 | 11.406 | 11.091 | 10.618 | 6.561 | 3.681 | 1.705 | 1.722 | Primary | 2749
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - Leading the Way | 10.499 | 9.664 | 9.383 | 9.049 | 8.812 | 8.606 | 8.225 | 4.331 | 1.353 | -0.823 | -0.664 | Primary | 2750
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - Leading the Way | 11.27 | 11.065 | 10.733 | 10.353 | 10.136 | 9.988 | 9.657 | 5.854 | 2.994 | 1.086 | 1.391 | Primary | 2751
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - Leading the Way | 18.726 | 17.909 | 17.832 | 17.732 | 17.693 | 17.684 | 17.582 | 15.324 | 13.642 | 12.457 | 12.876 | Primary | 2752
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - Leading the Way | 16.479 | 16.083 | 15.484 | 14.831 | 14.377 | 13.983 | 13.332 | 7.259 | 2.922 | 0.248 | 0.537 | Primary | 2753
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - Leading the Way | 8.885 | 8.738 | 8.507 | 8.264 | 8.067 | 7.878 | 7.589 | 5.425 | 4.001 | 3.117 | 3.24 | Primary | 2754
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - Leading the Way | 12.791 | 12.166 | 10.011 | 9.258 | 8.798 | 8.45 | 7.822 | 0.848 | -4.167 | -7.263 | -6.367 | Primary | 2755
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - Leading the Way | 23.231 | 13.574 | 6.282 | 5.694 | 5.29 | 4.97 | 4.447 | -1.016 | -5.096 | -7.787 | -7.524 | Primary | 2756
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - Leading the Way | 2.478 | 1.539 | 0.625 | -2.059 | -2.666 | -3.151 | -3.972 | -11.247 | -16.465 | -19.988 | -19.657 | Primary | 2757
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - Leading the Way | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2758
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - Leading the Way | 5.495 | 5.342 | 5.128 | 4.888 | 4.719 | 4.573 | 4.332 | 1.595 | -0.549 | -2.113 | -2.157 | Primary | 2759
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - Leading the Way | 12.108 | 11.123 | 10.583 | 9.989 | 9.587 | 9.272 | 8.782 | 3.919 | 0.354 | -1.933 | -1.538 | Primary | 2760
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 7.997 | 6.283 | 6.067 | 5.801 | 5.671 | 5.595 | 5.377 | 1.817 | -0.875 | -2.67 | -2.124 | Primary | 2761
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - Leading the Way | 27.962 | 27.985 | 28.008 | 28.03 | 28.05 | 28.07 | 28.089 | 28.17 | 28.234 | 28.288 | 28.337 | Primary | 2762
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - Leading the Way | 19.969 | 18.837 | 18.341 | 17.79 | 17.433 | 17.157 | 16.673 | 12.081 | 8.721 | 6.403 | 6.633 | Primary | 2763
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - Leading the Way | 8.359 | 7.722 | 7.815 | 7.835 | 7.811 | 7.715 | 7.496 | 4.59 | 2.697 | 2.031 | 2.715 | Primary | 2764
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - Leading the Way | 4.207 | 4.129 | 4.113 | 4.094 | 4.07 | 4.044 | 4.014 | 3.741 | 3.41 | 3.049 | 2.758 | Primary | 2765
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - Leading the Way | 14.377 | 13.941 | 13.296 | 12.613 | 12.206 | 11.929 | 11.34 | 5.147 | 0.426 | -2.936 | -2.574 | Primary | 2766
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - Leading the Way | 2.504 | 2.166 | 1.687 | 1.17 | 0.726 | 0.295 | -0.328 | -5.565 | -9.406 | -12.103 | -12.275 | Primary | 2767
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - Leading the Way | 8.834 | 7.848 | 7.455 | 7.053 | 6.727 | 6.451 | 6.081 | 3.186 | 1.3 | 0.125 | 0.262 | Primary | 2768
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - Leading the Way | 25.227 | 24.62 | 24.035 | 23.38 | 22.91 | 22.506 | 21.8 | 14.808 | 9.656 | 6.036 | 6.382 | Primary | 2769
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - Leading the Way | 11.739 | 11.295 | 10.61 | 9.85 | 9.4 | 9.097 | 8.508 | 2.39 | -2.039 | -4.877 | -4.252 | Primary | 2770
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - Leading the Way | 11.301 | 10.856 | 10.204 | 9.504 | 9.041 | 8.675 | 8.017 | 1.369 | -3.579 | -7.092 | -6.856 | Primary | 2771
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - Leading the Way | 14.004 | 13.806 | 13.877 | 13.928 | 14.022 | 14.129 | 14.186 | 13.389 | 12.789 | 12.397 | 12.902 | Primary | 2772
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - Leading the Way | 32.708 | 32.239 | 31.593 | 30.933 | 30.434 | 29.986 | 29.269 | 22.613 | 17.438 | 13.498 | 13.36 | Primary | 2773
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - Leading the Way | 9.772 | 8.198 | 8.071 | 7.905 | 7.792 | 7.68 | 7.414 | 4.598 | 2.572 | 1.264 | 1.639 | Primary | 2774
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - Leading the Way | 8.288 | 7.507 | 7.065 | 6.562 | 6.21 | 5.91 | 5.356 | -0.211 | -4.404 | -7.487 | -7.246 | Primary | 2775
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - Leading the Way | 30.745 | 30.755 | 30.763 | 30.769 | 30.779 | 30.789 | 30.797 | 30.797 | 30.798 | 30.805 | 30.839 | Primary | 2776
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - Leading the Way | 9.108 | 9.046 | 24.311 | 24.147 | 24.079 | 24.063 | 23.94 | 21.879 | 20.234 | 19.062 | 19.381 | Primary | 2777
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - Leading the Way | 8.727 | 7.019 | 21.553 | 21.064 | 20.712 | 20.399 | 19.837 | 13.825 | 9.376 | 6.205 | 6.647 | Primary | 2778
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - Leading the Way | 9.528 | 9.239 | 8.847 | 8.425 | 8.055 | 7.701 | 7.203 | 2.787 | -0.578 | -3.057 | -3.402 | Primary | 2779
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - Leading the Way | 12.117 | 12.001 | 11.826 | 11.647 | 11.504 | 11.373 | 11.158 | 9.625 | 8.551 | 7.824 | 7.938 | Primary | 2780
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - Leading the Way | 20.275 | 19.72 | 19.579 | 19.404 | 19.319 | 19.257 | 19.032 | 16.078 | 13.802 | 12.136 | 12.542 | Primary | 2781
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - Leading the Way | 10.956 | 10.426 | 9.658 | 8.917 | 8.372 | 7.906 | 7.146 | 0.55 | -4.075 | -6.993 | -6.514 | Primary | 2782
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - Leading the Way | 12.297 | 11.832 | 11.408 | 10.933 | 10.623 | 10.389 | 9.918 | 4.741 | 0.802 | -2.102 | -1.742 | Primary | 2783
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - Leading the Way | 10.916 | 10.276 | 9.811 | 9.297 | 8.918 | 8.59 | 8.001 | 2.828 | -0.919 | -3.547 | -3.271 | Primary | 2784
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 4.889 | 4.863 | 4.802 | 4.725 | 4.698 | 4.685 | 4.623 | 3.511 | 2.678 | 2.119 | 2.322 | Primary | 2785
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - Leading the Way | 4.744 | 4.714 | 4.651 | 4.568 | 4.518 | 4.479 | 4.397 | 3.031 | 1.99 | 1.306 | 1.498 | Primary | 2786
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 7.527 | 7.405 | 7.221 | 7.023 | 6.883 | 6.77 | 6.588 | 4.945 | 3.834 | 3.142 | 3.27 | Primary | 2787
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - Leading the Way | 7.398 | 7.261 | 7.059 | 6.84 | 6.697 | 6.592 | 6.414 | 4.36 | 2.869 | 1.859 | 2.04 | Primary | 2788
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - Leading the Way | 13.155 | 12.918 | 12.561 | 12.167 | 11.874 | 11.614 | 11.106 | 6.154 | 2.283 | -0.736 | -0.685 | Primary | 2789
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - Leading the Way | 22.096 | 21.616 | 20.957 | 20.335 | 19.911 | 19.579 | 19.039 | 14.237 | 10.847 | 8.658 | 8.883 | Primary | 2790
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - Leading the Way | 29.806 | 28.923 | 28.893 | 28.859 | 28.824 | 28.785 | 28.737 | 28.363 | 28.043 | 27.798 | 27.663 | Primary | 2791
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - Leading the Way | 5.815 | 5.387 | 5.346 | 5.303 | 5.274 | 5.252 | 5.212 | 4.655 | 4.237 | 3.932 | 3.99 | Primary | 2792
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - Leading the Way | 11.664 | 11.67 | 11.63 | 11.572 | 11.56 | 11.565 | 11.477 | 9.563 | 8.074 | 6.993 | 7.447 | Primary | 2793
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NG FES - System Transformation | 5.236 | 5.048 | 4.759 | 4.435 | 4.079 | 3.694 | 3.239 | 0.996 | -2.293 | -6.921 | -14.107 | Primary | 2794
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NG FES - System Transformation | 11.738 | 11.004 | 9.245 | 8.685 | 8.067 | 7.416 | 6.675 | 3.25 | -3.476 | -10.277 | -18.987 | Primary | 2795
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NG FES - System Transformation | 7.797 | 7.512 | 9.123 | 8.713 | 8.263 | 7.785 | 7.255 | 4.49 | 0.64 | -3.752 | -10.025 | Primary | 2796
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NG FES - System Transformation | 6.008 | 5.814 | 5.518 | 5.192 | 4.832 | 4.454 | 4.044 | 1.935 | -1.668 | -5.976 | -12.493 | Primary | 2797
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NG FES - System Transformation | 26.375 | 26.376 | 26.376 | 26.377 | 26.378 | 26.378 | 26.379 | 26.38 | 26.38 | 26.38 | 26.38 | Primary | 2798
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NG FES - System Transformation | 2.685 | 2.644 | 2.571 | 2.487 | 2.382 | 2.258 | 2.108 | 1.195 | -0.45 | -2.31 | -4.812 | Primary | 2799
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NG FES - System Transformation | 4.063 | 4.032 | 3.994 | 3.958 | 3.919 | 3.879 | 3.838 | 3.626 | 3.381 | 3.18 | 2.948 | Primary | 2800
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NG FES - System Transformation | 4.423 | 4.252 | 4.041 | 3.809 | 3.549 | 3.261 | 2.927 | 1.051 | -1.783 | -4.637 | -8.013 | Primary | 2801
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NG FES - System Transformation | 8.3 | 8.205 | 8.07 | 7.93 | 7.762 | 7.569 | 7.323 | 5.922 | 3.411 | 0.401 | -3.672 | Primary | 2802
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NG FES - System Transformation | 12.338 | 12.083 | 11.732 | 11.39 | 11.011 | 10.599 | 10.14 | 7.797 | 5.094 | 2.356 | -1.477 | Primary | 2803
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NG FES - System Transformation | 4.834 | 4.268 | 3.911 | 3.559 | 3.173 | 2.761 | 2.313 | -0.144 | -4.822 | -9.81 | -16.749 | Primary | 2804
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NG FES - System Transformation | 11.711 | 11.199 | 11.002 | 10.787 | 10.541 | 10.27 | 9.97 | 8.156 | 5.048 | 1.225 | -4.587 | Primary | 2805
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NG FES - System Transformation | 7.369 | 7.028 | 6.62 | 6.203 | 5.743 | 5.244 | 4.697 | 1.524 | -2.423 | -6.532 | -11.92 | Primary | 2806
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NG FES - System Transformation | 6.616 | 5.998 | 5.724 | 5.447 | 5.141 | 4.813 | 4.459 | 2.417 | -0.798 | -4.412 | -9.684 | Primary | 2807
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 13.169 | 13.042 | 12.861 | 12.658 | 12.409 | 12.115 | 11.295 | 7.421 | 4.825 | 2.675 | 0.144 | Primary | 2808
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NG FES - System Transformation | 16.735 | 16.731 | 16.706 | 16.669 | 16.616 | 16.517 | 16.301 | 15.046 | 14.738 | 13.838 | 12.806 | Primary | 2809
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NG FES - System Transformation | 9.63 | 8.696 | 8.548 | 8.384 | 8.184 | 7.956 | 7.705 | 6.022 | 2.869 | -0.264 | -4.605 | Primary | 2810
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NG FES - System Transformation | 10.8 | 10.177 | 9.862 | 9.532 | 9.173 | 8.791 | 8.401 | 6.186 | 3.031 | -0.846 | -6.694 | Primary | 2811
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NG FES - System Transformation | 16.042 | 15.882 | 15.68 | 15.487 | 15.276 | 15.049 | 14.801 | 13.367 | 11.172 | 8.526 | 4.482 | Primary | 2812
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NG FES - System Transformation | 10.382 | 10.329 | 10.251 | 10.149 | 10.01 | 9.833 | 9.608 | 7.98 | 5.788 | 4.24 | 2.69 | Primary | 2813
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NG FES - System Transformation | 21.454 | 21.194 | 20.882 | 20.564 | 20.207 | 19.817 | 19.384 | 16.89 | 13.198 | 9.591 | 4.983 | Primary | 2814
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 17.653 | 17.458 | 17.229 | 16.99 | 16.732 | 16.46 | 16.173 | 14.564 | 11.883 | 9.13 | 5.581 | Primary | 2815
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NG FES - System Transformation | 13.036 | 12.412 | 11.957 | 11.484 | 10.976 | 10.438 | 9.84 | 6.706 | 2.639 | -2.378 | -9.776 | Primary | 2816
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NG FES - System Transformation | 7.769 | 7.272 | 7.218 | 7.162 | 7.091 | 7.009 | 6.9 | 6.323 | 4.688 | 2.971 | 0.641 | Primary | 2817
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NG FES - System Transformation | 8.771 | 8.568 | 8.244 | 7.87 | 7.434 | 6.947 | 6.36 | 3.213 | -1.37 | -6.435 | -13.551 | Primary | 2818
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NG FES - System Transformation | 7.681 | 7.12 | 6.684 | 6.284 | 5.853 | 5.398 | 4.9 | 2.566 | -0.222 | -3.394 | -7.711 | Primary | 2819
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NG FES - System Transformation | 7.958 | 7.76 | 7.488 | 7.217 | 6.912 | 6.568 | 6.137 | 3.773 | 0.574 | -3.231 | -8.767 | Primary | 2820
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NG FES - System Transformation | 9.036 | 8.818 | 8.516 | 8.19 | 7.835 | 7.463 | 7.071 | 5.002 | 1.759 | -1.692 | -6.566 | Primary | 2821
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NG FES - System Transformation | 3.813 | 3.608 | 3.303 | 2.966 | 2.588 | 2.18 | 1.73 | -0.831 | -5.027 | -9.745 | -16.764 | Primary | 2822
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NG FES - System Transformation | 7.624 | 7.26 | 6.815 | 6.347 | 5.848 | 5.325 | 4.756 | 1.835 | -2.505 | -7.125 | -13.092 | Primary | 2823
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NG FES - System Transformation | 10.215 | 9.991 | 10.057 | 10.107 | 10.132 | 10.137 | 10.11 | 9.76 | 8.083 | 6.508 | 4.531 | Primary | 2824
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NG FES - System Transformation | 6.325 | 5.381 | 5.16 | 4.956 | 4.727 | 4.482 | 4.216 | 2.792 | 0.42 | -1.88 | -4.886 | Primary | 2825
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NG FES - System Transformation | 16.791 | 15.591 | 15.137 | 14.661 | 14.133 | 13.542 | 12.811 | 8.904 | 4.169 | -1.403 | -9.046 | Primary | 2826
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NG FES - System Transformation | 12.908 | 12.903 | 12.871 | 12.828 | 12.772 | 12.705 | 12.614 | 12.109 | 10.944 | 9.711 | 8.007 | Primary | 2827
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NG FES - System Transformation | 6.776 | 6.753 | 6.724 | 6.695 | 6.665 | 6.632 | 6.597 | 6.42 | 6.182 | 5.924 | 5.581 | Primary | 2828
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 12.653 | 12.662 | 12.647 | 12.618 | 12.569 | 12.502 | 12.41 | 11.744 | 10.265 | 8.733 | 6.679 | Primary | 2829
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NG FES - System Transformation | 16.777 | 16.767 | 16.737 | 16.69 | 16.623 | 16.531 | 16.408 | 15.501 | 13.98 | 12.483 | 10.504 | Primary | 2830
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NG FES - System Transformation | 4.718 | 4.697 | 4.673 | 4.652 | 4.627 | 4.599 | 4.557 | 4.321 | 3.589 | 2.712 | 1.441 | Primary | 2831
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NG FES - System Transformation | 9.111 | 9.002 | 8.867 | 8.738 | 8.6 | 8.456 | 8.301 | 7.466 | 6.075 | 4.477 | 2.084 | Primary | 2832
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NG FES - System Transformation | 10.232 | 10.062 | 9.827 | 9.589 | 9.324 | 9.039 | 8.732 | 7.032 | 3.856 | 0.459 | -4.391 | Primary | 2833
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NG FES - System Transformation | 23.089 | 22.79 | 22.749 | 22.708 | 22.657 | 22.6 | 22.538 | 22.137 | 21.199 | 20.123 | 18.502 | Primary | 2834
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NG FES - System Transformation | 6.669 | 6.579 | 6.435 | 6.282 | 6.087 | 5.852 | 5.568 | 3.71 | 0.509 | -2.43 | -6.2 | Primary | 2835
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NG FES - System Transformation | 4.9 | 4.207 | 3.803 | 3.35 | 2.835 | 2.269 | 1.621 | -1.845 | -6.567 | -11.116 | -17.085 | Primary | 2836
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NG FES - System Transformation | 11.931 | 10.713 | 10.438 | 10.152 | 9.828 | 9.476 | 9.075 | 6.867 | 2.457 | -1.941 | -7.888 | Primary | 2837
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 8.863 | 8.705 | 8.489 | 8.278 | 8.037 | 7.776 | 7.496 | 5.927 | 3.57 | 1.319 | -1.776 | Primary | 2838
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NG FES - System Transformation | 14.144 | 13.889 | 13.562 | 13.25 | 12.907 | 12.545 | 12.167 | 10.062 | 6.469 | 2.308 | -4.018 | Primary | 2839
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NG FES - System Transformation | 4.139 | 3.663 | 3.557 | 3.445 | 3.312 | 3.164 | 2.987 | 2.042 | -0.269 | -2.592 | -5.368 | Primary | 2840
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NG FES - System Transformation | 18.218 | 18.059 | 17.83 | 17.576 | 17.29 | 16.98 | 16.634 | 14.685 | 11.251 | 7.704 | 2.701 | Primary | 2841
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NG FES - System Transformation | 18.859 | 18.84 | 18.808 | 18.771 | 18.727 | 18.677 | 18.619 | 18.245 | 17.321 | 16.293 | 14.868 | Primary | 2842
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NG FES - System Transformation | 7.972 | 7.837 | 7.648 | 7.468 | 7.262 | 7.035 | 6.769 | 5.392 | 3.322 | 1.166 | -1.883 | Primary | 2843
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NG FES - System Transformation | 8.983 | 8.954 | 8.907 | 8.848 | 8.771 | 8.675 | 8.558 | 7.775 | 6.631 | 5.608 | 4.46 | Primary | 2844
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NG FES - System Transformation | 1.509 | 1.399 | 1.199 | 0.959 | 0.685 | 0.383 | 0.046 | -1.847 | -4.952 | -9.001 | -15.118 | Primary | 2845
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NG FES - System Transformation | 5.177 | 4.424 | 3.587 | 2.921 | 2.203 | 1.451 | 0.668 | -3.272 | -7.642 | -12.191 | -18.532 | Primary | 2846
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NG FES - System Transformation | 10.29 | 9.987 | 8.847 | 8.443 | 7.997 | 7.511 | 6.93 | 4.007 | -0.424 | -5.502 | -12.501 | Primary | 2847
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NG FES - System Transformation | 15.569 | 15.216 | 15.147 | 15.061 | 14.95 | 14.816 | 14.654 | 13.629 | 12.108 | 10.869 | 9.609 | Primary | 2848
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NG FES - System Transformation | 10.695 | 9.316 | 9.111 | 8.885 | 8.613 | 8.305 | 7.931 | 5.787 | 0.639 | -4.537 | -11.413 | Primary | 2849
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NG FES - System Transformation | 7.834 | 7.494 | 7.04 | 6.569 | 6.055 | 5.511 | 4.93 | 1.885 | -2.286 | -6.922 | -13.75 | Primary | 2850
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NG FES - System Transformation | 22.501 | 22.068 | 21.541 | 21.094 | 20.602 | 20.079 | 19.498 | 16.636 | 13.146 | 9.944 | 5.682 | Primary | 2851
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NG FES - System Transformation | 4.991 | 4.792 | 4.513 | 4.202 | 3.856 | 3.486 | 3.071 | 0.871 | -2.567 | -6.583 | -12.305 | Primary | 2852
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NG FES - System Transformation | 11.663 | 11.52 | 11.33 | 11.144 | 10.941 | 10.728 | 10.491 | 9.323 | 7.592 | 5.147 | 1.307 | Primary | 2853
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NG FES - System Transformation | 18.203 | 18.113 | 17.972 | 17.813 | 17.627 | 17.42 | 17.182 | 15.766 | 13.087 | 10.207 | 6.094 | Primary | 2854
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NG FES - System Transformation | 9.287 | 9.313 | 7.87 | 7.848 | 7.803 | 7.734 | 7.626 | 6.852 | 5.23 | 3.686 | 1.716 | Primary | 2855
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NG FES - System Transformation | 27.427 | 27.452 | 27.458 | 27.442 | 27.402 | 27.335 | 27.241 | 26.436 | 25.208 | 24.489 | 23.954 | Primary | 2856
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NG FES - System Transformation | 14.411 | 13.953 | 13.974 | 13.986 | 13.98 | 13.961 | 13.915 | 13.574 | 12.644 | 11.293 | 9.207 | Primary | 2857
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NG FES - System Transformation | 2.721 | 2.453 | 2.039 | 1.542 | 0.941 | 0.234 | -0.579 | -5.613 | -10.407 | -12.885 | -14.376 | Primary | 2858
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NG FES - System Transformation | 18.045 | 18.11 | 18.158 | 18.193 | 18.214 | 18.225 | 18.222 | 18.094 | 17.499 | 16.893 | 16.252 | Primary | 2859
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 7.321 | 6.813 | 6.413 | 6.008 | 5.57 | 5.1 | 4.57 | 1.87 | -1.303 | -4.947 | -10.008 | Primary | 2860
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NG FES - System Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2861
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NG FES - System Transformation | 2.939 | 2.909 | 2.834 | 2.745 | 2.637 | 2.512 | 2.346 | 1.37 | -0.759 | -3.696 | -8.326 | Primary | 2862
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NG FES - System Transformation | 14.176 | 13.879 | 13.5 | 13.121 | 12.704 | 12.258 | 11.768 | 9.234 | 5.795 | 2.73 | -1.024 | Primary | 2863
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NG FES - System Transformation | 15.184 | 12.768 | 12.755 | 12.73 | 12.677 | 12.602 | 12.506 | 11.721 | 10.063 | 8.455 | 6.243 | Primary | 2864
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NG FES - System Transformation | 8.413 | 7.699 | 7.216 | 6.78 | 6.294 | 5.77 | 5.164 | 2.01 | -3.575 | -9.315 | -16.982 | Primary | 2865
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NG FES - System Transformation | 18.347 | 18.255 | 18.14 | 18.039 | 17.923 | 17.797 | 17.642 | 16.876 | 15.279 | 13.593 | 11.409 | Primary | 2866
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NG FES - System Transformation | 8.323 | 7.957 | 7.467 | 6.967 | 6.422 | 5.845 | 5.194 | 2.027 | -2.511 | -7.831 | -15.531 | Primary | 2867
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NG FES - System Transformation | 3.978 | 3.279 | 2.84 | 2.375 | 1.863 | 1.301 | 0.659 | -2.787 | -6.8 | -11.385 | -17.598 | Primary | 2868
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NG FES - System Transformation | 2.719 | 2.419 | 2.059 | 1.745 | 1.406 | 1.048 | 0.661 | -1.232 | -3.457 | -6.239 | -10.27 | Primary | 2869
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NG FES - System Transformation | 8.487 | 8.475 | 8.449 | 23.811 | 23.759 | 23.69 | 23.593 | 22.957 | 22.086 | 21.35 | 20.507 | Primary | 2870
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NG FES - System Transformation | 21.026 | 20.753 | 20.747 | 20.736 | 20.721 | 20.703 | 20.677 | 20.556 | 19.931 | 19.303 | 18.54 | Primary | 2871
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NG FES - System Transformation | 19.095 | 19.001 | 18.854 | 18.697 | 18.516 | 18.311 | 18.041 | 16.678 | 14.623 | 11.928 | 7.931 | Primary | 2872
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NG FES - System Transformation | 16.664 | 16.764 | 16.854 | 16.935 | 17.007 | 17.07 | 17.126 | 17.3 | 17.292 | 17.264 | 17.235 | Primary | 2873
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NG FES - System Transformation | 14.684 | 14.749 | 14.782 | 14.808 | 14.809 | 14.787 | 14.737 | 14.304 | 13.323 | 12.447 | 11.422 | Primary | 2874
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NG FES - System Transformation | 1.322 | 1.322 | 1.268 | 1.159 | 20.881 | 20.63 | 20.304 | 17.567 | 13.086 | 9.395 | 4.849 | Primary | 2875
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NG FES - System Transformation | 7.549 | 7.254 | 6.882 | 6.513 | 6.115 | 5.699 | 5.259 | 3.045 | -0.17 | -3.821 | -9.025 | Primary | 2876
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NG FES - System Transformation | 6.707 | 6.412 | 6.018 | 5.62 | 5.183 | 4.708 | 4.154 | 1.391 | -1.887 | -5.382 | -10.06 | Primary | 2877
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NG FES - System Transformation | 17.697 | 17.609 | 17.493 | 17.368 | 17.229 | 17.079 | 16.92 | 16.001 | 14.59 | 13.228 | 11.407 | Primary | 2878
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NG FES - System Transformation | 6.565 | 6.433 | 6.261 | 6.095 | 5.907 | 5.701 | 5.474 | 4.271 | 2.17 | -0.003 | -2.803 | Primary | 2879
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NG FES - System Transformation | 6.77 | 6.47 | 6.115 | 5.783 | 5.424 | 5.047 | 4.64 | 2.581 | -0.269 | -2.906 | -6.203 | Primary | 2880
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NG FES - System Transformation | 18.623 | 18.612 | 18.584 | 18.551 | 18.507 | 18.455 | 18.392 | 17.993 | 17.315 | 16.595 | 15.572 | Primary | 2881
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NG FES - System Transformation | 6.881 | 6.682 | 6.426 | 6.187 | 5.925 | 5.643 | 5.331 | 3.766 | 1.808 | -0.811 | -4.825 | Primary | 2882
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NG FES - System Transformation | 2.78 | 2.763 | 2.741 | 2.72 | 2.696 | 2.67 | 2.639 | 2.48 | 2.206 | 1.986 | 1.731 | Primary | 2883
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NG FES - System Transformation | 9.164 | 8.828 | 8.723 | 8.607 | 8.467 | 8.308 | 8.12 | 6.948 | 4.81 | 2.55 | -0.499 | Primary | 2884
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NG FES - System Transformation | 14.986 | 14.829 | 14.625 | 14.42 | 14.195 | 13.958 | 13.699 | 12.403 | 10.534 | 8.622 | 6.053 | Primary | 2885
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NG FES - System Transformation | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary | 2886
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NG FES - System Transformation | 21.178 | 21.048 | 20.888 | 20.742 | 20.579 | 20.405 | 20.211 | 19.212 | 17.362 | 15.431 | 12.749 | Primary | 2887
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NG FES - System Transformation | 8.328 | 8.142 | 7.898 | 7.668 | 7.415 | 7.144 | 6.83 | 5.211 | 2.596 | -0.83 | -6.066 | Primary | 2888
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NG FES - System Transformation | 14.101 | 13.933 | 13.713 | 13.485 | 13.235 | 12.968 | 12.666 | 11.076 | 8.591 | 5.757 | 1.733 | Primary | 2889
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NG FES - System Transformation | 33.321 | 32.968 | 32.949 | 32.93 | 32.906 | 32.878 | 32.842 | 32.674 | 32.174 | 31.651 | 30.973 | Primary | 2890
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NG FES - System Transformation | 4.048 | 3.36 | 2.917 | 2.456 | 1.955 | 1.427 | 0.82 | -1.94 | -5.509 | -9.707 | -15.775 | Primary | 2891
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NG FES - System Transformation | 14.833 | 14.123 | 13.876 | 13.596 | 13.279 | 12.914 | 12.467 | 9.909 | 5.736 | 1.337 | -3.975 | Primary | 2892
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NG FES - System Transformation | 11.874 | 11.723 | 11.518 | 11.297 | 11.041 | 10.758 | 10.45 | 8.594 | 5.182 | 1.673 | -2.952 | Primary | 2893
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NG FES - System Transformation | 14.931 | 14.888 | 14.828 | 14.762 | 14.68 | 14.585 | 14.472 | 13.767 | 12.377 | 10.881 | 8.904 | Primary | 2894
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NG FES - System Transformation | 24.288 | 22.49 | 22.218 | 21.951 | 21.666 | 21.368 | 21.054 | 19.501 | 17.461 | 15.276 | 12.105 | Primary | 2895
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NG FES - System Transformation | 5.123 | 4.581 | 4.23 | 3.867 | 3.477 | 3.066 | 2.639 | 0.282 | -3.598 | -7.894 | -13.754 | Primary | 2896
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NG FES - System Transformation | 1.223 | 0.503 | 0.066 | -0.353 | -0.807 | -1.286 | -1.815 | -4.5 | -8.9 | -14.05 | -21.594 | Primary | 2897
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NG FES - System Transformation | 3.33 | 3.28 | 1.933 | 1.867 | 1.792 | 1.711 | 1.621 | 1.136 | 0.628 | 0.19 | -0.299 | Primary | 2898
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NG FES - System Transformation | 8.713 | 8.226 | 9.922 | 9.645 | 9.33 | 8.99 | 8.625 | 6.575 | 2.782 | -1.04 | -6.33 | Primary | 2899
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NG FES - System Transformation | 7.127 | 7.116 | 7.061 | 6.985 | 6.886 | 6.764 | 6.588 | 5.403 | 2.228 | -1.767 | -7.937 | Primary | 2900
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NG FES - System Transformation | 32.7 | 31.312 | 31.245 | 31.17 | 31.083 | 30.985 | 30.884 | 30.172 | 29.035 | 27.652 | 25.552 | Primary | 2901
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NG FES - System Transformation | 12.167 | 12.026 | 11.828 | 11.619 | 11.39 | 11.147 | 10.9 | 9.488 | 6.735 | 3.665 | -0.93 | Primary | 2902
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NG FES - System Transformation | 8.846 | 8.133 | 7.896 | 7.706 | 7.501 | 7.288 | 7.071 | 5.977 | 4.405 | 2.52 | -0.236 | Primary | 2903
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NG FES - System Transformation | 8.75 | 8.805 | 8.843 | 8.869 | 8.881 | 8.879 | 8.856 | 8.578 | 7.775 | 6.772 | 5.332 | Primary | 2904
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NG FES - System Transformation | 13.932 | 13.882 | 13.793 | 13.684 | 13.556 | 13.415 | 13.257 | 12.329 | 10.016 | 7.802 | 4.854 | Primary | 2905
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NG FES - System Transformation | 14.633 | 14.557 | 14.433 | 14.256 | 14.016 | 13.709 | 13.322 | 10.576 | 6.652 | 3.982 | 1.72 | Primary | 2906
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NG FES - System Transformation | 18.739 | 18.603 | 18.438 | 18.254 | 18.052 | 17.833 | 17.59 | 16.148 | 13.183 | 9.809 | 5.354 | Primary | 2907
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NG FES - System Transformation | 5.5 | 4.469 | 4.198 | 3.907 | 3.589 | 3.247 | 2.851 | 0.664 | -2.791 | -6.576 | -11.242 | Primary | 2908
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NG FES - System Transformation | 5.376 | 3.922 | 3.032 | 2.102 | 1.118 | 0.066 | -1.138 | -6.962 | -12.268 | -19.686 | -30.219 | Primary | 2909
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NG FES - System Transformation | 13.184 | 12.366 | 12.023 | 11.753 | 11.461 | 11.155 | 10.805 | 9.203 | 6.927 | 4.537 | 1.318 | Primary | 2910
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NG FES - System Transformation | 15.716 | 14.939 | 14.631 | 14.312 | 13.962 | 13.59 | 13.189 | 11.049 | 7.658 | 3.817 | -1.929 | Primary | 2911
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NG FES - System Transformation | 9.88 | 9.742 | 9.526 | 9.287 | 9.021 | 8.735 | 8.425 | 6.729 | 4.051 | 1.067 | -3.389 | Primary | 2912
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NG FES - System Transformation | 11.05 | 11.066 | 11.071 | 11.071 | 11.065 | 11.052 | 11.032 | 10.858 | 10.488 | 10.134 | 9.786 | Primary | 2913
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NG FES - System Transformation | 21.438 | 21.371 | 21.271 | 21.159 | 21.034 | 20.894 | 20.716 | 19.754 | 18.66 | 17.137 | 14.924 | Primary | 2914
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NG FES - System Transformation | 16.224 | 16.321 | 16.403 | 16.474 | 16.531 | 16.576 | 16.604 | 16.62 | 15.823 | 15.097 | 14.234 | Primary | 2915
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 10.656 | 10.342 | 9.943 | 9.546 | 9.118 | 8.665 | 8.163 | 5.643 | 2.203 | -1.882 | -7.702 | Primary | 2916
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NG FES - System Transformation | 21.899 | 21.867 | 21.824 | 21.78 | 21.729 | 21.673 | 21.606 | 21.24 | 20.647 | 19.954 | 19.038 | Primary | 2917
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NG FES - System Transformation | 2.507 | 2.327 | 2.062 | 1.783 | 1.47 | 1.135 | 0.763 | -1.196 | -4.232 | -8.205 | -14.242 | Primary | 2918
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NG FES - System Transformation | 6.6 | 6.589 | 6.574 | 6.558 | 6.54 | 6.52 | 6.499 | 6.373 | 6.094 | 5.813 | 5.425 | Primary | 2919
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NG FES - System Transformation | 7.877 | 7.146 | 6.975 | 6.82 | 6.643 | 6.449 | 6.217 | 5.127 | 3.567 | 1.456 | -1.612 | Primary | 2920
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NG FES - System Transformation | 12.761 | 12.263 | 11.598 | 10.889 | 10.105 | 9.258 | 8.331 | 3.156 | -4.084 | -11.824 | -22.725 | Primary | 2921
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NG FES - System Transformation | 10.343 | 8.897 | 8.136 | 7.8 | 7.416 | 6.997 | 6.535 | 3.93 | -0.39 | -4.919 | -11.271 | Primary | 2922
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NG FES - System Transformation | 3.891 | 3.712 | 3.5 | 3.282 | 3.043 | 2.788 | 2.515 | 0.962 | -1.416 | -3.662 | -6.419 | Primary | 2923
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NG FES - System Transformation | 3.904 | 3.823 | 3.735 | 3.644 | 3.547 | 3.444 | 3.336 | 2.741 | 2.022 | 1.317 | 0.586 | Primary | 2924
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NG FES - System Transformation | 3.062 | 2.728 | 23.897 | 23.738 | 23.538 | 23.294 | 22.974 | 20.957 | 17.669 | 14.643 | 10.957 | Primary | 2925
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NG FES - System Transformation | 13.776 | 13.254 | 12.914 | 12.578 | 12.217 | 11.841 | 11.44 | 9.593 | 7.87 | 6.224 | 4.069 | Primary | 2926
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NG FES - System Transformation | 4.315 | 4.172 | 3.995 | 3.819 | 3.635 | 3.447 | 3.252 | 2.3 | 1.238 | 0.026 | -1.676 | Primary | 2927
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NG FES - System Transformation | 3.555 | 3.423 | 3.264 | 3.107 | 2.934 | 2.751 | 2.556 | 1.517 | 0.192 | -1.002 | -2.431 | Primary | 2928
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NG FES - System Transformation | 13.886 | 13.299 | 13.013 | 12.702 | 12.353 | 11.972 | 11.533 | 9.203 | 4.902 | 0.492 | -5.645 | Primary | 2929
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NG FES - System Transformation | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 2930
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NG FES - System Transformation | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 2931
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NG FES - System Transformation | 17.538 | 17.024 | 16.864 | 16.701 | 16.516 | 16.319 | 16.102 | 14.9 | 12.621 | 10.023 | 6.264 | Primary | 2932
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NG FES - System Transformation | 15.241 | 14.173 | 14.087 | 13.993 | 13.885 | 13.765 | 13.63 | 12.835 | 11.751 | 10.843 | 9.887 | Primary | 2933
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NG FES - System Transformation | 10.768 | 10.601 | 10.382 | 10.172 | 9.934 | 9.674 | 9.371 | 7.769 | 5.365 | 2.657 | -1.206 | Primary | 2934
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NG FES - System Transformation | 12.89 | 12.605 | 12.267 | 11.958 | 11.62 | 11.263 | 10.881 | 8.897 | 6.227 | 3.691 | 0.448 | Primary | 2935
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NG FES - System Transformation | 10.406 | 9.598 | 9.399 | 9.178 | 8.934 | 8.672 | 8.392 | 6.818 | 4.354 | 1.562 | -2.397 | Primary | 2936
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NG FES - System Transformation | 11.175 | 11.096 | 10.974 | 10.839 | 10.68 | 10.498 | 10.283 | 8.975 | 6.737 | 4.137 | 0.26 | Primary | 2937
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NG FES - System Transformation | 18.638 | 17.859 | 17.856 | 17.839 | 17.803 | 17.75 | 17.67 | 17.091 | 15.485 | 13.832 | 11.599 | Primary | 2938
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NG FES - System Transformation | 16.318 | 16.063 | 15.732 | 15.394 | 15.008 | 14.581 | 14.092 | 11.294 | 7.325 | 3.46 | -1.591 | Primary | 2939
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NG FES - System Transformation | 8.843 | 8.704 | 8.52 | 8.34 | 8.143 | 7.936 | 7.715 | 6.617 | 5.353 | 4.221 | 2.708 | Primary | 2940
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NG FES - System Transformation | 12.623 | 12.261 | 10.512 | 10.224 | 9.889 | 9.495 | 8.986 | 6.063 | 2.129 | -2.629 | -9.246 | Primary | 2941
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NG FES - System Transformation | 23.047 | 13.555 | 6.529 | 6.24 | 5.91 | 5.543 | 5.11 | 2.757 | -0.866 | -4.736 | -9.819 | Primary | 2942
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NG FES - System Transformation | 2.279 | 1.501 | 0.918 | -1.387 | -1.936 | -2.51 | -3.135 | -6.24 | -10.665 | -15.384 | -22.07 | Primary | 2943
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NG FES - System Transformation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 2944
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NG FES - System Transformation | 5.428 | 5.32 | 5.191 | 5.052 | 4.894 | 4.722 | 4.528 | 3.347 | 1.319 | -0.78 | -3.457 | Primary | 2945
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NG FES - System Transformation | 11.97 | 11.182 | 10.93 | 10.656 | 10.353 | 10 | 9.525 | 6.967 | 4.295 | 0.714 | -4.136 | Primary | 2946
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 7.884 | 6.273 | 6.229 | 6.164 | 6.073 | 5.96 | 5.804 | 4.822 | 2.339 | -0.167 | -3.532 | Primary | 2947
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NG FES - System Transformation | 27.949 | 27.966 | 27.982 | 27.996 | 28.008 | 28.02 | 28.029 | 28.062 | 28.072 | 28.075 | 28.079 | Primary | 2948
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NG FES - System Transformation | 19.863 | 18.852 | 18.573 | 18.277 | 17.959 | 17.627 | 17.271 | 15.456 | 12.856 | 9.77 | 5.247 | Primary | 2949
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NG FES - System Transformation | 8.209 | 7.536 | 7.623 | 7.656 | 7.621 | 7.517 | 7.335 | 5.583 | 2.74 | 0.996 | -0.383 | Primary | 2950
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NG FES - System Transformation | 4.1 | 3.964 | 3.887 | 3.803 | 3.711 | 3.612 | 3.505 | 2.872 | 2.024 | 1.136 | 0.241 | Primary | 2951
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NG FES - System Transformation | 14.237 | 13.979 | 13.656 | 13.349 | 13.02 | 12.679 | 12.317 | 10.39 | 7.155 | 2.976 | -3.659 | Primary | 2952
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NG FES - System Transformation | 2.4 | 2.085 | 1.696 | 1.296 | 0.86 | 0.397 | -0.102 | -2.766 | -6.389 | -9.732 | -13.846 | Primary | 2953
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NG FES - System Transformation | 8.689 | 7.773 | 7.5 | 7.222 | 6.921 | 6.603 | 6.254 | 4.648 | 3.057 | 1.406 | -0.642 | Primary | 2954
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NG FES - System Transformation | 25.107 | 24.6 | 24.223 | 23.821 | 23.385 | 22.922 | 22.428 | 19.747 | 15.521 | 10.986 | 4.617 | Primary | 2955
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NG FES - System Transformation | 11.585 | 11.413 | 11.149 | 10.864 | 10.542 | 10.188 | 9.758 | 7.526 | 4.212 | 0.125 | -5.988 | Primary | 2956
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NG FES - System Transformation | 11.178 | 10.891 | 10.524 | 10.159 | 9.764 | 9.346 | 8.88 | 6.444 | 2.493 | -1.85 | -8.129 | Primary | 2957
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NG FES - System Transformation | 13.887 | 13.68 | 13.763 | 13.833 | 13.885 | 13.924 | 13.94 | 13.868 | 13.021 | 12.103 | 10.853 | Primary | 2958
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NG FES - System Transformation | 32.572 | 32.128 | 31.617 | 31.139 | 30.63 | 30.101 | 29.563 | 26.719 | 22.453 | 17.736 | 11.198 | Primary | 2959
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NG FES - System Transformation | 9.699 | 8.118 | 8.029 | 7.925 | 7.796 | 7.644 | 7.475 | 6.361 | 4.513 | 2.692 | 0.103 | Primary | 2960
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NG FES - System Transformation | 8.192 | 7.462 | 7.158 | 6.835 | 6.486 | 6.119 | 5.746 | 3.704 | 0.546 | -3.139 | -8.605 | Primary | 2961
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NG FES - System Transformation | 30.736 | 30.746 | 30.753 | 30.761 | 30.767 | 30.772 | 30.777 | 30.785 | 30.767 | 30.733 | 30.678 | Primary | 2962
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NG FES - System Transformation | 9.013 | 9.014 | 24.39 | 24.355 | 24.308 | 24.25 | 24.171 | 23.69 | 22.481 | 20.846 | 18.301 | Primary | 2963
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NG FES - System Transformation | 8.632 | 6.966 | 21.641 | 21.336 | 20.999 | 20.64 | 20.257 | 18.19 | 14.473 | 10.772 | 5.647 | Primary | 2964
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NG FES - System Transformation | 9.435 | 9.19 | 8.889 | 8.571 | 8.224 | 7.849 | 7.427 | 5.155 | 1.902 | -1.114 | -4.725 | Primary | 2965
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NG FES - System Transformation | 12.086 | 11.969 | 11.821 | 11.678 | 11.528 | 11.376 | 11.226 | 10.514 | 9.764 | 8.844 | 7.419 | Primary | 2966
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NG FES - System Transformation | 20.208 | 19.659 | 19.577 | 19.492 | 19.39 | 19.279 | 19.162 | 18.378 | 16.59 | 14.482 | 11.224 | Primary | 2967
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NG FES - System Transformation | 10.755 | 10.343 | 9.843 | 9.408 | 8.927 | 8.409 | 7.835 | 4.903 | 1.096 | -2.812 | -8.222 | Primary | 2968
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NG FES - System Transformation | 12.191 | 11.822 | 11.58 | 11.32 | 11.039 | 10.745 | 10.442 | 8.791 | 6.134 | 2.631 | -2.771 | Primary | 2969
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NG FES - System Transformation | 10.827 | 10.239 | 9.911 | 9.573 | 9.207 | 8.826 | 8.432 | 6.436 | 3.569 | 0.427 | -4.294 | Primary | 2970
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 4.86 | 4.861 | 4.852 | 4.838 | 4.816 | 4.789 | 4.75 | 4.48 | 3.704 | 2.904 | 1.798 | Primary | 2971
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NG FES - System Transformation | 4.71 | 4.711 | 4.7 | 4.679 | 4.646 | 4.604 | 4.543 | 4.143 | 3.133 | 2.214 | 1.105 | Primary | 2972
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 7.49 | 7.42 | 7.319 | 7.215 | 7.099 | 6.974 | 6.828 | 6.108 | 5.159 | 4.207 | 2.913 | Primary | 2973
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NG FES - System Transformation | 7.353 | 7.29 | 7.2 | 7.105 | 6.998 | 6.883 | 6.742 | 6.041 | 4.816 | 3.517 | 1.74 | Primary | 2974
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NG FES - System Transformation | 13.103 | 12.883 | 12.605 | 12.32 | 12.018 | 11.708 | 11.399 | 9.697 | 6.825 | 3.457 | -1.714 | Primary | 2975
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NG FES - System Transformation | 21.938 | 21.6 | 21.206 | 20.875 | 20.513 | 20.129 | 19.692 | 17.531 | 14.549 | 11.441 | 7.194 | Primary | 2976
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NG FES - System Transformation | 29.761 | 28.857 | 28.809 | 28.757 | 28.7 | 28.637 | 28.567 | 28.142 | 27.609 | 27.12 | 26.648 | Primary | 2977
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NG FES - System Transformation | 5.798 | 5.381 | 5.358 | 5.336 | 5.31 | 5.281 | 5.245 | 5.061 | 4.692 | 4.305 | 3.796 | Primary | 2978
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NG FES - System Transformation | 11.586 | 11.596 | 11.586 | 11.57 | 11.541 | 11.502 | 11.45 | 11.052 | 9.753 | 8.238 | 6.055 | Primary | 2979
NPgN | ACKLAM | 11 | 33 | BOWESFIELD | NORTON | TS5 7LD | NPg Best View | 5.609 | 5.298 | 4.736 | 4.091 | 3.674 | 3.371 | 3.019 | 1.645 | -3.66 | -7.845 | -12.287 | Primary | 2980
NPgN | AMBERTON ROAD | 11 | 66 | HARTMOOR | HARTMOOR | TS24 8PQ | NPg Best View | 12.173 | 11.365 | 9.414 | 8.582 | 7.976 | 7.469 | 6.878 | 4.361 | -3.776 | -10.032 | -16.297 | Primary | 2981
NPgN | ANNFIELD 66/20KV | 20 | 66 | ANNFIELD | STELLA SOUTH | DH9 7XW | NPg Best View | 8.063 | 7.752 | 9.216 | 8.609 | 8.165 | 7.779 | 7.326 | 5.39 | 0.416 | -3.464 | -7.437 | Primary | 2982
NPgN | ASHINGTON | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE63 8UJ | NPg Best View | 6.296 | 6.092 | 5.671 | 5.174 | 4.839 | 4.568 | 4.244 | 2.936 | -2.104 | -6.19 | -10.349 | Primary | 2983
NPgN | AYCLIFFE FORREST | 11 | 33 | DARLINGTON NORTH | NORTON | DL1 3NL | NPg Best View | 26.376 | 26.378 | 26.379 | 26.381 | 26.382 | 26.383 | 26.384 | 26.388 | 26.391 | 26.394 | 26.396 | Primary | 2984
NPgN | AYCLIFFE INDUSTRIAL | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6HY | NPg Best View | 2.919 | 2.925 | 2.851 | 2.744 | 2.685 | 2.638 | 2.559 | 2.163 | 0.378 | -1.018 | -2.444 | Primary | 2985
NPgN | BARDEN FRIAR | 20 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5JR | NPg Best View | 4.085 | 4.064 | 4.037 | 4.01 | 3.984 | 3.958 | 3.926 | 3.773 | 3.557 | 3.384 | 3.223 | Primary | 2986
NPgN | BEDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 1AH | NPg Best View | 4.696 | 4.586 | 4.388 | 4.148 | 3.932 | 3.721 | 3.471 | 2.163 | -0.537 | -2.675 | -4.824 | Primary | 2987
NPgN | BELMONT | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 2HL | NPg Best View | 8.618 | 8.569 | 8.394 | 8.189 | 8.031 | 7.912 | 7.766 | 7.129 | 4.229 | 1.864 | -0.606 | Primary | 2988
NPgN | BENSHAM | 11 | 66 | DUNSTON | STELLA NORTH | NE8 2XY | NPg Best View | 12.691 | 12.501 | 12.159 | 11.769 | 11.514 | 11.27 | 10.939 | 9.403 | 6.18 | 3.911 | 1.723 | Primary | 2989
NPgN | BENTON SQUARE | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE12 9SR | NPg Best View | 5.095 | 4.571 | 4.157 | 3.708 | 3.339 | 2.997 | 2.599 | 0.775 | -5.076 | -9.938 | -14.67 | Primary | 2990
NPgN | BENWELL | 11 | 66 | DUNSTON | STELLA NORTH | NE4 8XQ | NPg Best View | 11.936 | 11.429 | 11.141 | 10.797 | 10.556 | 10.349 | 10.096 | 8.909 | 4.445 | 0.794 | -2.858 | Primary | 2991
NPgN | BILLINGHAM MARSH HOUSE | 11 | 66 | NORTH TEES | NORTON | TS23 2AL | NPg Best View | 7.632 | 7.29 | 6.78 | 6.215 | 5.773 | 5.344 | 4.839 | 2.292 | -2.122 | -5.358 | -8.574 | Primary | 2992
NPgN | BILLY MILL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE29 8LP | NPg Best View | 6.832 | 6.236 | 5.888 | 5.498 | 5.222 | 4.973 | 4.675 | 3.316 | -0.735 | -3.981 | -7.183 | Primary | 2993
NPgN | BIRTLEY GROVE 66/11KV | 11 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 13.324 | 13.206 | 12.968 | 12.685 | 12.399 | 12.084 | 11.211 | 7.387 | 4.63 | 2.973 | 1.509 | Primary | 2994
NPgN | BIRTLEY GROVE 66/20KV | 20 | 66 | RAVENSWORTH | STELLA SOUTH | DH3 1JH | NPg Best View | 16.868 | 16.902 | 16.866 | 16.769 | 16.653 | 16.533 | 16.393 | 15.711 | 14.684 | 14.204 | 13.812 | Primary | 2995
NPgN | BLAYDON BURN | 11 | 66 | DUNSTON | STELLA NORTH | NE21 4BG | NPg Best View | 9.753 | 8.878 | 8.725 | 8.53 | 8.338 | 8.134 | 7.878 | 6.536 | 2.614 | -0.476 | -3.31 | Primary | 2996
NPgN | BLUCHER 33/11KV | 11 | 33 | BLUCHER | STELLA NORTH | NE15 9SB | NPg Best View | 10.958 | 10.367 | 10.013 | 9.619 | 9.28 | 8.96 | 8.592 | 6.931 | 2.146 | -1.8 | -5.547 | Primary | 2997
NPgN | BOLDON DOWNHILL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE36 0AS | NPg Best View | 16.165 | 16.022 | 15.784 | 15.52 | 15.322 | 15.144 | 14.93 | 13.938 | 10.701 | 8.052 | 5.5 | Primary | 2998
NPgN | BOROUGHBRIDGE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | YO51 9NS | NPg Best View | 10.44 | 10.37 | 10.24 | 10.061 | 9.869 | 9.639 | 9.35 | 7.517 | 5.367 | 4.13 | 3.077 | Primary | 2999
NPgN | BOWESFIELD 33/11KV | 11 | 33 | BOWESFIELD | NORTON | TS18 3HR | NPg Best View | 21.625 | 21.39 | 21.039 | 20.653 | 20.284 | 19.911 | 19.476 | 17.238 | 12.962 | 9.626 | 6.423 | Primary | 3000
NPgN | BOWESFIELD 66/11KV | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 17.85 | 17.743 | 17.563 | 17.36 | 17.174 | 16.986 | 16.765 | 15.701 | 12.958 | 10.583 | 8.284 | Primary | 3001
NPgN | BRANCEPETH | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL15 0TW | NPg Best View | 13.304 | 12.642 | 12.02 | 11.314 | 10.813 | 10.382 | 9.886 | 7.725 | 1.814 | -2.871 | -7.587 | Primary | 3002
NPgN | BREAMISH STREET | 11 | 66 | WEST BOLDON | WEST BOLDON | NE1 2BL | NPg Best View | 7.934 | 7.438 | 7.34 | 7.22 | 7.148 | 7.101 | 7.035 | 6.749 | 4.791 | 3.232 | 1.644 | Primary | 3003
NPgN | BRENDA TRADING | 11 | 66 | HARTMOOR | HARTMOOR | TS25 1PD | NPg Best View | 9.224 | 8.904 | 8.298 | 7.587 | 7.066 | 6.627 | 6.094 | 3.531 | -2.453 | -6.746 | -11.244 | Primary | 3004
NPgN | CAMPLESHON ROAD | 11 | 33 | MELROSEGATE | OSBALDWICK | YO23 1HZ | NPg Best View | 8.034 | 7.492 | 7.003 | 6.511 | 6.134 | 5.811 | 5.422 | 3.83 | 0.156 | -2.614 | -5.393 | Primary | 3005
NPgN | CARLEY HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 1SG | NPg Best View | 8.153 | 7.931 | 7.532 | 7.072 | 6.722 | 6.427 | 6.077 | 4.521 | -0.028 | -3.524 | -6.992 | Primary | 3006
NPgN | CARLIN HOW T3 T4 | 11 | 66 | LACKENBY | LACKENBY | TS13 4DL | NPg Best View | 9.175 | 9.017 | 8.706 | 8.354 | 8.024 | 7.718 | 7.365 | 5.916 | 1.792 | -1.616 | -4.867 | Primary | 3007
NPgN | CARR HILL | 11 | 66 | WEST BOLDON | WEST BOLDON | NE10 9SY | NPg Best View | 3.991 | 3.778 | 3.346 | 2.832 | 2.443 | 2.093 | 1.676 | -0.194 | -5.989 | -10.614 | -15.12 | Primary | 3008
NPgN | CATTERICK CAMP | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL9 3HE | NPg Best View | 7.922 | 7.62 | 7.168 | 6.657 | 6.226 | 5.825 | 5.365 | 3.267 | -1.622 | -5.73 | -9.845 | Primary | 3009
NPgN | CLOSE | 11 | 66 | DUNSTON | STELLA NORTH | NE1 3NB | NPg Best View | 10.486 | 10.363 | 10.491 | 10.581 | 10.673 | 10.756 | 10.805 | 10.936 | 9.408 | 8.21 | 7.045 | Primary | 3010
NPgN | CONEYTHORPE | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG5 0RZ | NPg Best View | 6.535 | 5.664 | 5.465 | 5.26 | 5.081 | 4.907 | 4.689 | 3.707 | 1.12 | -0.94 | -2.922 | Primary | 3011
NPgN | CONSETT | 20 | 66 | ANNFIELD | STELLA SOUTH | DH8 7ND | NPg Best View | 17.23 | 16.023 | 15.406 | 14.666 | 14.12 | 13.632 | 13.051 | 10.342 | 3.9 | -0.873 | -5.66 | Primary | 3012
NPgN | CORPORATION STREET | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE4 5SS | NPg Best View | 13.062 | 13.073 | 13.023 | 12.949 | 12.913 | 12.892 | 12.849 | 12.663 | 11.36 | 10.34 | 9.274 | Primary | 3013
NPgN | COWTON | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL6 2NF | NPg Best View | 6.787 | 6.763 | 6.727 | 6.689 | 6.659 | 6.632 | 6.601 | 6.472 | 6.176 | 5.941 | 5.708 | Primary | 3014
NPgN | CRAMLINGTON T1 T3 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 12.787 | 12.815 | 12.786 | 12.721 | 12.68 | 12.643 | 12.581 | 12.178 | 10.44 | 9.113 | 7.819 | Primary | 3015
NPgN | CRAMLINGTON T2 T4 | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 8AJ | NPg Best View | 16.869 | 16.839 | 16.75 | 16.623 | 16.526 | 16.432 | 16.308 | 15.513 | 13.697 | 12.42 | 11.165 | Primary | 3016
NPgN | DARLEY | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG3 2PP | NPg Best View | 4.791 | 4.756 | 4.689 | 4.618 | 4.578 | 4.557 | 4.532 | 4.41 | 3.463 | 2.661 | 1.798 | Primary | 3017
NPgN | DARLINGTON 132/6KV | 6 | 132 | DARLINGTON 132/6kV | NORTON | DL1 1SW | NPg Best View | 9.197 | 9.07 | 8.87 | 8.656 | 8.519 | 8.403 | 8.268 | 7.667 | 5.701 | 4.145 | 2.593 | Primary | 3018
NPgN | DARLINGTON 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1SW | NPg Best View | 10.413 | 10.279 | 10.004 | 9.693 | 9.454 | 9.239 | 8.977 | 7.83 | 3.691 | 0.346 | -2.85 | Primary | 3019
NPgN | DARLINGTON CENTRAL 33/11KV | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 1HG | NPg Best View | 23.191 | 22.943 | 22.93 | 22.91 | 22.896 | 22.884 | 22.856 | 22.762 | 21.568 | 20.555 | 19.624 | Primary | 3020
NPgN | DARLINGTON EAST | 11 | 33 | DARLINGTON CENTRAL | NORTON | DL1 4NP | NPg Best View | 6.91 | 6.865 | 6.688 | 6.464 | 6.277 | 6.074 | 5.8 | 4.277 | 0.67 | -1.866 | -4.19 | Primary | 3021
NPgN | DARLINGTON WEST | 11 | 33 | DARLINGTON NORTH | NORTON | DL3 9QG | NPg Best View | 5.209 | 4.461 | 3.862 | 3.166 | 2.605 | 2.08 | 1.446 | -1.506 | -7.178 | -11.068 | -14.847 | Primary | 3022
NPgN | DENWICK | 20 | 66 | LINTON | BLYTH 132kV | NE66 3RG | NPg Best View | 12.15 | 10.955 | 10.602 | 10.187 | 9.865 | 9.575 | 9.228 | 7.648 | 2.258 | -1.991 | -6.095 | Primary | 3023
NPgN | DUNSTON 66/11KV | 11 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 9.042 | 8.978 | 8.821 | 8.647 | 8.488 | 8.319 | 8.094 | 7.009 | 4.216 | 2.017 | 0.023 | Primary | 3024
NPgN | DUNSTON 66/20KV | 20 | 66 | DUNSTON | STELLA NORTH | NE11 9DH | NPg Best View | 14.372 | 14.183 | 13.838 | 13.468 | 13.19 | 12.937 | 12.626 | 11.267 | 6.196 | 1.946 | -2.117 | Primary | 3025
NPgN | DURHAM EAST | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5SU | NPg Best View | 4.403 | 3.997 | 3.922 | 3.819 | 3.744 | 3.682 | 3.592 | 3.158 | 0.888 | -1.018 | -2.949 | Primary | 3026
NPgN | EASTFIELD | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 3BY | NPg Best View | 18.373 | 18.234 | 17.957 | 17.624 | 17.341 | 17.076 | 16.756 | 15.257 | 10.829 | 7.299 | 3.953 | Primary | 3027
NPgN | EASTGATE CEMENT | 20 | 66 | TORONTO | SPENNYMOOR | DL13 2LA | NPg Best View | 18.941 | 18.95 | 18.926 | 18.892 | 18.868 | 18.851 | 18.824 | 18.687 | 17.645 | 16.736 | 15.845 | Primary | 3028
NPgN | EDUCATIONAL PRECINCT | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE5 4JQ | NPg Best View | 8.252 | 8.147 | 7.928 | 7.688 | 7.534 | 7.409 | 7.235 | 6.414 | 3.953 | 2.081 | 0.156 | Primary | 3029
NPgN | ELVINGTON | 11 | 33 | MELROSEGATE | OSBALDWICK | YO41 4DY | NPg Best View | 9.127 | 9.143 | 9.12 | 9.079 | 9.029 | 8.967 | 8.876 | 8.288 | 7.286 | 6.596 | 5.948 | Primary | 3030
NPgN | FARADAY STREET | 11 | 66 | NORTH TEES | NORTON | TS1 4JG | NPg Best View | 1.794 | 1.68 | 1.377 | 0.994 | 0.736 | 0.541 | 0.3 | -0.725 | -5.302 | -9.034 | -12.847 | Primary | 3031
NPgN | FAWDON T1 | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE3 2SW and NE13 6BH | NPg Best View | 5.762 | 5.228 | 4.502 | 3.844 | 3.347 | 2.852 | 2.228 | -0.597 | -6.113 | -10.199 | -14.02 | Primary | 3032
NPgN | FISHBURN | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | TS29 6JQ | NPg Best View | 10.686 | 10.284 | 8.902 | 8.198 | 7.684 | 7.255 | 6.759 | 4.537 | -1.3 | -5.762 | -10.404 | Primary | 3033
NPgN | FLATWORTH CENTRAL | 11 | 33 | FLATWORTH | TYNEMOUTH | NE29 7SH | NPg Best View | 15.742 | 15.465 | 15.445 | 15.396 | 15.325 | 15.235 | 15.106 | 14.354 | 12.977 | 12.005 | 11.117 | Primary | 3034
NPgN | FOSS ISLANDS | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 7US | NPg Best View | 11.052 | 9.708 | 9.426 | 9.065 | 8.806 | 8.584 | 8.297 | 6.894 | 0.722 | -4.179 | -8.955 | Primary | 3035
NPgN | FOSSWAY 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE6 4AN | NPg Best View | 8.13 | 7.784 | 7.217 | 6.574 | 6.116 | 5.71 | 5.219 | 2.953 | -2.718 | -7.15 | -11.608 | Primary | 3036
NPgN | FOURSTONES 20KV | 20 | 275 | FOURSTONES | FOURSTONES | NE47 5DY | NPg Best View | 22.93 | 22.596 | 22.081 | 21.584 | 21.227 | 20.896 | 20.466 | 18.512 | 14.64 | 11.852 | 9.081 | Primary | 3037
NPgN | FYLANDS BRIDGE | 11 | 66 | TORONTO | SPENNYMOOR | DL14 9TA | NPg Best View | 5.296 | 5.093 | 4.71 | 4.266 | 3.937 | 3.657 | 3.324 | 1.862 | -2.526 | -6.052 | -9.648 | Primary | 3038
NPgN | GALE LANE | 11 | 33 | POPPLETON | POPPLETON | YO24 3AF | NPg Best View | 11.85 | 11.662 | 11.337 | 10.99 | 10.764 | 10.599 | 10.408 | 9.72 | 7.054 | 4.919 | 2.614 | Primary | 3039
NPgN | GARWOOD STREET | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 5DQ | NPg Best View | 18.336 | 18.269 | 18.084 | 17.859 | 17.666 | 17.49 | 17.279 | 16.301 | 12.817 | 10.013 | 7.327 | Primary | 3040
NPgN | GATESHEAD CENTRAL | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE8 1HB | NPg Best View | 9.433 | 9.467 | 7.985 | 7.904 | 7.846 | 7.789 | 7.702 | 7.158 | 5.394 | 4.152 | 2.931 | Primary | 3041
NPgN | GATESHEAD EAST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE8 3AH | NPg Best View | 27.498 | 27.55 | 27.569 | 27.553 | 27.504 | 27.42 | 27.294 | 26.408 | 25.419 | 24.954 | 24.643 | Primary | 3042
NPgN | GOSFORTH 33/11KV | 11 | 33 | GOSFORTH | TYNEMOUTH | NE3 1RR | NPg Best View | 14.673 | 14.24 | 14.233 | 14.202 | 14.227 | 14.278 | 14.31 | 14.446 | 13.319 | 12.412 | 11.338 | Primary | 3043
NPgN | GRANGETOWN | 11 | 66 | LACKENBY | LACKENBY | TS6 7AS | NPg Best View | 2.943 | 2.783 | 2.415 | 1.928 | 1.33 | 0.595 | -0.346 | -5.601 | -9.562 | -11.17 | -12.128 | Primary | 3044
NPgN | GREATHAM | 11 | 132 | GREATHAM | SALTHOLME | TS25 2DD | NPg Best View | 18.274 | 18.439 | 18.577 | 18.694 | 18.801 | 18.898 | 18.975 | 19.285 | 19.09 | 18.907 | 18.696 | Primary | 3045
NPgN | GUISBOROUGH T1 T2 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 7.55 | 7.087 | 6.639 | 6.139 | 5.722 | 5.338 | 4.894 | 3.042 | -1.239 | -4.545 | -7.751 | Primary | 3046
NPgN | GUISBOROUGH T3 | 11 | 66 | LACKENBY | LACKENBY | TS14 6GQ | NPg Best View | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 3047
NPgN | HARLOW GREEN | 11 | 66 | WEST BOLDON | WEST BOLDON | NE9 6NT | NPg Best View | 3.147 | 3.051 | 2.802 | 2.513 | 2.359 | 2.275 | 2.177 | 1.822 | -1.364 | -3.964 | -6.769 | Primary | 3048
NPgN | HARMIRE BRIDGE | 20 | 66 | TORONTO | SPENNYMOOR | DL12 8QJ | NPg Best View | 14.413 | 14.15 | 13.737 | 13.286 | 12.923 | 12.571 | 12.143 | 10.101 | 6.446 | 3.79 | 1.215 | Primary | 3049
NPgN | HARRATON | 11 | 132 | HARRATON | STELLA SOUTH | NE38 9BZ | NPg Best View | 15.359 | 13.029 | 13.05 | 13.05 | 13.031 | 12.999 | 12.931 | 12.545 | 10.808 | 9.494 | 8.271 | Primary | 3050
NPgN | HARROGATE 132/11KV | 11 | 132 | HARROGATE 132/11kV | KNARESBOROUGH | HG1 2BN | NPg Best View | 8.87 | 8.208 | 7.629 | 7.025 | 6.568 | 6.168 | 5.683 | 3.544 | -2.871 | -7.952 | -13.059 | Primary | 3051
NPgN | HARROGATE WEST | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 0QB | NPg Best View | 18.564 | 18.506 | 18.382 | 18.252 | 18.164 | 18.098 | 18.008 | 17.632 | 15.949 | 14.584 | 13.16 | Primary | 3052
NPgN | HARTMOOR 66/20KV | 20 | 66 | HARTMOOR | HARTMOOR | TS27 3BL | NPg Best View | 8.752 | 8.278 | 7.531 | 6.715 | 6.157 | 5.712 | 5.188 | 2.946 | -3.159 | -7.862 | -12.871 | Primary | 3053
NPgN | HAWTHORN PIT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 9NX | NPg Best View | 4.306 | 3.634 | 3.103 | 2.481 | 1.964 | 1.475 | 0.903 | -1.655 | -7.202 | -11.315 | -15.267 | Primary | 3054
NPgN | HAXBY ROAD T2 T3 | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 8FZ | NPg Best View | 3.065 | 2.754 | 2.303 | 1.858 | 1.544 | 1.289 | 0.979 | -0.327 | -3.533 | -5.954 | -8.504 | Primary | 3055
NPgN | HEBBURN | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1BD | NPg Best View | 8.549 | 8.519 | 8.448 | 23.758 | 23.672 | 23.584 | 23.474 | 22.817 | 21.868 | 21.314 | 20.788 | Primary | 3056
NPgN | HEBBURN WEST | 11 | 66 | WEST BOLDON | WEST BOLDON | NE31 1NA | NPg Best View | 21.073 | 20.799 | 20.781 | 20.75 | 20.731 | 20.719 | 20.705 | 20.649 | 19.899 | 19.293 | 18.705 | Primary | 3057
NPgN | HEDWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE32 4SW | NPg Best View | 19.351 | 19.205 | 18.919 | 18.59 | 18.364 | 18.195 | 17.993 | 17.147 | 14.081 | 11.725 | 9.244 | Primary | 3058
NPgN | HEIGHINGTON | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6JW | NPg Best View | 16.827 | 17.003 | 17.163 | 17.311 | 17.447 | 17.571 | 17.679 | 18.139 | 18.439 | 18.693 | 18.921 | Primary | 3059
NPgN | HEXHAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE46 4NT | NPg Best View | 14.936 | 15.092 | 15.176 | 15.23 | 15.299 | 15.361 | 15.38 | 15.362 | 14.358 | 13.686 | 13.002 | Primary | 3060
NPgN | HIGH BARMSTON | 11 | 66 | WEST BOLDON | WEST BOLDON | NE38 8QA | NPg Best View | 1.488 | 1.513 | 1.393 | 1.169 | 20.828 | 20.517 | 20.099 | 17.307 | 12.486 | 9.298 | 6.475 | Primary | 3061
NPgN | HIGH FLATTS | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH2 2LR | NPg Best View | 7.79 | 7.487 | 7 | 6.482 | 6.093 | 5.757 | 5.37 | 3.798 | -0.379 | -3.705 | -7.109 | Primary | 3062
NPgN | HOUGHTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | DH4 5HP | NPg Best View | 6.984 | 6.686 | 6.191 | 5.63 | 5.211 | 4.825 | 4.364 | 2.356 | -1.889 | -4.905 | -7.853 | Primary | 3063
NPgN | HOWDON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 0JX | NPg Best View | 17.765 | 17.719 | 17.628 | 17.525 | 17.409 | 17.283 | 17.133 | 16.41 | 14.797 | 13.481 | 12.279 | Primary | 3064
NPgN | HUNTINGTON NEW LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO32 9TA | NPg Best View | 6.782 | 6.701 | 6.521 | 6.329 | 6.161 | 6.007 | 5.819 | 5.046 | 2.685 | 0.857 | -0.934 | Primary | 3065
NPgN | HUSTHWAITE 33/11KV | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO61 4PN | NPg Best View | 6.948 | 6.689 | 6.322 | 5.948 | 5.629 | 5.32 | 4.956 | 3.279 | 0.137 | -2.301 | -4.687 | Primary | 3066
NPgN | JARROW | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE32 5LD | NPg Best View | 18.689 | 18.69 | 18.657 | 18.61 | 18.574 | 18.539 | 18.491 | 18.234 | 17.415 | 16.788 | 16.175 | Primary | 3067
NPgN | KENTON | 11 | 33 | BLUCHER | STELLA NORTH | NE3 4UP | NPg Best View | 7.105 | 6.909 | 6.564 | 6.211 | 5.948 | 5.73 | 5.476 | 4.518 | 1.57 | -0.751 | -3.132 | Primary | 3068
NPgN | KIELDER | 20 | 33 | SPADEADAM 33kV | SPADEADAM | NE48 1BH | NPg Best View | 2.8 | 2.788 | 2.766 | 2.741 | 2.722 | 2.703 | 2.679 | 2.564 | 2.285 | 2.08 | 1.885 | Primary | 3069
NPgN | KILLINGWORTH | 11 | 33 | GOSFORTH | TYNEMOUTH | NE12 6QQ | NPg Best View | 9.333 | 9.034 | 8.902 | 8.749 | 8.604 | 8.471 | 8.313 | 7.547 | 5.159 | 3.258 | 1.395 | Primary | 3070
NPgN | KIRBYMOORSIDE | 11 | 66 | MALTON GRID | OSBALDWICK | YO62 6EZ | NPg Best View | 15.142 | 15.012 | 14.787 | 14.541 | 14.349 | 14.176 | 13.968 | 13.064 | 10.817 | 9.066 | 7.332 | Primary | 3071
NPgN | LEAM CENTRAL | 20 | 66 | WEST BOLDON | WEST BOLDON | NE10 8NQ | NPg Best View | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | Primary | 3072
NPgN | LINTON 66/20KV | 20 | 66 | LINTON | BLYTH 132kV | NE61 3AX | NPg Best View | 21.313 | 21.186 | 20.977 | 20.758 | 20.594 | 20.452 | 20.283 | 19.534 | 17.177 | 15.321 | 13.476 | Primary | 3073
NPgN | LONGBENTON | 11 | 33 | GOSFORTH | TYNEMOUTH | NE7 7LR | NPg Best View | 8.634 | 8.389 | 7.965 | 7.514 | 7.238 | 7.042 | 6.81 | 5.874 | 2.071 | -0.949 | -4.166 | Primary | 3074
NPgN | LOW SPENNYMOOR | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL16 7RS | NPg Best View | 14.305 | 14.092 | 13.739 | 13.347 | 13.079 | 12.857 | 12.597 | 11.425 | 8.131 | 5.598 | 3.002 | Primary | 3075
NPgN | LYNEMOUTH | 20 | 66 | LINTON | BLYTH 132kV | NE61 5XH | NPg Best View | 33.39 | 33.045 | 33.021 | 32.991 | 32.974 | 32.965 | 32.947 | 32.888 | 32.318 | 31.87 | 31.414 | Primary | 3076
NPgN | MADDISON STREET | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE24 1HD | NPg Best View | 4.473 | 3.716 | 3.077 | 2.372 | 1.866 | 1.461 | 0.978 | -0.905 | -5.796 | -9.452 | -13.303 | Primary | 3077
NPgN | MALLEABLE | 11 | 66 | NORTH TEES | NORTON | TS18 2NR | NPg Best View | 15.087 | 14.377 | 14.066 | 13.688 | 13.34 | 12.997 | 12.607 | 10.525 | 5.92 | 2.206 | -1.51 | Primary | 3078
NPgN | MALTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 6BT | NPg Best View | 12.098 | 12.068 | 11.928 | 11.76 | 11.551 | 11.334 | 11.069 | 9.789 | 5.763 | 2.453 | -0.614 | Primary | 3079
NPgN | MEADOWFIELD | 11 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH7 8ER | NPg Best View | 15.059 | 15.034 | 14.956 | 14.859 | 14.782 | 14.716 | 14.632 | 14.185 | 12.631 | 11.381 | 10.113 | Primary | 3080
NPgN | MELROSEGATE 33/11KV | 11 | 33 | MELROSEGATE | OSBALDWICK | YO31 0YB | NPg Best View | 24.425 | 22.646 | 22.345 | 22.021 | 21.782 | 21.563 | 21.3 | 20.191 | 17.494 | 15.381 | 13.319 | Primary | 3081
NPgN | MILLBANK LANE | 11 | 33 | BOWESFIELD | NORTON | TS17 0AX | NPg Best View | 5.358 | 4.903 | 4.567 | 4.189 | 3.864 | 3.551 | 3.193 | 1.546 | -3.089 | -7.049 | -10.915 | Primary | 3082
NPgN | MONKSEATON | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE25 9AF | NPg Best View | 1.586 | 0.848 | 0.272 | -0.32 | -0.768 | -1.139 | -1.572 | -3.392 | -9.219 | -14.07 | -19.032 | Primary | 3083
NPgN | MOOR MONKTON PUMPS | 11 | 33 | POPPLETON | POPPLETON | YO30 1BY | NPg Best View | 3.41 | 3.389 | 2.065 | 2.016 | 1.973 | 1.926 | 1.861 | 1.529 | 1.127 | 0.869 | 0.63 | Primary | 3084
NPgN | MORPETH | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE61 6JH | NPg Best View | 8.983 | 8.596 | 10.307 | 9.998 | 9.754 | 9.518 | 9.215 | 7.826 | 3.198 | -0.511 | -4.048 | Primary | 3085
NPgN | MOUNT ROAD | 11 | 33 | OFFERTON | OFFERTON | SR4 7LJ | NPg Best View | 7.354 | 7.255 | 6.989 | 6.654 | 6.495 | 6.412 | 6.306 | 5.749 | 1.203 | -2.57 | -6.55 | Primary | 3086
NPgN | NEWBURN HAUGH | 11 | 132 | NEWBURN HAUGH | STELLA NORTH | NE15 8SF | NPg Best View | 32.752 | 31.396 | 31.344 | 31.278 | 31.203 | 31.123 | 31.024 | 30.479 | 28.778 | 27.331 | 25.993 | Primary | 3087
NPgN | NEWBY | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO12 6NL | NPg Best View | 12.288 | 12.203 | 12.008 | 11.778 | 11.589 | 11.411 | 11.198 | 10.283 | 6.518 | 3.325 | 0.326 | Primary | 3088
NPgN | NEWCASTLE AIRPORT | 11 | 33 | BLUCHER | STELLA NORTH | NE13 8DF | NPg Best View | 9.016 | 8.367 | 8.132 | 7.923 | 7.757 | 7.606 | 7.428 | 6.755 | 4.637 | 2.952 | 1.335 | Primary | 3089
NPgN | NEWTON AYCLIFFE SOUTH | 11 | 33 | DARLINGTON NORTH | NORTON | DL5 6EA | NPg Best View | 8.936 | 9.03 | 9.079 | 9.1 | 9.154 | 9.211 | 9.247 | 9.335 | 8.476 | 7.801 | 7.074 | Primary | 3090
NPgN | NORTH STREET | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 1DU | NPg Best View | 14.021 | 14.013 | 13.935 | 13.822 | 13.712 | 13.604 | 13.47 | 12.83 | 10.073 | 7.801 | 5.707 | Primary | 3091
NPgN | NORTH TEES T1 T2 | 11 | 66 | NORTH TEES | NORTON | TS23 1PX | NPg Best View | 14.878 | 14.886 | 14.809 | 14.642 | 14.41 | 14.092 | 13.665 | 10.886 | 7.73 | 5.909 | 4.415 | Primary | 3092
NPgN | NORTH TEES T3 T4 | 11 | 66 | NORTH TEES | NORTON | TS23 1PY | NPg Best View | 19.018 | 18.924 | 18.744 | 18.511 | 18.372 | 18.257 | 18.116 | 17.316 | 14.031 | 11.16 | 8.187 | Primary | 3093
NPgN | NORTHALLERTON | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 0QE | NPg Best View | 5.737 | 4.75 | 4.455 | 4.109 | 3.814 | 3.541 | 3.239 | 1.759 | -1.978 | -5.081 | -8.207 | Primary | 3094
NPgN | NORTON 132/11KV | 11 | 132 | NORTON 132/11kV | NORTON | TS21 1EG | NPg Best View | 6.026 | 4.533 | 3.44 | 2.217 | 1.275 | 0.463 | -0.462 | -4.263 | -11.967 | -17.832 | -23.873 | Primary | 3095
NPgN | OATLANDS | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 8BY | NPg Best View | 13.482 | 12.692 | 12.302 | 11.945 | 11.685 | 11.466 | 11.2 | 10.11 | 7.384 | 5.298 | 3.147 | Primary | 3096
NPgN | OFFERTON 33/11KV | 11 | 33 | OFFERTON | OFFERTON | SR4 9NR | NPg Best View | 15.884 | 15.105 | 14.692 | 14.232 | 13.886 | 13.584 | 13.228 | 11.774 | 7.144 | 3.45 | -0.156 | Primary | 3097
NPgN | PALLION TRADING | 11 | 33 | OFFERTON | OFFERTON | SR4 6SN | NPg Best View | 10.039 | 9.938 | 9.691 | 9.396 | 9.163 | 8.955 | 8.7 | 7.633 | 4.024 | 1.111 | -1.674 | Primary | 3098
NPgN | PETERLEE INDUSTRIAL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2HR | NPg Best View | 11.177 | 11.253 | 11.317 | 11.372 | 11.419 | 11.458 | 11.486 | 11.569 | 11.486 | 11.399 | 11.304 | Primary | 3099
NPgN | PETERLEE WEST | 11 | 66 | HARTMOOR | HARTMOOR | DH6 2RA | NPg Best View | 21.577 | 21.534 | 21.419 | 21.262 | 21.158 | 21.071 | 20.964 | 20.518 | 18.992 | 17.784 | 16.546 | Primary | 3100
NPgN | PILGRIM | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE1 2LA | NPg Best View | 16.425 | 16.609 | 16.762 | 16.891 | 17.013 | 17.125 | 17.217 | 17.587 | 17.042 | 16.602 | 16.174 | Primary | 3101
NPgN | POTTER HOUSE T1 T3 | 20 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 10.883 | 10.534 | 9.984 | 9.389 | 8.934 | 8.543 | 8.1 | 6.269 | 1.534 | -2.18 | -5.949 | Primary | 3102
NPgN | POTTER HOUSE T4 T5 | 11 | 66 | POTTER HOUSE | SPENNYMOOR | DH1 5FF | NPg Best View | 22.009 | 22.004 | 21.967 | 21.927 | 21.901 | 21.883 | 21.853 | 21.721 | 21.136 | 20.66 | 20.152 | Primary | 3103
NPgN | PRISSICK | 11 | 66 | LACKENBY | LACKENBY | TS4 3SG | NPg Best View | 2.755 | 2.571 | 2.189 | 1.753 | 1.441 | 1.191 | 0.894 | -0.224 | -4.804 | -8.49 | -12.162 | Primary | 3104
NPgN | RAVENSCAR | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO13 0LZ | NPg Best View | 6.616 | 6.607 | 6.587 | 6.562 | 6.546 | 6.533 | 6.516 | 6.44 | 6.102 | 5.831 | 5.568 | Primary | 3105
NPgN | RAWCLIFFE LANE | 11 | 33 | MELROSEGATE | OSBALDWICK | YO30 5SW | NPg Best View | 8.199 | 7.454 | 7.178 | 6.905 | 6.699 | 6.549 | 6.37 | 5.721 | 3.479 | 1.792 | -0.054 | Primary | 3106
NPgN | REDCAR | 11 | 66 | LACKENBY | LACKENBY | TS10 2PA | NPg Best View | 13.065 | 12.573 | 11.766 | 10.852 | 10.052 | 9.29 | 8.399 | 4.224 | -5.277 | -12.722 | -19.839 | Primary | 3107
NPgN | RESERVOIR | 20 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 5QP | NPg Best View | 10.593 | 9.156 | 8.298 | 7.817 | 7.438 | 7.085 | 6.656 | 4.649 | -0.869 | -5.112 | -9.234 | Primary | 3108
NPgN | RICHMOND T1 | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL10 5BJ | NPg Best View | 3.999 | 3.873 | 3.683 | 3.471 | 3.258 | 3.036 | 2.779 | 1.497 | -0.974 | -2.976 | -4.858 | Primary | 3109
NPgN | RICHMOND T2 | 11 | 33 | DARLINGTON NORTH | NORTON | DL10 5BJ | NPg Best View | 4.018 | 3.994 | 3.957 | 3.914 | 3.867 | 3.814 | 3.749 | 3.406 | 2.915 | 2.475 | 2.049 | Primary | 3110
NPgN | RIPON | 11 | 33 | WORMALD GREEN 132/33kV | KNARESBOROUGH | HG4 1QE | NPg Best View | 3.335 | 2.979 | 24.05 | 23.757 | 23.521 | 23.292 | 22.996 | 21.232 | 17.796 | 15.398 | 12.992 | Primary | 3111
NPgN | RISE CARR | 6 | 33 | DARLINGTON NORTH | NORTON | DL3 0RP | NPg Best View | 13.976 | 13.493 | 13.146 | 12.782 | 12.49 | 12.215 | 11.879 | 10.517 | 8.503 | 7.174 | 5.91 | Primary | 3112
NPgN | ROMANBY | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL7 8HP | NPg Best View | 4.397 | 4.269 | 4.079 | 3.875 | 3.723 | 3.584 | 3.424 | 2.771 | 1.421 | 0.364 | -0.675 | Primary | 3113
NPgN | RUDBY | 11 | 33 | BOWESFIELD | NORTON | TS15 0JT | NPg Best View | 3.634 | 3.534 | 3.387 | 3.23 | 3.086 | 2.938 | 2.761 | 1.909 | 0.553 | -0.476 | -1.442 | Primary | 3114
NPgN | SCARBOROUGH 33/11KV | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO11 2YH | NPg Best View | 14.136 | 13.574 | 13.229 | 12.813 | 12.484 | 12.194 | 11.842 | 10.26 | 4.847 | 0.485 | -3.749 | Primary | 3115
NPgN | SCARBOROUGH 66/11KV | 11 | 66 | MALTON GRID | OSBALDWICK | YO12 4EW | NPg Best View | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | Primary | 3116
NPgN | SEAHAM | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | TBC | NPg Best View | 0 | 0 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Primary | 3117
NPgN | SEGHILL | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 7EY | NPg Best View | 17.717 | 17.236 | 17.045 | 16.823 | 16.667 | 16.534 | 16.369 | 15.685 | 12.736 | 10.323 | 7.95 | Primary | 3118
NPgN | SOWERBY | 11 | 33 | HUSTHWAITE | KNARESBOROUGH | YO7 3NT | NPg Best View | 15.339 | 14.319 | 14.268 | 14.202 | 14.126 | 14.038 | 13.925 | 13.289 | 12.226 | 11.411 | 10.664 | Primary | 3119
NPgN | SEVERUS HILL | 11 | 33 | POPPLETON | POPPLETON | YO26 4RR | NPg Best View | 11.016 | 10.822 | 10.483 | 10.121 | 9.861 | 9.644 | 9.38 | 8.19 | 5.058 | 2.722 | 0.301 | Primary | 3120
NPgN | SHERIFF HUTTON | 11 | 66 | MALTON GRID | OSBALDWICK | YO60 6QN | NPg Best View | 13.088 | 12.859 | 12.521 | 12.184 | 11.899 | 11.625 | 11.295 | 9.78 | 6.877 | 4.644 | 2.457 | Primary | 3121
NPgN | SHOTTON | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR8 2EL | NPg Best View | 10.567 | 9.817 | 9.626 | 9.389 | 9.19 | 9.001 | 8.774 | 7.751 | 4.63 | 2.033 | -0.474 | Primary | 3122
NPgN | SIMONSIDE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE34 9PD | NPg Best View | 11.343 | 11.236 | 11.008 | 10.74 | 10.556 | 10.404 | 10.215 | 9.284 | 6.258 | 3.898 | 1.475 | Primary | 3123
NPgN | SKELDERGATE | 11 | 33 | POPPLETON | POPPLETON | YO1 6HN | NPg Best View | 18.812 | 18.064 | 18.053 | 18.011 | 17.994 | 17.985 | 17.949 | 17.679 | 15.845 | 14.382 | 12.927 | Primary | 3124
NPgN | SKERNESIDE | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DL5 6JH | NPg Best View | 16.604 | 16.346 | 15.902 | 15.405 | 15.015 | 14.641 | 14.182 | 11.86 | 7.288 | 4.001 | 0.782 | Primary | 3125
NPgN | SPADEADAM 20KV | 20 | 11 | SPADEADAM | HARKER | CA8 7AT | NPg Best View | 8.964 | 8.877 | 8.729 | 8.567 | 8.438 | 8.308 | 8.138 | 7.36 | 5.951 | 4.915 | 3.948 | Primary | 3126
NPgN | SPENCERBECK | 11 | 66 | LACKENBY | LACKENBY | TS3 8TE | NPg Best View | 12.914 | 12.518 | 10.585 | 10.035 | 9.634 | 9.284 | 8.87 | 6.941 | 1.421 | -2.618 | -6.624 | Primary | 3127
NPgN | SPENNYMOOR 66/20KV | 20 | 66 | SPENNYMOOR 132/66kV | SPENNYMOOR | DH6 5JX | NPg Best View | 23.356 | 13.845 | 6.704 | 6.266 | 5.918 | 5.603 | 5.226 | 3.426 | -0.877 | -4.112 | -7.365 | Primary | 3128
NPgN | STARBECK | 11 | 33 | HARROGATE 132/33kV | KNARESBOROUGH | HG2 7PT | NPg Best View | 2.696 | 1.967 | 1.304 | -1.142 | -1.615 | -2.027 | -2.527 | -4.619 | -9.992 | -14.218 | -18.491 | Primary | 3129
NPgN | STOBSWOOD COAL | 11 | 66 | LINTON | BLYTH 132kV | NE61 3AL | NPg Best View | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Primary | 3130
NPgN | STOKESLEY | 11 | 33 | BOWESFIELD | NORTON | TS9 5HS | NPg Best View | 5.549 | 5.452 | 5.299 | 5.115 | 4.97 | 4.83 | 4.664 | 3.735 | 1.45 | -0.4 | -2.223 | Primary | 3131
NPgN | STONEY CUT | 20 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR7 8RQ | NPg Best View | 12.225 | 11.45 | 11.106 | 10.666 | 10.324 | 10.022 | 9.677 | 8.158 | 4.235 | 1.318 | -1.591 | Primary | 3132
NPgN | SUNDERLAND T1 T2 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 8.106 | 6.493 | 6.385 | 6.22 | 6.132 | 6.065 | 5.963 | 5.367 | 2.477 | 0.267 | -1.95 | Primary | 3133
NPgN | SUNDERLAND T5 T6 | 11 | 66 | WEST BOLDON | WEST BOLDON | SR4 6BU | NPg Best View | 27.975 | 28.004 | 28.031 | 28.056 | 28.079 | 28.101 | 28.12 | 28.201 | 28.265 | 28.318 | 28.365 | Primary | 3134
NPgN | TANFIELD | 11 | 66 | ANNFIELD | STELLA SOUTH | DH9 9DB | NPg Best View | 20.028 | 18.999 | 18.618 | 18.194 | 17.881 | 17.613 | 17.306 | 16.049 | 12.49 | 9.628 | 6.729 | Primary | 3135
NPgN | TEAM VALLEY | 20 | 66 | RAVENSWORTH | STELLA SOUTH | NE11 0SX | NPg Best View | 8.55 | 8.011 | 8.186 | 8.273 | 8.285 | 8.207 | 8.018 | 6.428 | 4.419 | 3.582 | 3.042 | Primary | 3136
NPgN | TEES INDUSTRIAL T1 T2 | 11 | 66 | SEAL SANDS | SALTHOLME | TS23 3NF | NPg Best View | 4.301 | 4.263 | 4.279 | 4.287 | 4.285 | 4.274 | 4.248 | 4.066 | 3.739 | 3.381 | 3.019 | Primary | 3137
NPgN | TEMPLE PARK | 11 | 66 | WEST BOLDON | WEST BOLDON | NE34 8TH | NPg Best View | 14.487 | 14.19 | 13.721 | 13.222 | 12.897 | 12.642 | 12.342 | 11.064 | 6.079 | 1.912 | -2.342 | Primary | 3138
NPgN | THIRSK | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | YO7 4NH | NPg Best View | 2.604 | 2.363 | 1.999 | 1.597 | 1.229 | 0.855 | 0.408 | -1.768 | -5.651 | -8.676 | -11.549 | Primary | 3139
NPgN | THORNTON DALE | 11 | 66 | MALTON GRID | OSBALDWICK | YO18 7SJ | NPg Best View | 8.918 | 8.027 | 7.743 | 7.443 | 7.182 | 6.947 | 6.666 | 5.507 | 3.616 | 2.273 | 0.912 | Primary | 3140
NPgN | TORONTO 66/20KV | 20 | 66 | TORONTO | SPENNYMOOR | DL14 7RJ | NPg Best View | 25.316 | 24.837 | 24.398 | 23.898 | 23.494 | 23.117 | 22.677 | 20.665 | 15.198 | 10.767 | 6.503 | Primary | 3141
NPgN | TUNSTALL | 11 | 66 | HAWTHORN PIT GRID | HAWTHORN PIT GRID | SR3 2BT | NPg Best View | 11.842 | 11.576 | 11.082 | 10.514 | 10.125 | 9.818 | 9.456 | 7.969 | 3.201 | -0.446 | -4.239 | Primary | 3142
NPgN | TYNEMOUTH CENTRAL | 11 | 33 | CHIRTON GRANGE | TYNEMOUTH | NE30 1JG | NPg Best View | 11.392 | 11.087 | 10.597 | 10.064 | 9.666 | 9.322 | 8.925 | 7.175 | 1.984 | -2.261 | -6.514 | Primary | 3143
NPgN | UNIVERSITY | 11 | 33 | BARRACK ROAD | STELLA NORTH | NE2 4PZ | NPg Best View | 14.122 | 13.99 | 14.121 | 14.223 | 14.337 | 14.451 | 14.54 | 14.907 | 14.218 | 13.667 | 13.073 | Primary | 3144
NPgN | URLAY NOOK | 11 | 33 | BOWESFIELD | NORTON | TS16 0QB | NPg Best View | 32.847 | 32.521 | 32.05 | 31.567 | 31.164 | 30.776 | 30.326 | 28.306 | 23.006 | 18.493 | 14.107 | Primary | 3145
NPgN | USWORTH | 11 | 66 | WEST BOLDON | WEST BOLDON | NE37 3HY | NPg Best View | 9.865 | 8.361 | 8.313 | 8.231 | 8.163 | 8.08 | 7.949 | 7.233 | 5.108 | 3.469 | 1.962 | Primary | 3146
NPgN | WALKER | 11 | 66 | WEST BOLDON | WEST BOLDON | NE6 3PZ | NPg Best View | 8.335 | 7.655 | 7.314 | 6.936 | 6.61 | 6.311 | 5.969 | 4.548 | 0.17 | -3.503 | -7.076 | Primary | 3147
NPgN | WANSBECK | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE22 7DH | NPg Best View | 30.752 | 30.767 | 30.779 | 30.788 | 30.8 | 30.811 | 30.82 | 30.863 | 30.858 | 30.855 | 30.847 | Primary | 3148
NPgN | WARDLEY | 6 | 66 | WEST BOLDON | WEST BOLDON | NE31 1LP | NPg Best View | 9.173 | 9.18 | 24.517 | 24.428 | 24.387 | 24.373 | 24.346 | 24.245 | 22.484 | 21 | 19.456 | Primary | 3149
NPgN | WARKWORTH | 20 | 66 | LINTON | BLYTH 132kV | NE65 0YD | NPg Best View | 8.83 | 7.239 | 21.911 | 21.562 | 21.272 | 20.996 | 20.661 | 19.157 | 14.536 | 10.805 | 7.261 | Primary | 3150
NPgN | WENSLEYDALE | 11 | 33 | LEEMING BAR_SKEEBY | NORTON | DL8 5ED | NPg Best View | 9.603 | 9.398 | 9.098 | 8.759 | 8.437 | 8.114 | 7.735 | 5.84 | 2.462 | -0.231 | -2.851 | Primary | 3151
NPgN | WEST HARTFORD | 11 | 66 | BLYTH 66kV | BLYTH 66kV | NE23 3JP | NPg Best View | 12.166 | 12.093 | 11.977 | 11.858 | 11.762 | 11.669 | 11.556 | 11.125 | 10.031 | 9.133 | 8.306 | Primary | 3152
NPgN | WEST SOUTHWICK | 11 | 66 | WEST BOLDON | WEST BOLDON | SR5 3TX | NPg Best View | 20.336 | 19.844 | 19.772 | 19.677 | 19.615 | 19.562 | 19.483 | 19.136 | 16.693 | 14.595 | 12.582 | Primary | 3153
NPgN | WEST WYLAM | 20 | 66 | COALBURNS | STELLA SOUTH | NE42 5EX | NPg Best View | 11.181 | 10.849 | 10.321 | 9.796 | 9.391 | 9.014 | 8.54 | 6.393 | 1.645 | -1.865 | -5.29 | Primary | 3154
NPgN | WESTERHOPE | 11 | 33 | BLUCHER | STELLA NORTH | NE5 5HH | NPg Best View | 12.365 | 12.006 | 11.701 | 11.352 | 11.091 | 10.869 | 10.612 | 9.531 | 5.358 | 1.825 | -1.664 | Primary | 3155
NPgN | WESTOE | 11 | 33 | SOUTH SHIELDS | SOUTH SHIELDS | NE33 3GE | NPg Best View | 11.01 | 10.473 | 10.144 | 9.778 | 9.486 | 9.216 | 8.889 | 7.521 | 3.66 | 0.483 | -2.572 | Primary | 3156
NPgN | WHITBY T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO22 4JE | NPg Best View | 4.907 | 4.908 | 4.873 | 4.823 | 4.797 | 4.779 | 4.752 | 4.609 | 3.685 | 2.959 | 2.239 | Primary | 3157
NPgN | WHITBY T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO22 4JE | NPg Best View | 4.77 | 4.77 | 4.736 | 4.679 | 4.633 | 4.589 | 4.532 | 4.201 | 3.086 | 2.27 | 1.492 | Primary | 3158
NPgN | WHITBY WEST T1 | 11 | 33 | SCARBOROUGH GRID | OSBALDWICK | YO21 1LY | NPg Best View | 7.565 | 7.49 | 7.359 | 7.214 | 7.1 | 7.002 | 6.883 | 6.37 | 5.22 | 4.375 | 3.522 | Primary | 3159
NPgN | WHITBY WEST T2 | 11 | 66 | MALTON GRID | OSBALDWICK | YO21 1LY | NPg Best View | 7.434 | 7.352 | 7.207 | 7.042 | 6.922 | 6.824 | 6.71 | 6.211 | 4.634 | 3.415 | 2.179 | Primary | 3160
NPgN | WILLINGTON | 11 | 33 | FLATWORTH | TYNEMOUTH | NE28 7HS | NPg Best View | 13.202 | 13.043 | 12.779 | 12.495 | 12.238 | 11.994 | 11.714 | 10.545 | 6.526 | 2.963 | -0.422 | Primary | 3161
NPgN | WORMALD GREEN 132/11KV | 11 | 132 | WORMALD GREEN 132/11kV | KNARESBOROUGH | HG3 3PS | NPg Best View | 22.256 | 21.932 | 21.455 | 20.996 | 20.662 | 20.375 | 20.025 | 18.507 | 14.999 | 12.351 | 9.627 | Primary | 3162
NPgN | WYNYARD | 11 | 66 | HARTMOOR | HARTMOOR | TS2 2FB | NPg Best View | 29.816 | 28.934 | 28.897 | 28.86 | 28.816 | 28.766 | 28.702 | 28.365 | 28.004 | 27.736 | 27.493 | Primary | 3163
NPgN | YEDINGHAM | 11 | 66 | MALTON GRID | OSBALDWICK | YO17 8RR | NPg Best View | 5.832 | 5.422 | 5.399 | 5.371 | 5.349 | 5.33 | 5.306 | 5.2 | 4.758 | 4.4 | 4.049 | Primary | 3164
NPgN | YORK UNIVERSITY | 11 | 33 | MELROSEGATE | OSBALDWICK | YO10 5ZF | NPg Best View | 11.739 | 11.806 | 11.822 | 11.815 | 11.823 | 11.836 | 11.832 | 11.812 | 10.162 | 8.762 | 7.434 | Primary | 3165

## EISD Transmission
Earliest in Service Dates (EISDs) for new applications to the transmission network - to accompany a DNO's Network Headroom Report
IMPORTANT: Unlike the rest of the DNO Network Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output. Keeping customers informed continues to be Northern Powergrid's priority as the number of connection applications remains high meaning that availability of transmission capacity changes quickly. We are working with customers and the ESO to accelerate connection dates.
2024-03-28 | Transmission Owner's freeze date
Northern Powergrid (Northeast) | DNO Licence area
NGET | Transmission Owner providing
2024-03-28 | Last update (version, date)
| Generation |  | Demand
GSP | EISD | Under review at freeze date? | EISD | Under review at freeze date? | Comments (optional)
Blyth 132kV | 2032 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process | Under active review
Blyth 66kV | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process | To be reviewed with next application to transmission
Fourstones | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Hartmoor | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Hawthorn Pit | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Knaresborough | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Lackenby | 2031 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Norton | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Offerton | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Osbaldwick | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Poppleton | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Saltholme | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
South Shields | 2032 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Spennymoor | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Stella North | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Stella South | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Tynemouth | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
West Boldon | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Bradford West | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Camblesforth | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Creyke Beck | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Drax | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Elland | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Ferrybridge A | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Ferrybridge B | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Grimsby West | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Jordanthorpe | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Keadby | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Kirkstall | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Neepsend | 2036 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Norton Lees | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Pitsmoor | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Saltend North | 2037 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Sheffield City | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Skelton Grange C | 2035 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Templeborough (values assumed by NPg) | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Thorpe Marsh | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Thurcroft | 2034 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
West Melton | 2033 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Wincobank | 2030 | Under active review |  | To be reviewed | Being reviewed as part of the ongoing Transmission Works Review process
Links to additional public-domain information related to the EISDs, provided by the Transmission Owner
https://www.nationalgrid.com/electricity-transmission/connections/regional-customer-connections-update
Purpose
To indicate potential transmission constraints by 'Earliest in Service Date' per Grid Supply Point (GSP)
To accompany a DNO's Network Scenario Headroom Report of unused substation capacity at primary substations and Bulk Supply Points
To address stakeholder feedback that information in the Network Headroom Reports requires context of potential transmission restrictions to connecting at the distribution network.
Notes
1 | Unlike the rest of the DNO Network Scenario Headroom Reports, this is a snapshot of current status based on connection applications, not a scenario based output. Keeping customers informed continues to be Northern Powergrid's priority as the number of connection applications remains high meaning that availability of transmission capacity changes quickly.
Earliest in service dates (EISDs) represent a snapshot of the Transmission Owner's view at the 'freeze date' of the earliest date for connection for NEW applications for demand and generation of significant size (>1MW)
2 | Northern Powergrid are undertaking numerous projects in collaboration with the other network companies to accelerate these connection dates where possible. More information will be released in 2023 and current and future customers are being kept informed.
3 | For storage, both the demand and generation EISDs may be relevant.
Where an EISD has not been established for a GSP, this is shown as N/A.
4 | There is likely to be some headroom for connection because there is no constraint yet defined with defined construction works affecting connection, this is shown as "no date restriction identified".
5 | Where the transmission owner is actively reviewing construction works and earliest in service dates for new applications may be revised e.g. due to an application for capacity affecting that GSP, this is shown as "under active review"
6 | The EISDs reflect both works at a Grid Supply Point and in wider transmission network.
7 | The list of GSPs includes at a minimum the GSPs associated with the primary substations and Bulk Supply Points in the DNO's last Long-Term Development Statement Table 3. Future GSPs may not be included.